## PG&E 2022 CPUC Report Ignitions
Index | Utility Name | Fire Start |  | Location |  |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
|  | Date | Time | Latitude | Longitude | Material at Origin | Material at Origin - Comments | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes
20222036 | PG&E | 2022-11-22 | 14:14 | 35.36 | -119.044 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Customer | N/A | 100194714 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-22 | 14:10 | Contact From Object | N/A | Animal | Fuse | Outside Force
20222010 | PG&E | 2022-11-12 | 14:12 | 38.2461 | -122.4448 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 101998852 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-12 | 14:10 | Contact From Object | N/A | Other | Conductor - Primary | Outside Force
20221944 | PG&E | 2022-11-01 | 20:26 | 36.7733 | -119.5927 | Other | Pole | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 100722119 | No | 12000 | Pole | Overhead | Yes | 2022-11-01 | 18:44 | Contamination | N/A | N/A | N/A | N/A
20221869 | PG&E | 2022-10-27 | 21:05 | 36.2762 | -119.7434 | Other | Transformer bushing | Agricultural | Less than three(3) meters of linear travel | Self Extinguished | N/A | 100821671 | No | 750 | Transformer Bushing | Overhead | Yes | 2022-10-27 | 20:35 | Equipment/Facility Failure | Transformer Bushing | N/A | N/A | N/A
20221771 | PG&E | 2022-10-05 | 10:53 | 34.8556 | -120.279 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Self Extinguished | N/A | 101862511 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2022-10-05 | 10:49 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20221748 | PG&E | 2022-09-29 | 10:25 | 35.1934 | -118.9233 | Other | Jumper | Agricultural | Less than three(3) meters of linear travel | Customer | N/A | 100150838 | No | 750 | Jumper | Overhead | Yes | 2022-09-29 | 11:38 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20221753 | PG&E | 2022-09-28 | 22:09 | 37.2439 | -121.9642 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Unknown | N/A | 100514514 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-28 | 21:54 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221740 | PG&E | 2022-09-27 | 12:52 | 36.633 | -119.9897 | Other | Bird | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 100667215 | No | 12000 | Recloser | Overhead | Yes | 2022-09-19 | 11:25 | Contact From Object | N/A | Animal | Recloser | Outside Force
20221711 | PG&E | 2022-09-25 | 15:06 | 38.0004 | -121.8153 | Other | Mylar Balloon | Urban | Less than three(3) meters of linear travel | Unknown | N/A | 100454182 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-25 | 15:04 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221597 | PG&E | 2022-09-10 | 19:12 | 35.161 | -119.3772 | Other | Cut out | Desert Shrub | Less Than .25 Acres | Self Extinguished | N/A | 100189196 | Yes | 12000 | Other | Overhead | Yes | 2022-09-11 | 19:07 | Vandalism/Theft | N/A | N/A | N/A | N/A
20221580 | PG&E | 2022-09-09 | 14:23 | 39.7953 | -123.2604 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Customer | N/A | 102181416 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-09-09 | 16:11 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221551 | PG&E | 2022-09-07 | 11:12 | 35.371 | -118.9359 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Self Extinguished | N/A | 100214623 | Yes | 750 | Service Drop | Overhead | Yes | 2022-09-07 | 11:09 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221528 | PG&E | 2022-09-05 | 16:33 | 37.9936 | -121.3 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Customer | N/A | 102138681 | Yes | 12000 | Transformer | Overhead | Yes | 2022-09-05 | 15:33 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221476 | PG&E | 2022-08-29 | 16:21 | 35.0163 | -118.8428 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 100223285 | No | 12000 | Transformer | Overhead | Yes | 2022-08-29 | 16:13 | Contact From Object | N/A | Animal | Transformer | Outside Force
20221463 | PG&E | 2022-08-26 | 18:50 | 37.0948 | -120.9565 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 101187799 | No | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-08-27 | 18:42 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221432 | PG&E | 2022-08-22 | 11:41 | 35.4116 | -119.0559 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Utility | N/A | 40340737 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2022-08-22 | 11:34 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20221425 | PG&E | 2022-08-21 | 13:43 | 37.1497 | -120.5054 | Other | Service Drop | Agricultural | Less Than .25 Acres | Customer | N/A | 101080714 | No | 750 | Service Drop | Overhead | Yes | 2022-08-21 | 12:52 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221428 | PG&E | 2022-08-21 | 22:53 | 36.819 | -119.5987 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 100799319 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-22 | 21:00 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221423 | PG&E | 2022-08-21 | 04:27 | 38.4727 | -121.5343 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 101668289 | Yes | 21000 | Pole | Overhead | Yes | 2022-08-21 | 04:20 | Contact From Object | N/A | Vehicle | Pole | N/A
20221376 | PG&E | 2022-08-13 | 18:53 | 37.7158 | -121.9324 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Customer | N/A | 100912646 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-08-13 | 17:34 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221371 | PG&E | 2022-08-12 | 16:48 | 38.1154 | -121.0885 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Customer | N/A | 102074437 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-08-12 | 16:45 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221363 | PG&E | 2022-08-11 | 11:53 | 35.2276 | -118.9146 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Utility | N/A | 100123886 | No | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-08-11 | 11:47 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221352 | PG&E | 2022-08-09 | 21:53 | 39.0128 | -122.0477 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 101654771 | Yes | 12000 | Jumper | Overhead | Yes | 2022-08-10 | 21:51 | Contact From Object | N/A | Animal | Jumper | Outside Force
20221302 | PG&E | 2022-08-01 | 10:21 | 35.4211 | -119.0544 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Unknown | N/A | 100145916 | Yes | 12000 | Switch | Overhead | No | N/A | N/A | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221294 | PG&E | 2022-07-31 | 04:16 | 35.0595 | -119.0202 | Vegetation | N/A | Urban | Less Than .25 Acres | Self Extinguished | N/A | 100221134 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-31 | 04:14 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221293 | PG&E | 2022-07-31 | 01:34 | 34.6161 | -120.3728 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Self Extinguished | N/A | 101906973 | Yes | 12000 | Automatic Wire Splice | Overhead | Yes | 2022-07-31 | 22:12 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20221267 | PG&E | 2022-07-26 | 18:31 | 38.6601 | -122.4739 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Self Extinguished | N/A | 102251266 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-07-27 | 18:29 | Other | N/A | N/A | N/A | N/A
20221217 | PG&E | 2022-07-20 | 20:39 | 38.61 | -120.6569 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Customer | N/A | 101395273 | No | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-07-21 | 20:31 | Equipment/Facility Failure | Conductor - Open Wire Secondary | N/A | N/A | N/A
20221147 | PG&E | 2022-07-13 | 14:54 | 38.308 | -122.6892 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Self Extinguished | N/A | 104132226 | No | 750 | Pole | Overhead | Yes | 2022-07-13 | 14:52 | Contact From Object | N/A | Vehicle | Pole | N/A
20221120 | PG&E | 2022-07-10 | 11:50 | 35.5983 | -119.3126 | Other | Balloon | Agricultural | Less Than .25 Acres | Customer | N/A | 100178690 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-10 | 11:37 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221112 | PG&E | 2022-07-09 | 21:28 | 37.9556 | -121.2452 | Building | N/A | Urban | Less than three(3) meters of linear travel | Customer | N/A | 102111650 | No | 750 | Service Drop | Overhead | Yes | 2022-07-10 | 21:25 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221082 | PG&E | 2022-07-06 | 06:52 | 40.4949 | -122.3191 | Other | Animal | Agricultural | Less than three(3) meters of linear travel | Customer | N/A | 101494186 | Yes | 12000 | Transformer | Overhead | Yes | 2022-07-06 | 06:40 | Contact From Object | N/A | Animal | Transformer | Outside Force
20221083 | PG&E | 2022-07-06 | 07:03 | 38.4042 | -122.6311 | Other | Fault Tamer | Hardwood Forest | Less than three(3) meters of linear travel | Customer | N/A | 104100052 | Yes | 12000 | Fault Tamer | Overhead | Yes | 2022-07-06 | 06:50 | Equipment/Facility Failure | Fault Tamer | N/A | N/A | N/A
20221075 | PG&E | 2022-07-05 | 16:56 | 35.4155 | -119.0229 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 40340842 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2022-07-05 | 16:48 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20221069 | PG&E | 2022-07-05 | 08:29 | 35.1661 | -119.3759 | Vegetation | N/A | Desert Shrub | Less Than .25 Acres | Unknown | N/A | 100189204 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-05 | 01:24 | Vandalism/Theft | N/A | N/A | N/A | N/A
20221045 | PG&E | 2022-07-02 | 18:06 | 38.0846 | -121.7083 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Unknown | N/A | 101582430 | Yes | 21000 | Jumper | Overhead | Yes | 2022-07-03 | 18:01 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20221019 | PG&E | 2022-06-29 | 07:38 | 37.2511 | -121.9609 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Unknown | N/A | 100548384 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-29 | 07:27 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221219 | PG&E | 2022-06-25 | 12:45 | 38.3154 | -121.8832 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Unknown | N/A | 101561580 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-25 | 12:29 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221218 | PG&E | 2022-06-25 | 12:40 | 38.4406 | -121.8593 | Other | Conductor | Agricultural | Less Than .25 Acres | Unknown | N/A | 101580785 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-25 | 12:28 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220941 | PG&E | 2022-06-22 | 16:25 | 36.8592 | -119.694 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 100754255 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-22 | 07:28 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220936 | PG&E | 2022-06-13 | 19:07 | 37.793 | -121.2547 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Unknown | N/A | 43249380 | No | 115000 | Circuit Breaker | Overhead | No | N/A | N/A | Equipment/Facility Failure | Circuit Breaker | N/A | N/A | N/A
20221018 | PG&E | 2022-06-10 | 16:28 | 36.6839 | -119.7369 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 100809590 | Yes | 750 | Riser | Overhead | Yes | 2022-06-10 | 16:27 | Equipment/Facility Failure | Riser | N/A | N/A | N/A
20220752 | PG&E | 2022-06-03 | 17:56 | 37.3393 | -120.3692 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Customer | N/A | 101144101 | No | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-06-03 | 17:53 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220740 | PG&E | 2022-06-02 | 08:55 | 36.6146 | -119.5838 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Self Extinguished | N/A | 103319095 | No | 750 | Service Drop | Overhead | Yes | 2022-06-02 | 08:36 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20220716 | PG&E | 2022-05-31 | 07:01 | 38.4862 | -121.7906 | Other | Riser | Agricultural | Less than three(3) meters of linear travel | Self Extinguished | N/A | 101599641 | Yes | 12000 | Pothead | Overhead | Yes | 2022-05-31 | 06:50 | Equipment/Facility Failure | Pothead | N/A | N/A | N/A
20220699 | PG&E | 2022-05-27 | 06:59 | 38.4881 | -123.0286 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Self Extinguished | N/A | 102036349 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-27 | 22:48 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220692 | PG&E | 2022-05-26 | 15:41 | 38.3722 | -121.9437 | Vegetation | N/A | Urban | Less Than .25 Acres | Self Extinguished | N/A | 101571222 | No | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-05-26 | 15:38 | Contact From Object | N/A | Other | Conductor - Open Wire Secondary | Human Error
20220695 | PG&E | 2022-05-26 | 20:23 | 36.5195 | -119.6684 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 100830724 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-27 | 20:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220690 | PG&E | 2022-05-25 | 06:09 | 37.962 | -121.3052 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Unknown | N/A | 102099861 | Yes | 4000 | Transformer | Overhead | Yes | 2022-05-25 | 18:04 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20220620 | PG&E | 2022-05-18 | 12:53 | 37.9311 | -121.3185 | Vegetation | N/A | Urban | Less Than .25 Acres | Utility | N/A | 102130395 | No | 12000 | Pothead | Overhead | Yes | 2022-05-18 | 12:49 | Contact From Object | N/A | Animal | Pothead | Outside Force
20220570 | PG&E | 2022-05-10 | 09:56 | 37.7065 | -121.215 | Other | Conductor | Agricultural | Less than three(3) meters of linear travel | Unknown | N/A | 102069037 | Yes | 17000 | Conductor - Primary | Overhead | Yes | 2022-05-10 | 09:47 | Other | N/A | N/A | N/A | Human Error
20220563 | PG&E | 2022-05-08 | 17:31 | 39.1146 | -121.4956 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Customer | N/A | 101305011 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-05-09 | 17:28 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220562 | PG&E | 2022-05-08 | 16:17 | 39.5424 | -122.1831 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Unknown | N/A | 100332833 | Yes | 750 | Service Drop | Overhead | Yes | 2022-05-08 | 16:12 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220545 | PG&E | 2022-05-04 | 19:31 | 36.4884 | -119.4924 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Utility | N/A | 103149624 | Yes | 12000 | Transformer | Overhead | Yes | 2022-05-05 | 19:12 | Contact From Object | N/A | Vehicle | Transformer | N/A
20220512 | PG&E | 2022-04-28 | 20:03 | 36.9788 | -120.0698 | Other | Balloons | Urban | Less than three(3) meters of linear travel | Self Extinguished | N/A | 40239490 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-28 | 19:56 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220508 | PG&E | 2022-04-28 | 13:56 | 35.2415 | -119.0299 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 100148462 | No | 750 | Transformer Bushing | Overhead | Yes | 2022-04-28 | 13:48 | Equipment/Facility Failure | Transformer Bushing | N/A | N/A | N/A
20220485 | PG&E | 2022-04-24 | 14:29 | 38.1358 | -121.1738 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Self Extinguished | N/A | 102079450 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-04-24 | 14:22 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220414 | PG&E | 2022-04-11 | 13:10 | 39.4407 | -121.4567 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Customer | N/A | 100415109 | No | 750 | Service Drop | Overhead | Yes | 2022-04-11 | 13:03 | Contact From Object | N/A | Other | Service Drop | Weather
20220415 | PG&E | 2022-04-11 | 17:35 | 36.0231 | -120.1109 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Self Extinguished | N/A | 100701219 | No | 21000 | Pole | Overhead | Yes | 2022-04-12 | 17:19 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20220387 | PG&E | 2022-04-07 | 10:32 | 39.3715 | -121.2359 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Customer | N/A | 101286319 | Yes | 12000 | Pole | Overhead | Yes | 2022-04-27 | 10:27 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220364 | PG&E | 2022-04-03 | 07:52 | 37.5964 | -121.3609 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Unknown | N/A | 41132785 | No | 115000 | Insulator | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Insulator | Outside Force
20220346 | PG&E | 2022-03-28 | 10:16 | 35.8871 | -119.9154 | Other | Bird Nest | Herbaceous | Less than three(3) meters of linear travel | Unknown | N/A | 40748420 | No | 70000 | Pole | Overhead | Yes | 2022-03-28 | 10:16 | Contact From Object | N/A | Animal | Pole | Outside Force
20220322 | PG&E | 2022-03-25 | 17:43 | 39.9808 | -122.1557 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Self Extinguished | N/A | 103133375 | No | 12000 | Jumper | Overhead | Yes | 2022-03-25 | 18:11 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20220309 | PG&E | 2022-03-22 | 21:58 | 39.6491 | -121.4361 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Self Extinguished | N/A | 100424838 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-22 | 21:58 | Other | N/A | N/A | N/A | N/A
20220385 | PG&E | 2022-03-20 | 14:52 | 38.7493 | -121.5861 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Unknown | N/A | 101334953 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-20 | 14:49 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220202 | PG&E | 2022-02-26 | 17:41 | 35.5484 | -120.7989 | Other | Transformer | Hardwood Woodland | Less than three(3) meters of linear travel | Self Extinguished | N/A | 101947610 | No | 12000 | Transformer Bushing | Overhead | Yes | 2022-02-26 | 18:32 | Equipment/Facility Failure | Transformer Bushing | N/A | N/A | N/A
20220069 | PG&E | 2022-01-25 | 09:27 | 41.2855 | -123.8282 | Vegetation | N/A | Conifer Forest | Less than three(3) meters of linear travel | Utility | N/A | 103153668 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-01-25 | 09:20 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20222125 | PG&E | 2022-12-17 | 13:56 | 35.4284 | -118.943 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Kern County FD | 100203262 | Yes | 12000 | Pole | Overhead | Yes | 2022-12-17 | 13:54 | Equipment/Facility Failure | Other | N/A | N/A | N/A
20222130 | PG&E | 2022-12-17 | 11:37 | 36.6098 | -119.5244 | Other | Communication line | Urban | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 100887254 | Yes | 12000 | Automatic Wire Splice | Overhead | Yes | 2022-12-17 | 11:23 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20222054 | PG&E | 2022-11-28 | 9:52 | 37.8952 | -121.5865 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100497944 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-11-28 | 09:46 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20222144N | PG&E | 2022-11-28 | 13:36 | 38.9926 | -121.2841 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Lincoln FD | 100026568 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-28 | 13:28 | Contact From Object | N/A | Vehicle | Pole | N/A
20222048 | PG&E | 2022-11-27 | 22:16 | 39.129 | -121.4632 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Linda FD | 101329966 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-27 | 22:04 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20222043 | PG&E | 2022-11-25 | 11:12 | 37.7378 | -122.2034 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Oakland FD | 101342961 | Yes | 12000 | Transformer | Overhead | Yes | 2022-11-25 | 11:04 | Contact From Object | N/A | Animal | Transformer | Outside Force
20222035 | PG&E | 2022-11-22 | 16:20 | 36.9418 | -121.4479 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Hollister FD, CAL FIRE | 101717355 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-11-22 | 16:15 | Contact From Object | N/A | Vehicle | Guy/Span Wire | N/A
20222018 | PG&E | 2022-11-19 | 16:26 | 38.4057 | -121.9156 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Dixon FD | 101575004 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-19 | 16:21 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20222019 | PG&E | 2022-11-19 | 08:35 | 40.3891 | -122.2486 | Building | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | Cottonwood FD | 101487796 | No | 750 | Service Drop | Overhead | Yes | 2022-11-19 | 07:52 | Contact From Object | N/A | Animal | Service Drop | Outside Force
20222017 | PG&E | 2022-11-19 | 15:22 | 36.8018 | -121.7009 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Unknown Fire Department | 101720430 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-19 | 15:19 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20222013 | PG&E | 2022-11-16 | 09:32 | 38.047 | -122.2106 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Contra Costa County FD | 101424195 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-11-16 | 09:30 | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20222003 | PG&E | 2022-11-12 | 14:12 | 38.2461 | -122.4448 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 101998852 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-12 | 14:10 | Contact From Object | N/A | Other | Conductor - Primary | N/A
20221924 | PG&E | 2022-11-03 | 20:32 | 34.8937 | -120.4185 | Vegetation | N/A | Shrub | Less Than .25 Acres | Fire Agency | Santa Barbara County FD | 101868809 | No | 12000 | Splice/Clamp/Connector | Overhead | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221892 | PG&E | 2022-11-01 | 08:17 | 39.8266 | -121.8554 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 100402196 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-11-01 | 08:13 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221886 | PG&E | 2022-10-31 | 08:31 | 36.0812 | -119.4857 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 103885299 | No | 12000 | Pole | Overhead | Yes | 2022-10-31 | 08:29 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20221873 | PG&E | 2022-10-29 | 12:34 | 36.7754 | -119.7979 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno FD | 100858694 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-10-29 | 13:10 | Contact From Object | N/A | Other | Conductor - Open Wire Secondary | Human Error
20221862 | PG&E | 2022-10-26 | 15:21 | 38.7403 | -123.3522 | Vegetation | N/A | Conifer Forest | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 102215812 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-26 | 15:17 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221871 | PG&E | 2022-10-26 | 10:18 | 40.2433 | -124.1289 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 103948511 | No | 12000 | Fuse | Overhead | Yes | 2022-10-26 | 10:08 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221857 | PG&E | 2022-10-24 | 16:39 | 36.0942 | -119.5004 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Kings County FD | 100690028 | Yes | 12000 | Fuse | Overhead | Yes | 2022-10-24 | 16:38 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221854 | PG&E | 2022-10-23 | 11:03 | 38.4425 | -122.5409 | Vegetation | N/A | Conifer Forest | Less than three(3) meters of linear travel | Fire Agency | Kenwood Fire Dept | 101958013 | No | 750 | Service Drop | Overhead | Yes | 2022-10-23 | 10:53 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221849 | PG&E | 2022-10-22 | 20:24 | 37.3036 | -121.8398 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100572664 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-10-23 | 20:19 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221840 | PG&E | 2022-10-20 | 01:12 | 37.5119 | -122.5031 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 100315975 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-19 | 22:55 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221842 | PG&E | 2022-10-20 | 16:25 | 37.2922 | -122.2419 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100267338 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-20 | 16:25 | Other | N/A | N/A | N/A | N/A
20221837 | PG&E | 2022-10-19 | 15:02 | 34.9168 | -120.4452 | Other | Cut out | Urban | Less than three(3) meters of linear travel | Fire Agency | Santa Maria FD | 101898240 | No | 12000 | Fuse | Overhead | No | N/A | N/A | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221827 | PG&E | 2022-10-17 | 18:30 | 37.9946 | -121.0951 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Stanislaus County, Linden FD | 102118148 | No | 750 | Service Drop | Overhead | Yes | 2022-10-18 | 18:29 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221825 | PG&E | 2022-10-17 | 13:39 | 38.6676 | -123.412 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | North Sonoma Coast FD | 102200423 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-17 | 13:37 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221826 | PG&E | 2022-10-17 | 13:24 | 40.4188 | -124.1221 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101001028 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-13 | 13:20 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20221823 | PG&E | 2022-10-16 | 15:03 | 38.8896 | -121.4699 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Placer County FD, Linda FD, Pleasant Grove FD | 100048353 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-16 | 14:00 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221824 | PG&E | 2022-10-16 | 16:50 | 39.0487 | -121.0559 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100018944 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-10-16 | 18:06 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221821 | PG&E | 2022-10-15 | 11:09 | 38.7396 | -121.3961 | Vegetation | N/A | Agricultural | 10-99 Acres | Fire Agency | CAL FIRE | 100109777 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-15 | 11:08 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221813 | PG&E | 2022-10-14 | 14:10 | 38.0247 | -121.9056 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Contra Costa FD | 101566756 | No | 21000 | Capacitor Bank | Overhead | Yes | 2022-10-14 | 15:45 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20221815 | PG&E | 2022-10-14 | 15:52 | 37.0982 | -119.7991 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Madera County FD | 103213487 | No | 21000 | Pole | Overhead | Yes | 2022-10-14 | 15:46 | Contact From Object | N/A | Vehicle | Pole | N/A
20221806 | PG&E | 2022-10-12 | 06:26 | 37.9748 | -122.4923 | Vegetation | N/A | Hardwood Woodland | Less than three(3) meters of linear travel | Fire Agency | San Rafael FD | 41102539 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2022-10-12 | 06:24 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20221805 | PG&E | 2022-10-12 | 14:52 | 36.7667 | -121.7479 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | North County FD | 103811763 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-10-12 | 14:41 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221802 | PG&E | 2022-10-10 | 21:47 | 37.9407 | -121.6072 | Other | Balloon | Agricultural | Less Than .25 Acres | Fire Agency | Contra Costa FD | 100473215 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-11 | 21:43 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221798 | PG&E | 2022-10-10 | 02:15 | 38.3792 | -121.8409 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Dixon FD | 101566756 | Yes | 12000 | Jumper | Overhead | Yes | 2022-10-10 | 00:48 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20221782 | PG&E | 2022-10-07 | 10:33 | 37.098 | -120.1771 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Prison FD | 101128073 | No | 12000 | Pole | Overhead | Yes | 2022-10-07 | 10:38 | Contact From Object | N/A | Vehicle | Pole | N/A
20221790 | PG&E | 2022-10-07 | 22:29 | 36.7964 | -119.7544 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Fresno FD | 100835896 | Yes | 12000 | Riser | Overhead | Yes | 2022-10-07 | 22:22 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20221774 | PG&E | 2022-10-06 | 01:58 | 38.9513 | -123.6846 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 102186869 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-06 | 01:41 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221772 | PG&E | 2022-10-05 | 13:58 | 39.5786 | -121.6936 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 100396853 | No | 750 | Service Drop | Overhead | No | N/A | N/A | Contact From Object | N/A | Vehicle | Service Drop | N/A
20221767 | PG&E | 2022-10-04 | 21:52 | 38.8999 | -120.9928 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 100049423 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-10-04 | 21:51 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221765 | PG&E | 2022-10-04 | 14:44 | 38.4387 | -121.837 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Dixon FD | 101661346 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-10-04 | 14:38 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221759 | PG&E | 2022-10-02 | 14:08 | 36.5735 | -121.8754 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 40649689 | No | 60000 | Pole | Overhead | Yes | 2022-10-02 | 14:05 | Contact From Object | N/A | Vehicle | Pole | N/A
20221757 | PG&E | 2022-10-01 | 15:58 | 38.9973 | -122.8843 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Kelseyville FD | 102158713 | No | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-10-01 | 15:57 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20221755 | PG&E | 2022-10-01 | 03:44 | 37.8602 | -122.2975 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Berkeley FD | 101450482 | Yes | 750 | Riser | Overhead | Yes | 2022-10-01 | 04:27 | Equipment/Facility Failure | Riser | N/A | N/A | N/A
20221739 | PG&E | 2022-09-27 | 11:21 | 35.2038 | -118.7705 | Other | Conduit | Herbaceous | Less Than .25 Acres | Fire Agency | Kern County FD | 100146321 | No | 750 | Conductor - Underground Service | Subsurface | No | N/A | N/A | Equipment/Facility Failure | Conductor - Underground Service | N/A | N/A | N/A
20221738 | PG&E | 2022-09-26 | 13:12 | 38.751 | -120.7404 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101398224 | No | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-09-26 | 13:11 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221737 | PG&E | 2022-09-26 | 12:03 | 37.4223 | -121.9329 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 103449887 | No | 21000 | Switch | Overhead | Yes | 2022-09-26 | 11:53 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221731 | PG&E | 2022-09-25 | 16:48 | 35.6564 | -120.633 | Other | Communication line | Herbaceous | 0.26-9.99 Acres | Fire Agency | Paso Robles Fire Department | 101867356 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-25 | 16:45 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20221674 | PG&E | 2022-09-21 | 00:55 | 35.3673 | -119.001 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Bakersfield FD | 100248968 | No | 750 | Service Drop | Overhead | Yes | 2022-09-21 | 01:07 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221671 | PG&E | 2022-09-20 | 05:45 | 36.6111 | -119.4664 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Fresno County FD | 100832313 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-20 | 05:28 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221659 | PG&E | 2022-09-18 | 15:22 | 37.4918 | -120.5447 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101194298 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-09-18 | 15:19 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221658 | PG&E | 2022-09-18 | 12:25 | 37.3384 | -122.0071 | Other | Crossarm | Urban | Less Than .25 Acres | Fire Agency | Sunnyvale FD | 100555173 | Yes | 12000 | Crossarm | Overhead | Yes | 2022-09-18 | 12:09 | Contamination | N/A | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221649 | PG&E | 2022-09-17 | 16:00 | 38.0989 | -120.9021 | Other | Pole | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 102047735 | No | 12000 | Pole | Overhead | Yes | 2022-09-17 | 15:44 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20221641 | PG&E | 2022-09-16 | 16:15 | 39.1477 | -121.4864 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Olivehurst FD | 101308284 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-16 | 15:59 | Contact From Object | N/A | Animal | Jumper | Outside Force
20221636 | PG&E | 2022-09-16 | 05:44 | 36.6338 | -118.9957 | Other | Pole | Hardwood Forest | Less than three(3) meters of linear travel | Fire Agency | Tulare County FD | 100683665 | Yes | 12000 | Pole | Overhead | Yes | 2022-09-16 | 05:07 | Other | N/A | N/A | N/A | N/A
20221633 | PG&E | 2022-09-15 | 09:33 | 37.5323 | -121.9919 | Other | Conductor | Urban | Less Than .25 Acres | Fire Agency | Fremont FD | 100949820 | Yes | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2022-09-15 | 09:15 | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20221618 | PG&E | 2022-09-12 | 15:06 | 40.6777 | -124.2451 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 101001517 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-12 | 15:00 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221614 | PG&E | 2022-09-12 | 04:55 | 39.0416 | -120.966 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 104090590 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-12 | 04:32 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221620 | PG&E | 2022-09-12 | 16:30 | 36.94 | -121.8032 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Watsonville FD | 101693828 | Yes | 21000 | Other | Overhead | Yes | 2022-09-12 | 16:29 | Equipment/Facility Failure | Other | N/A | N/A | N/A
20221696 | PG&E | 2022-09-12 | 08:14 | 37.9737 | -122.3215 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Richmond FD | 101434649 | Yes | 750 | Other | Overhead | No | N/A | N/A | Other | N/A | N/A | N/A | N/A
20221603 | PG&E | 2022-09-11 | 07:55 | 36.8958 | -119.7904 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 103223669 | No | 21000 | Pole | Overhead | Yes | 2022-09-11 | 08:55 | Contact From Object | N/A | Animal | Pole | Outside Force
20221608 | PG&E | 2022-09-11 | 13:52 | 40.74 | -124.2008 | Other | Conductor | Urban | Structure Only | Fire Agency | Humboldt FD | 100996405 | Yes | 750 | Transformer | Overhead | Yes | 2022-09-11 | 13:44 | Other | N/A | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221600 | PG&E | 2022-09-10 | 20:14 | 37.0662 | -120.9784 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101187655 | Yes | 12000 | Pole | Overhead | Yes | 2022-09-11 | 19:52 | Contact From Object | N/A | Vehicle | Pole | N/A
20221590 | PG&E | 2022-09-10 | 03:30 | 37.5147 | -119.99 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101086335 | No | 21000 | Insulator | Overhead | Yes | 2022-09-10 | 03:25 | Contamination | N/A | N/A | N/A | N/A
20221594 | PG&E | 2022-09-10 | 17:10 | 38.4697 | -121.5629 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Clarksburg FD | 101580817 | No | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2022-09-11 | 17:00 | Other | N/A | N/A | N/A | N/A
20221592 | PG&E | 2022-09-10 | 04:44 | 38.9553 | -121.4192 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Unknown Fire Department | 43685287 | No | 60000 | Pole | Overhead | Yes | 2022-09-09 | 04:41 | Other | N/A | N/A | N/A | Weather
20221577 | PG&E | 2022-09-09 | 08:03 | 39.0507 | -121.0759 | Other | Squirrel | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 100019185 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-09 | 07:59 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221578 | PG&E | 2022-09-09 | 10:03 | 38.336 | -122.6685 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 101986402 | Yes | 12000 | Jumper | Overhead | No | N/A | N/A | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20221581 | PG&E | 2022-09-09 | 16:04 | 37.342 | -120.6327 | Other | Regulator | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE, City of Atwater FD | 103578476 | No | 12000 | Voltage Regulator | Overhead | Yes | 2022-09-09 | 15:57 | Equipment/Facility Failure | Voltage Regulator | N/A | N/A | N/A
20221567 | PG&E | 2022-09-08 | 15:01 | 38.0996 | -122.1423 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Benicia FD | 102286851 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-08 | 14:48 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221566 | PG&E | 2022-09-08 | 13:22 | 35.4648 | -120.6511 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | ATASCADERO FD | 101896293 | Yes | 12000 | Fuse | Overhead | Yes | 2022-09-08 | 13:19 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221573 | PG&E | 2022-09-08 | 19:33 | 37.4324 | -121.8717 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Milpitas FD | 100558266 | Yes | 12000 | Switch | Overhead | Yes | 2022-09-09 | 19:29 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221558 | PG&E | 2022-09-07 | 19:46 | 35.2613 | -118.8248 | Other | Capacitor Bank | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Kern County FD | 100225748 | No | 12000 | Capacitor Bank | Overhead | Yes | 2022-09-07 | 19:45 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20221550 | PG&E | 2022-09-07 | 13:18 | 37.9671 | -121.3187 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Stockton FD | 103569342 | No | 12000 | Capacitor Bank | Overhead | No | N/A | N/A | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20221548 | PG&E | 2022-09-07 | 12:10 | 37.7122 | -121.9303 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Alameda County FD | 100912671 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-09-07 | 12:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221555 | PG&E | 2022-09-07 | 17:42 | 37.2292 | -121.9988 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Santa Clara FD | 100557138 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-08 | 17:32 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221545 | PG&E | 2022-09-07 | 05:25 | 37.4547 | -121.9221 | Vegetation | N/A | Wetland | Less Than .25 Acres | Fire Agency | Milpitas FD | 103094422 | No | 21000 | Switch | Overhead | Yes | 2022-09-07 | 05:56 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221554 | PG&E | 2022-09-07 | 17:21 | 38.4168 | -121.9155 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Dixon FD | 101581941 | Yes | 12000 | Unknown | Overhead | Yes | 2022-09-07 | 17:20 | Unknown | N/A | N/A | N/A | N/A
20221547 | PG&E | 2022-09-07 | 08:56 | 38.7151 | -120.9491 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 104114542 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-09-07 | 01:51 | Other | N/A | N/A | N/A | N/A
20221538 | PG&E | 2022-09-06 | 16:26 | 37.273 | -122.023 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Cupertino FD | 100507664 | Yes | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2022-09-06 | 16:03 | Contact From Object | N/A | Animal | Conductor - Insulated Secondary | Outside Force
20221536 | PG&E | 2022-09-06 | 14:19 | 37.2116 | -121.8486 | Other | Crossarm | Urban | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 1006406320 | Yes | 21000 | Insulator | Overhead | Yes | 2022-09-06 | 14:05 | Equipment/Facility Failure | Insulator | N/A | N/A | N/A
20221542 | PG&E | 2022-09-06 | 21:11 | 36.782 | -119.6903 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Fresno FD | 100887758 | Yes | 750 | Transformer | Overhead | Yes | 2022-09-07 | 20:29 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221563 | PG&E | 2022-09-06 | 18:16 | 39.0068 | -120.7438 | Vegetation | N/A | Shrub | Greater than 5,000 Acres | Fire Agency | US Forest Service, CAL FIRE | N/A | No | 60000 | N/A | Overhead | Yes | 2022-09-06 | 18:13 | Under Investigation | N/A | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221523 | PG&E | 2022-09-05 | 14:15 | 38.3684 | -121.9622 | Other | Conductor | Urban | Less Than .25 Acres | Fire Agency | Vacaville FD | 101561414 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-09-05 | 14:02 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221525 | PG&E | 2022-09-05 | 14:31 | 38.3667 | -122.7633 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Santa Rosa FD | 101967696 | Yes | 750 | Conductor - Racked Secondary | Overhead | No | N/A | N/A | Contact From Object | N/A | Vegetation | Conductor - Racked Secondary | N/A
20221522 | PG&E | 2022-09-05 | 13:16 | 37.2802 | -121.9665 | Other | Conductor | Urban | Less than three(3) meters of linear travel | Fire Agency | Cambel FD | 100541171 | Yes | 12000 | Guy/Span Wire | Overhead | Yes | 2022-09-05 | 13:14 | Equipment/Facility Failure | Guy/Span Wire | N/A | N/A | N/A
20221514 | PG&E | 2022-09-04 | 14:50 | 38.7198 | -120.5743 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101420844 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-09-04 | 14:43 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221515 | PG&E | 2022-09-04 | 16:02 | 38.6793 | -122.881 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101977114 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-04 | 15:58 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221517 | PG&E | 2022-09-04 | 16:57 | 37.1226 | -121.6514 | Other | Conductor | Urban | Less Than .25 Acres | Fire Agency | South Santa Clara FD | 102349927 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-09-04 | 16:36 | Contact From Object | N/A | Animal | Conductor - Open Wire Secondary | Outside Force
20221506 | PG&E | 2022-09-03 | 6:06 | 39.3086 | -120.9745 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100004759 | Yes | 750 | Tree Connect | Overhead | Yes | 2022-09-03 | 05:52 | Contact From Object | N/A | Vegetation | Conductor - Service | N/A
20221499 | PG&E | 2022-09-02 | 13:02 | 39.5314 | -122.2139 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Willows FD | 100337120 | Yes | 21000 | Conductor - Primary | Overhead | No | N/A | N/A | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20221498 | PG&E | 2022-09-02 | 03:49 | 38.0019 | -122.4643 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | San Rafael FD | 102222277 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-02 | 05:00 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221533 | PG&E | 2022-09-01 | 17:56 | 37.9761 | -121.1937 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Stockton FD | 102127554 | Yes | 750 | Service Drop | Overhead | Yes | 2022-09-02 | 17:54 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221494 | PG&E | 2022-09-01 | 08:35 | 40.0758 | -122.1606 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 101543132 | Yes | 12000 | Conductor - Primary | Overhead | No | N/A | N/A | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221491 | PG&E | 2022-08-31 | 17:04 | 36.7514 | -119.6234 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100729368 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-09-01 | 16:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221492 | PG&E | 2022-08-31 | 17:13 | 35.3612 | -118.929 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Kern County FD | 100250596 | No | 21000 | Switch | Overhead | Yes | 2022-09-01 | 17:11 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221478 | PG&E | 2022-08-30 | 14:19 | 40.6597 | -122.3994 | Vegetation | N/A | Shrub | Less Than .25 Acres | Fire Agency | CAL FIRE | 101464261 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-08-30 | 14:10 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20221479 | PG&E | 2022-08-30 | 15:55 | 36.0962 | -120.4438 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100707186 | Yes | 750 | Service Drop | Overhead | Yes | 2022-08-30 | 15:35 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221473 | PG&E | 2022-08-28 | 17:14 | 37.9334 | -120.8437 | Vegetation | N/A | Herbaceous | 10-99 Acres | Fire Agency | Tuolumne County, CAL FIRE | 102343389 | No | 17000 | Pole | Overhead | Yes | 2022-08-29 | 16:53 | Contact From Object | N/A | Vehicle | Pole | N/A
20221457 | PG&E | 2022-08-26 | 07:52 | 39.02 | -120.8694 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 40874873 | No | 60000 | Conductor - Transmission | Overhead | Yes | 2022-08-26 | 7:27 | Equipment/Facility Failure | Conductor - Transmission | N/A | N/A | N/A
20221454 | PG&E | 2022-08-26 | 00:47 | 36.3429 | -119.9054 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 40775782 | No | 70000 | Conductor - Transmission | Overhead | Yes | 2022-08-26 | 00:38 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20221462 | PG&E | 2022-08-26 | 16:45 | 41.2826 | -123.5465 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | US Forest Service | 100961768 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-26 | 16:43 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221461 | PG&E | 2022-08-26 | 15:20 | 35.4993 | -118.91 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Kern County FD | 103782805 | No | 21000 | Switch | Overhead | No | N/A | N/A | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221451 | PG&E | 2022-08-25 | 12:20 | 37.491 | -120.5612 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101194050 | No | 21000 | Transformer Bushing | Overhead | Yes | 2022-08-25 | 12:18 | Contact From Object | N/A | Animal | Transformer Bushing | Outside Force
20221447 | PG&E | 2022-08-24 | 17:42 | 37.9737 | -121.3327 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Stockton FD | 102056563 | Yes | 750 | Service Drop | Overhead | Yes | 2022-08-24 | 17:41 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221448 | PG&E | 2022-08-24 | 21:27 | 37.282 | -121.7636 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 40445676 | No | 21000 | Switch | Subsurface | Yes | 2022-08-25 | 21:19 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221431 | PG&E | 2022-08-22 | 11:13 | 37.6489 | -122.12 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Hayward FD | 100929402 | Yes | 750 | Service Drop | Overhead | Yes | 2022-08-22 | 12:44 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221440 | PG&E | 2022-08-22 | 19:54 | 38.5907 | -121.8359 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 101557918 | Yes | 750 | Service Drop | Overhead | Yes | 2022-08-23 | 19:53 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221417 | PG&E | 2022-08-20 | 13:36 | 36.5362 | -121.4096 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 101769339 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-20 | 13:35 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221418 | PG&E | 2022-08-20 | 14:28 | 37.1205 | -120.4733 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 40661545 | No | 115000 | Conductor - Transmission | Overhead | Yes | 2022-08-20 | 11:46 | Contact From Object | N/A | Vehicle | Conductor - Transmission | N/A
20221419 | PG&E | 2022-08-20 | 14:53 | 36.8055 | -121.6655 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Salinas FD | 101719881 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-20 | 14:39 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221416 | PG&E | 2022-08-19 | 15:11 | 38.1162 | -122.566 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Unknown Fire Department | 40617297 | No | 12000 | Conductor - Primary | Overhead | No | N/A | N/A | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221398 | PG&E | 2022-08-17 | 07:09 | 39.8206 | -121.8691 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 100434999 | No | 12000 | Pothead | Overhead | Yes | 2022-08-17 | 06:59 | Contact From Object | N/A | Animal | Pothead | Outside Force
20221403 | PG&E | 2022-08-17 | 10:49 | 36.996 | -121.8876 | Vegetation | N/A | Conifer Forest | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 101691715 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-08-17 | 10:47 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221409 | PG&E | 2022-08-17 | 17:09 | 35.6524 | -120.6404 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Paso Robles FD | 101867453 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-17 | 16:52 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221407 | PG&E | 2022-08-17 | 13:38 | 36.9116 | -121.8005 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 101699594 | Yes | 21000 | Splice/Clamp/Connector | Overhead | Yes | 2022-08-17 | 13:33 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221385 | PG&E | 2022-08-15 | 18:09 | 40.2287 | -123.8571 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100990162 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-08-16 | 17:02 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20221381 | PG&E | 2022-08-14 | 11:46 | 35.3445 | -119.0708 | Other | Balloon | Urban | Less than three(3) meters of linear travel | Fire Agency | Bakersfield FD | 100156832 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-08-14 | 11:44 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221377 | PG&E | 2022-08-14 | 02:42 | 37.0379 | -119.5039 | Other | Vehicle | Hardwood Woodland | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100678191 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-14 | 02:34 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221375 | PG&E | 2022-08-13 | 16:30 | 37.9868 | -122.0954 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Martinez FD | 107815974 | No | 21000 | Transformer | Subsurface | Yes | 2022-08-13 | 16:28 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221372 | PG&E | 2022-08-12 | 18:18 | 38.6692 | -121.7105 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Woodland Fire Department | 101639450 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-13 | 18:17 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221367 | PG&E | 2022-08-12 | 11:58 | 36.8583 | -119.8251 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101123802 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-08-12 | 11:34 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221362 | PG&E | 2022-08-11 | 11:47 | 38.84 | -120.8731 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 104014009 | Yes | 750 | Transformer | Overhead | Yes | 2022-08-11 | 13:28 | Contact From Object | N/A | Vegetation | Transformer | N/A
20221354 | PG&E | 2022-08-10 | 08:59 | 37.7396 | -121.9463 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | San Ramon FD | 100956638 | No | 21000 | Fuse | Overhead | Yes | 2022-08-10 | 05:49 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221347 | PG&E | 2022-08-09 | 10:55 | 36.571 | -121.8054 | Vegetation | N/A | Hardwood Woodland | 0.26-9.99 Acres | Fire Agency | Monterey FD | 101777237 | Yes | 21000 | Automatic Wire Splice | Overhead | Yes | 2022-08-09 | 10:51 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20221345 | PG&E | 2022-08-09 | 09:07 | 38.2302 | -122.3434 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Napa County FD | 102282472 | Yes | 12000 | Transformer | Overhead | Yes | 2022-08-09 | 09:01 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221349 | PG&E | 2022-08-09 | 16:23 | 38.5499 | -123.1463 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101950175 | Yes | 750 | Service Drop | Overhead | Yes | 2022-08-09 | 16:25 | Other | N/A | N/A | N/A | N/A
20221343 | PG&E | 2022-08-08 | 11:34 | 37.2214 | -121.9086 | Other | Squirrel | Hardwood Woodland | Less Than .25 Acres | Fire Agency | San Jose FD | 102353541 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-08-08 | 11:02 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221337 | PG&E | 2022-08-06 | 20:27 | 38.8957 | -121.2939 | Other | Jumper | Urban | Less than three(3) meters of linear travel | Fire Agency | Lincoln FD | 40190340 | No | 12000 | Jumper | Overhead | No | N/A | N/A | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20221331 | PG&E | 2022-08-05 | 14:47 | 37.8189 | -121.5499 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Tracy FD | 102094155 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-05 | 14:08 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221335 | PG&E | 2022-08-05 | 13:33 | 35.6849 | -120.9564 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 103009198 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-05 | 13:30 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221323 | PG&E | 2022-08-04 | 18:01 | 39.0079 | -120.8588 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Foresthill FD | 100023304 | No | 750 | Service Drop | Overhead | No | N/A | N/A | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221315 | PG&E | 2022-08-03 | 11:36 | 37.5364 | -120.4999 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 44971863 | No | 12000 | Recloser | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Recloser | Outside Force
20221311 | PG&E | 2022-08-03 | 05:58 | 38.0095 | -121.3322 | Other | Crossarm | Urban | Less than three(3) meters of linear travel | Fire Agency | Metro FD | 102109591 | Yes | 750 | Crossarm | Overhead | Yes | 2022-08-03 | 05:57 | Contact From Object | N/A | Animal | Crossarm | Outside Force
20221314 | PG&E | 2022-08-03 | 11:29 | 35.2996 | -120.7065 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101850483 | No | 21000 | Splice/Clamp/Connector | Overhead | Yes | 2022-08-03 | 11:19 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221321 | PG&E | 2022-08-03 | 21:12 | 37.696 | -121.4182 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Tracy FD | 102140029 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2022-08-04 | 20:38 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20221310 | PG&E | 2022-08-02 | 18:02 | 35.2602 | -119.1711 | Other | Pole | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Kern County FD | 100163368 | No | 12000 | Pole | Overhead | Yes | 2022-08-02 | 18:02 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20221303 | PG&E | 2022-08-01 | 11:34 | 38.0423 | -121.2489 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Morada FD | 102129281 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-01 | 11:33 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20221298 | PG&E | 2022-08-01 | 00:05 | 35.4666 | -120.6501 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Atascadero FD | 101896289 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-08-01 | 00:01 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221305 | PG&E | 2022-08-01 | 16:25 | 40.1536 | -122.2755 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101525506 | Yes | 12000 | Insulator | Overhead | Yes | 2022-08-01 | 16:14 | Equipment/Facility Failure | Insulator | N/A | N/A | N/A
20221283 | PG&E | 2022-07-29 | 15:40 | 38.5605 | -121.925 | Other | Vehicle | Agricultural | Less Than .25 Acres | Fire Agency | Madison FD | 101625665 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-29 | 15:33 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20221278 | PG&E | 2022-07-28 | 13:16 | 36.9568 | -120.0953 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101137014 | Yes | 12000 | Pole | Overhead | Yes | 2022-07-28 | 13:13 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20221276 | PG&E | 2022-07-27 | 15:05 | 39.2938 | -121.3199 | Vegetation | N/A | Hardwood Woodland | 10-99 Acres | Fire Agency | CAL FIRE | 103574528 | No | 750 | Service Drop | Overhead | Yes | 2022-07-27 | 17:00 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221265 | PG&E | 2022-07-26 | 14:54 | 39.2683 | -123.7026 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102186267 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-26 | 14:50 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20221264 | PG&E | 2022-07-26 | 12:53 | 38.0575 | -122.8237 | Vegetation | N/A | Conifer Forest | Less than three(3) meters of linear travel | Fire Agency | Marin FD | 102229450 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-26 | 12:48 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221258 | PG&E | 2022-07-25 | 15:43 | 36.6827 | -119.5657 | Other | Transformer | Agricultural | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100763814 | Yes | 12000 | Transformer | Overhead | Yes | 2022-07-25 | 15:22 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221256 | PG&E | 2022-07-25 | 09:17 | 38.6438 | -122.7436 | Vegetation | N/A | Conifer Forest | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 103959977 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-07-25 | 09:11 | Other | N/A | N/A | N/A | N/A
20221235 | PG&E | 2022-07-22 | 16:51 | 35.4237 | -119.0271 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 100144754 | Yes | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2022-07-22 | 17:14 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20221234 | PG&E | 2022-07-22 | 15:58 | 36.7782 | -119.8177 | Other | Service neutral | Urban | Structure Only | Fire Agency | Fresno FD | 100858884 | Yes | 750 | Meter | Overhead | Yes | 2022-07-22 | 15:57 | Equipment/Facility Failure | Meter | N/A | N/A | N/A
20221229 | PG&E | 2022-07-21 | 17:40 | 38.0435 | -120.3983 | Other | Service neutral | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101041017 | No | 750 | Service Drop | Overhead | Yes | 2022-07-21 | 17:37 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221221 | PG&E | 2022-07-21 | 11:53 | 38.8271 | -121.2024 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Placer County FD | 100057392 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-07-21 | 11:27 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20221202 | PG&E | 2022-07-20 | 04:39 | 36.668 | -121.7787 | Other | Conductor | Urban | Less than three(3) meters of linear travel | Fire Agency | Hillcrest FD | 107336714 | No | 750 | Conductor - Insulated Secondary | Subsurface | Yes | 2022-07-20 | 04:28 | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20221208 | PG&E | 2022-07-20 | 15:30 | 38.5896 | -121.8401 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Plainfield FD | 101640076 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-20 | 15:49 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221213 | PG&E | 2022-07-20 | 18:58 | 36.6473 | -119.3865 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 100738741 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-21 | 18:56 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20221215 | PG&E | 2022-07-20 | 17:50 | 39.4472 | -121.5516 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 100393766 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-20 | 18:34 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221211 | PG&E | 2022-07-20 | 17:55 | 38.6793 | -121.9725 | Other | Transformer | Urban | Less Than .25 Acres | Fire Agency | Madison FD | 101644236 | Yes | 12000 | Transformer | Overhead | Yes | 2022-07-21 | 17:53 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221200 | PG&E | 2022-07-19 | 23:08 | 36.8788 | -121.6955 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Monterey County FD, CAL FIRE | 101710681 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-07-20 | 22:42 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221198 | PG&E | 2022-07-19 | 23:05 | 38.0005 | -121.7867 | Other | Switch | Urban | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100455662 | Yes | 21000 | Switch | Subsurface | Yes | 2022-07-19 | 22:51 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20221187 | PG&E | 2022-07-18 | 10:40 | 36.7483 | -119.8599 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno County, CAL FIRE | 100632119 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-07-18 | 10:35 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20221189 | PG&E | 2022-07-18 | 12:59 | 37.4018 | -120.6131 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 103319121 | No | 750 | Service Drop | Overhead | Yes | 2022-07-18 | 12:57 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221186 | PG&E | 2022-07-18 | 09:46 | 36.634 | -121.6988 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101724755 | No | 12000 | Jumper | Overhead | Yes | 2022-07-18 | 09:41 | Other | N/A | N/A | N/A | N/A
20221442 | PG&E | 2022-07-18 | 06:53 | 34.9594 | -118.9364 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 40595697 | No | 70000 | Pole | Overhead | Yes | 2022-07-18 | 06:53 | Other | N/A | N/A | N/A | Weather
20221179 | PG&E | 2022-07-17 | 13:06 | 38.5962 | -121.5303 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | West Sacramento FD | 101654519 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-07-17 | 12:55 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221170 | PG&E | 2022-07-16 | 13:31 | 37.8838 | -121.6231 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Contra Costa FD | 100497588 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-07-16 | 13:25 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221177 | PG&E | 2022-07-16 | 21:45 | 38.2198 | -122.5431 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101997149 | Yes | 12000 | Pole | Overhead | Yes | 2022-07-17 | 21:44 | Contact From Object | N/A | Vehicle | Pole | N/A
20221172 | PG&E | 2022-07-16 | 16:02 | 38.5956 | -121.544 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | West Sacramento FD | 101605111 | Yes | 12000 | Transformer | Overhead | Yes | 2022-07-16 | 16:00 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20221163 | PG&E | 2022-07-15 | 07:12 | 39.5296 | -121.1734 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE, U.S. Forest Service | 100396604 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-15 | 06:26 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20221145 | PG&E | 2022-07-13 | 13:25 | 36.4294 | -120.1048 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 100716472 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-13 | 13:04 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20221149 | PG&E | 2022-07-13 | 18:38 | 36.7881 | -121.665 | Vegetation | N/A | Hardwood Woodland | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 101720985 | Yes | 750 | Service Drop | Overhead | Yes | 2022-07-14 | 18:25 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221151 | PG&E | 2022-07-13 | 00:40 | 37.8701 | -122.3098 | Other | Boat | Water | Less Than .25 Acres | Fire Agency | Berkeley FD | 101451344 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-13 | 0:35 | Contact From Object | N/A | Other | Conductor - Primary | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221125 | PG&E | 2022-07-11 | 08:50 | 39.3708 | -121.4258 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Customer, CAL FIRE | 100414293 | No | 750 | Service Drop | Overhead | No | N/A | N/A | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221126 | PG&E | 2022-07-11 | 08:53 | 38.9262 | -121.4203 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Wheatland FD | 100034761 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-11 | 08:36 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221128 | PG&E | 2022-07-11 | 09:40 | 37.7833 | -122.2014 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Oakland FD | 101355164 | Yes | 12000 | Transformer | Overhead | Yes | 2022-07-11 | 09:32 | Contact From Object | N/A | Animal | Transformer | Outside Force | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221131 | PG&E | 2022-07-11 | 19:45 | 38.8133 | -121.4846 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Pleasant Grove FD | 101341532 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-07-12 | 19:39 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221124 | PG&E | 2022-07-11 | 05:16 | 39.1417 | -121.5758 | Vegetation | N/A | Water | Less Than .25 Acres | Fire Agency | Linda FD | 101312942 | Yes | 12000 | Pole | Overhead | Yes | 2022-07-11 | 05:07 | Vandalism/Theft | N/A | N/A | N/A | N/A
20221117 | PG&E | 2022-07-10 | 05:46 | 35.3362 | -119.0109 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Kern County FD | 100254416 | Yes | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2022-07-10 | 05:34 | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20221119 | PG&E | 2022-07-10 | 11:22 | 39.1181 | -123.201 | Other | Balloon | Urban | 0.26-9.99 Acres | Fire Agency | Ukiah Valley Fire Authority | 102178810 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-10 | 11:17 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221123 | PG&E | 2022-07-10 | 17:36 | 38.5253 | -121.8135 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Dixon FD | 101625782 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-11 | 17:30 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221122 | PG&E | 2022-07-10 | 16:08 | 38.6859 | -121.7677 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Woodland FD | 101601799 | Yes | 750 | Service Drop | Overhead | Yes | 2022-07-10 | 16:06 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221118 | PG&E | 2022-07-10 | 10:54 | 37.5173 | -121.9615 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fremont FD | 100945467 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-10 | 10:51 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20222191 | PG&E | 2022-07-10 | 3:20 | 38.3486 | -123.0647 | Building | N/A | Herbaceous | Unknown | Fire Agency | Bodega Bay FD | N/A | Yes | 750 | N/A | Overhead | Yes | 2022-07-10 | 03:15 | Under Investigation | N/A | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20221113 | PG&E | 2022-07-09 | 22:16 | 37.6458 | -121.7834 | Other | Balloon | Urban | Less Than .25 Acres | Fire Agency | Alameda County FD | 40742681 | No | 60000 | Conductor - Transmission | Overhead | Yes | 2022-07-10 | 21:37 | Contact From Object | N/A | Balloon | Conductor - Transmission | Outside Force
20221111 | PG&E | 2022-07-09 | 17:19 | 35.6493 | -120.6721 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 107287689 | No | 12000 | Riser | Subsurface | Yes | 2022-07-10 | 17:10 | Contact From Object | N/A | Other | Riser | Outside Force
20221107 | PG&E | 2022-07-08 | 15:30 | 39.4365 | -121.5431 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 100393970 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-08 | 15:28 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221096 | PG&E | 2022-07-07 | 12:15 | 39.0516 | -123.4061 | Vegetation | N/A | Hardwood Forest | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 102214012 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-07 | 12:06 | Other | N/A | N/A | N/A | Human Error
20221094 | PG&E | 2022-07-07 | 10:45 | 39.4853 | -121.7543 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 100360025 | Yes | 12000 | Lightning Arrestor | Overhead | Yes | 2022-07-07 | 06:35 | Contact From Object | N/A | Animal | Lightning Arrestor | Outside Force
20221100 | PG&E | 2022-07-07 | 19:15 | 39.2897 | -123.792 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102189899 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-08 | 17:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221072 | PG&E | 2022-07-05 | 12:51 | 40.1731 | -122.2241 | Building | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Red Bluff Fire Department | 101543924 | Yes | 12000 | Conductor - Primary | Subsurface | Yes | 2022-07-05 | 12:48 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20221068 | PG&E | 2022-07-05 | 05:39 | 34.9446 | -118.8733 | Other | Balloon | Agricultural | 0.26-9.99 Acres | Fire Agency | Kern County FD | 100222424 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-05 | 04:11 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221071 | PG&E | 2022-07-05 | 13:03 | 38.9259 | -122.8528 | Vegetation | N/A | Hardwood Woodland | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 102145939 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-05 | 12:58 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221086 | PG&E | 2022-07-05 | 12:14 | 36.3909 | -119.8433 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Unknown Fire Department | 100849071 | No | 750 | Splice/Clamp/Connector | Overhead | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20221070 | PG&E | 2022-07-05 | 11:45 | 36.9828 | -121.8423 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 101692320 | Yes | 21000 | Unknown | Overhead | Yes | 2022-07-05 | 11:14 | Unknown | N/A | N/A | N/A | N/A
20221053 | PG&E | 2022-07-03 | 10:39 | 37.0209 | -120.0724 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 101113556 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-03 | 10:26 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20221051 | PG&E | 2022-07-03 | 08:19 | 39.0331 | -121.6 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Linda FD | 101331625 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-07-03 | 07:03 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221052 | PG&E | 2022-07-03 | 08:33 | 38.1657 | -121.1135 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Clements FD | 102078445 | No | 21000 | Fuse | Overhead | Yes | 2022-07-03 | 08:16 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221039 | PG&E | 2022-07-02 | 06:43 | 37.7986 | -122.1499 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Oakland FD | 101347515 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-07-02 | 06:42 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221033 | PG&E | 2022-07-01 | 01:08 | 37.8567 | -120.9463 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 40765227 | No | 115000 | Conductor - Transmission | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Conductor - Transmission | Outside Force
20221034 | PG&E | 2022-07-01 | 11:30 | 38.569 | -121.9714 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Winters FD | 101565566 | No | 12000 | Fuse | Overhead | Yes | 2022-07-01 | 9:19 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20221022 | PG&E | 2022-06-29 | 13:21 | 37.3017 | -119.6488 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101020948 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-29 | 13:19 | Other | N/A | N/A | N/A | N/A
20221023 | PG&E | 2022-06-29 | 14:43 | 38.2184 | -121.2574 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 102048715 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-06-29 | 14:42 | Other | N/A | N/A | N/A | N/A
20221008 | PG&E | 2022-06-28 | 11:00 | 37.793 | -121.2547 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Manteca FD | 43249284 | No | 115000 | Insulator | Overhead | Yes | 2022-06-28 | 09:50 | Contact From Object | N/A | Animal | Insulator | Outside Force
20221220 | PG&E | 2022-06-28 | 15:10 | 37.2567 | -121.805 | Other | Balloon | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100601590 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-28 | 15:08 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20221014 | PG&E | 2022-06-28 | 19:52 | 35.4279 | -120.6343 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 103155578 | Yes | 12000 | Voltage Regulator | Overhead | Yes | 2022-06-28 | 21:02 | Equipment/Facility Failure | Voltage Regulator | N/A | N/A | N/A
20220999 | PG&E | 2022-06-27 | 00:05 | 37.2822 | -122.0379 | Building | N/A | Hardwood Woodland | Less than three(3) meters of linear travel | Fire Agency | Santa Clara County FD | 100533000 | No | 750 | Service Drop | Overhead | Yes | 2022-06-26 | 23:44 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20221005 | PG&E | 2022-06-27 | 20:41 | 37.1247 | -120.2692 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Chowchilla FD | 101130968 | Yes | 750 | Service Drop | Overhead | Yes | 2022-06-28 | 21:33 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20221002 | PG&E | 2022-06-27 | 14:55 | 36.7551 | -121.6554 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 103948244 | Yes | 12000 | Pole | Overhead | Yes | 2022-06-27 | 14:46 | Contact From Object | N/A | Vehicle | Pole | N/A
20220993 | PG&E | 2022-06-26 | 19:13 | 38.7456 | -121.3176 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Placer County Fire Department | 100063870 | No | 750 | Service Drop | Overhead | Yes | 2022-06-27 | 19:10 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20220994 | PG&E | 2022-06-26 | 21:36 | 37.8384 | -121.0049 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 102329498 | No | 17000 | Fuse | Overhead | Yes | 2022-06-27 | 21:14 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20220991 | PG&E | 2022-06-26 | 14:47 | 38.3793 | -122.0006 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Vacaville FD | 101597936 | Yes | 12000 | Fuse | Overhead | Yes | 2022-06-26 | 14:45 | Other | N/A | N/A | N/A | N/A
20220977 | PG&E | 2022-06-25 | 06:33 | 36.2095 | -120.2744 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100715494 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-25 | 06:07 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220982 | PG&E | 2022-06-25 | 15:44 | 37.1231 | -122.0106 | Vegetation | N/A | Conifer Forest | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 103897338 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-25 | 15:24 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220981 | PG&E | 2022-06-25 | 12:34 | 37.1986 | -121.9954 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Santa Clara County FD, CAL FIRE | 100552641 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-25 | 12:24 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220976 | PG&E | 2022-06-25 | 05:58 | 36.9303 | -121.4118 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Hollister FD | 101717976 | No | 21000 | Pole | Overhead | Yes | 2022-06-25 | 05:52 | Contact From Object | N/A | Vehicle | Pole | N/A
20220974 | PG&E | 2022-06-24 | 18:06 | 35.2015 | -118.8377 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 100147704 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-25 | 17:01 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220980 | PG&E | 2022-06-24 | 15:52 | 38.9042 | -123.2722 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102203721 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-24 | 15:35 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220968 | PG&E | 2022-06-24 | 12:50 | 36.5036 | -119.1844 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Tulare County FD | 100705243 | Yes | 12000 | Pole | Overhead | Yes | 2022-06-24 | 12:46 | Contact From Object | N/A | Vegetation | Pole | N/A
20220973 | PG&E | 2022-06-24 | 18:01 | 39.0453 | -123.1508 | Vegetation | N/A | Barren/Other | Less Than .25 Acres | Fire Agency | CAL FIRE | 102192499 | No | 12000 | Jumper | Overhead | No | N/A | N/A | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20220971 | PG&E | 2022-06-24 | 17:26 | 37.2966 | -120.486 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Merced FD | 101157009 | Yes | 21000 | Transformer | Overhead | Yes | 2022-06-25 | 17:24 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20220948 | PG&E | 2022-06-23 | 09:40 | 36.791 | -121.6332 | Vegetation | N/A | Hardwood Woodland | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101709181 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-23 | 09:37 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220954 | PG&E | 2022-06-23 | 14:00 | 38.4242 | -121.9776 | Other | Pole | Urban | 10-99 Acres | Fire Agency | CAL FIRE | 103692242 | No | 12000 | Pole | Overhead | Yes | 2022-06-23 | 13:56 | Contact From Object | N/A | Vehicle | Pole | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220962 | PG&E | 2022-06-23 | 22:37 | 38.6636 | -121.9043 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Madison FD | 101639773 | No | 12000 | Transformer Bushing | Overhead | No | N/A | N/A | Contact From Object | N/A | Vehicle | Transformer Bushing | N/A
20220959 | PG&E | 2022-06-23 | 17:17 | 38.9253 | -121.2617 | Other | Secondary connector | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100038092 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-06-24 | 17:04 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220953 | PG&E | 2022-06-23 | 13:15 | 37.301 | -121.9328 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100590373 | Yes | 12000 | Pole | Overhead | Yes | 2022-06-23 | 12:45 | Equipment/Facility Failure | Pole | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220927 | PG&E | 2022-06-22 | 09:19 | 34.8585 | -120.4203 | Other | Balloon | Urban | Less than three(3) meters of linear travel | Fire Agency | Orcutt FD | 101858036 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-22 | 09:18 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220942 | PG&E | 2022-06-22 | 17:50 | 37.3305 | -120.5273 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101160103 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-23 | 17:44 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220930 | PG&E | 2022-06-22 | 08:06 | 36.9307 | -119.7546 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 101121487 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-22 | 08:05 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220935 | PG&E | 2022-06-22 | 11:13 | 36.5072 | -119.5886 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Kingsburg Fire Department | 104119730 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-22 | 11:02 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20221754 | PG&E | 2022-06-22 | 06:57 | 36.8634 | -119.6022 | Vegetation | N/A | Agricultural | 10-99 Acres | Fire Agency | Unknown Fire Department | 40748489, 40807014, 40806744, 40818599, 40859602, 40859524, 44076445, 40582969,40652057, 40651754 ,40761990, 40807016, 40806746 | No | 115000 | Conductor - Transmission | Overhead | Yes | 2022-06-22 | 07:07 | Equipment/Facility Failure | Conductor - Transmission | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220915 | PG&E | 2022-06-21 | 12:16 | 36.763 | -119.6347 | Other | Fuse Cut Out | Agricultural | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100780819 | Yes | 12000 | Fuse | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Fuse | Outside Force
20220917 | PG&E | 2022-06-21 | 12:45 | 35.3087 | -119.2524 | Other | Nest | Agricultural | Less Than .25 Acres | Fire Agency | County FD | 100197175 | Yes | 12000 | Insulator | Overhead | Yes | 2022-06-21 | 13:27 | Contact From Object | N/A | Animal | Insulator | Outside Force
20220920 | PG&E | 2022-06-21 | 18:05 | 37.5353 | -121.9846 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fremont FD | 100958822 | Yes | 750 | Guy/Span Wire | Overhead | Yes | 2022-06-21 | 19:17 | Equipment/Facility Failure | Guy/Span Wire | N/A | N/A | N/A
20220919 | PG&E | 2022-06-21 | 14:52 | 37.3509 | -121.8642 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | San Jose FD | 100572368 | No | 12000 | Pole | Overhead | Yes | 2022-06-21 | 14:35 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20220918 | PG&E | 2022-06-21 | 14:46 | 37.4616 | -122.2773 | Vegetation | N/A | Urban | 10-99 Acres | Fire Agency | CAL FIRE | N/A | No | 60000 | N/A | Overhead | Yes | 2022-06-21 | 14:20 | Under Investigation | N/A | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220906 | PG&E | 2022-06-20 | 13:45 | 36.4713 | -121.4687 | Vegetation | N/A | Barren/Other | Less Than .25 Acres | Fire Agency | CAL FIRE | 101744843 | Yes | 750 | Service Drop | Overhead | No | N/A | N/A | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220911 | PG&E | 2022-06-20 | 20:41 | 38.0308 | -121.2267 | Other | Solar Panels | Agricultural | Structure Only | Fire Agency | Waterloo FD | 102131342 | No | 750 | Service Drop | Overhead | Yes | 2022-06-21 | 20:33 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20220950 | PG&E | 2022-06-18 | 17:33 | 37.9142 | -122.3757 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Contra Costa FD | 101437031 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-18 | 17:30 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220876 | PG&E | 2022-06-17 | 03:59 | 39.9827 | -122.1767 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Corning FD, CAL FIRE | 101540811 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-17 | 03:48 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220878 | PG&E | 2022-06-17 | 07:00 | 37.5145 | -122.0125 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Fremont FD | 100946552 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-17 | 06:55 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220871 | PG&E | 2022-06-16 | 18:52 | 38.5308 | -121.6291 | Vegetation | N/A | Herbaceous | 10-99 Acres | Fire Agency | Davis FD | 101593098 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-17 | 19:29 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20221236 | PG&E | 2022-06-16 | 12:55 | 37.324 | -122.382 | Other | Conductor | Shrub | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100320488 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-16 | 12:51 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220868 | PG&E | 2022-06-16 | 15:10 | 39.7131 | -121.7774 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Chico FD, CAL FIRE | 100438017 | Yes | 12000 | Guy/Span Wire | Overhead | Yes | 2022-06-16 | 14:57 | Contact From Object | N/A | Vehicle | Guy/Span Wire | N/A
20220860 | PG&E | 2022-06-15 | 15:10 | 39.4643 | -121.5927 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100360028 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-15 | 15:08 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220859 | PG&E | 2022-06-15 | 10:32 | 37.424 | -120.6676 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Merced County Fire Department | 104034479 | No | 750 | Service Drop | Overhead | No | N/A | N/A | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220858 | PG&E | 2022-06-15 | 06:29 | 36.9287 | -121.3896 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | Hollister FD | 101774147 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-15 | 06:11 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220848 | PG&E | 2022-06-14 | 09:12 | 37.0462 | -121.9401 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101796504 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-14 | 09:05 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220854 | PG&E | 2022-06-14 | 00:04 | 36.6767 | -120.0054 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100639204 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-13 | 23:27 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220851 | PG&E | 2022-06-14 | 10:35 | 38.0288 | -122.1174 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Contra Costa County FD, CAL FIRE | 103316597 | Yes | 21000 | Automatic Wire Splice | Overhead | Yes | 2022-06-14 | 10:32 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20220842 | PG&E | 2022-06-13 | 06:35 | 34.8937 | -120.3194 | Other | Crossarm | Barren/Other | 0.26-9.99 Acres | Fire Agency | Santa Barbara County FD | 101861834 | Yes | 12000 | Crossarm | Overhead | Yes | 2022-06-13 | 05:54 | Contamination | N/A | N/A | N/A | N/A
20220834 | PG&E | 2022-06-12 | 03:04 | 35.3197 | -119.0279 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Bakersfield FD | 100252514 | No | 21000 | Common Neutral | Overhead | Yes | 2022-06-12 | 08:58 | Contact From Object | N/A | Vegetation | Common Neutral | N/A
20220832 | PG&E | 2022-06-11 | 16:28 | 40.1334 | -122.2061 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 101537668 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-11 | 16:02 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220824 | PG&E | 2022-06-11 | 01:16 | 38.4355 | -121.8411 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Dixon FD | 101597383 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-06-11 | 00:50 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220827 | PG&E | 2022-06-11 | 07:31 | 38.6695 | -121.7484 | Building | N/A | Urban | Structure Only | Fire Agency | Woodland FD | 107978263 | No | 750 | Service Drop | Subsurface | Yes | 2022-06-11 | 07:05 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220853 | PG&E | 2022-06-10 | 07:55 | 36.684 | -119.7386 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno County FD | 100809595 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-10 | 07:49 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220816 | PG&E | 2022-06-10 | 16:06 | 37.0411 | -121.7195 | Vegetation | N/A | Hardwood Woodland | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100609688 | No | 4000 | Conductor - Primary | Overhead | Yes | 2022-06-10 | 16:05 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220815 | PG&E | 2022-06-10 | 14:49 | 39.0174 | -123.1726 | Vegetation | N/A | Hardwood Forest | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 103593475 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-10 | 14:42 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220819 | PG&E | 2022-06-10 | 16:57 | 37.1686 | -122.3582 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 100320895 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-10 | 16:38 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220810 | PG&E | 2022-06-10 | 12:46 | 36.2243 | -121.066 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101729038 | No | 12000 | Tie Wire | Overhead | Yes | 2022-06-10 | 12:40 | Equipment/Facility Failure | Tie Wire | N/A | N/A | N/A
20220801 | PG&E | 2022-06-09 | 11:03 | 38.5535 | -121.7522 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Davis FD | 101650173 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-09 | 11:00 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220792 | PG&E | 2022-06-08 | 12:37 | 35.3571 | -118.9858 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Bakersfield FD | 100147271 | Yes | 21000 | Transformer | Overhead | Yes | 2022-06-08 | 12:31 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20220795 | PG&E | 2022-06-08 | 15:19 | 36.086 | -119.5645 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kings County FD | 100711316 | No | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-06-08 | 17:37 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220787 | PG&E | 2022-06-07 | 14:22 | 37.6567 | -121.4827 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 102068072 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-07 | 14:05 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220785 | PG&E | 2022-06-07 | 09:52 | 35.2833 | -119.6168 | Vegetation | N/A | Desert Shrub | 0.26-9.99 Acres | Fire Agency | Kern County FD | 100236744 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-07 | 09:51 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220789 | PG&E | 2022-06-07 | 21:19 | 36.7541 | -119.7982 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno Fire Department | 100864962 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-08 | 21:16 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220786 | PG&E | 2022-06-07 | 12:00 | 37.5125 | -122.3268 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100269256 | Yes | 12000 | Unknown | Overhead | Yes | 2022-06-07 | 11:50 | Unknown | N/A | N/A | N/A | N/A
20220777 | PG&E | 2022-06-06 | 14:54 | 38.6356 | -120.605 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101399032 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-06-06 | 14:13 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220754 | PG&E | 2022-06-04 | 00:27 | 35.2722 | -120.6728 | Other | Pole | Shrub | Less Than .25 Acres | Fire Agency | San Luis Obispo FD | 101927702 | No | 12000 | Pole | Overhead | Yes | 2022-06-04 | 00:54 | Contamination | N/A | N/A | N/A | N/A
20220746 | PG&E | 2022-06-03 | 07:32 | 38.0155 | -121.8086 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Unknown Fire Department | 103909634 | No | 750 | Service Drop | Overhead | No | N/A | N/A | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220750 | PG&E | 2022-06-03 | 14:21 | 38.952 | -121.4369 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Pleasant Grove FD | 101292442 | No | 12000 | Pole | Overhead | Yes | 2022-06-03 | 14:50 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20220753 | PG&E | 2022-06-03 | 22:13 | 36.9093 | -121.8011 | Other | Crossarm | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 101792848 | Yes | 21000 | Crossarm | Overhead | Yes | 2022-06-04 | 21:13 | Contamination | N/A | N/A | N/A | N/A
20220735 | PG&E | 2022-06-01 | 14:04 | 38.9709 | -123.1189 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | Hopland FD | 104001434 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-01 | 13:55 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220724 | PG&E | 2022-05-31 | 20:17 | 39.1543 | -121.0667 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Nevada County Consolidated Department | 103821736 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-06-01 | 19:45 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220707 | PG&E | 2022-05-28 | 15:13 | 38.8434 | -121.2163 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 103804151 | No | 12000 | Transformer Bushing | Overhead | Yes | 2022-05-28 | 15:11 | Contact From Object | N/A | Animal | Transformer Bushing | Outside Force
20220732 | PG&E | 2022-05-28 | 17:54 | 39.4136 | -121.6582 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100377256 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-28 | 17:48 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220698 | PG&E | 2022-05-27 | 05:27 | 39.5514 | -121.8061 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 100440013 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-27 | 05:19 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220703 | PG&E | 2022-05-27 | 22:42 | 38.7153 | -122.9186 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Geyserville FD | 101957306 | No | 12000 | Transformer | Overhead | Yes | 2022-05-28 | 22:37 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20220688 | PG&E | 2022-05-26 | 10:31 | 37.362 | -121.8637 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100573548 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-26 | 10:24 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220687 | PG&E | 2022-05-26 | 09:01 | 39.5041 | -121.6283 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 100357190 | No | 750 | Service Drop | Overhead | Yes | 2022-05-26 | 08:59 | Contact From Object | N/A | Vegetation | Service Drop | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220685 | PG&E | 2022-05-26 | 07:59 | 36.8789 | -121.6935 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101710680 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-05-26 | 07:57 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220673 | PG&E | 2022-05-25 | 18:25 | 37.5948 | -122.3791 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Burlingame FD | 103984030 | No | 12000 | Fuse | Overhead | No | N/A | N/A | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20220670 | PG&E | 2022-05-24 | 20:54 | 37.8207 | -122.2686 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Oakland FD | 101364919 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-25 | 20:47 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220663 | PG&E | 2022-05-24 | 11:34 | 38.8344 | -121.3869 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 100053234 | No | 750 | Service Drop | Overhead | Yes | 2022-05-24 | 10:59 | Contact From Object | N/A | Vehicle | Service Drop | N/A
20220659 | PG&E | 2022-05-23 | 11:10 | 34.6308 | -120.1454 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 101920929 | Yes | 12000 | Jumper | Overhead | Yes | 2022-05-23 | 09:00 | Other | N/A | N/A | N/A | Human Error
20220654 | PG&E | 2022-05-23 | 14:53 | 37.7715 | -121.8282 | Vegetation | N/A | Urban | 10-99 Acres | Fire Agency | Alameda County FD | 100899076 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-05-23 | 14:48 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220653 | PG&E | 2022-05-23 | 07:53 | 35.3516 | -119.0135 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Bakersfield FD | 100244707 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-05-23 | 07:50 | Contact From Object | N/A | Balloon | Splice/Clamp/Connector | Outside Force
20220657 | PG&E | 2022-05-23 | 17:27 | 38.5109 | -122.4524 | Vegetation | N/A | Shrub | 0.26-9.99 Acres | Fire Agency | St Helena FD, CAL FIRE | 102242543 | Yes | 21000 | Chance Clamp | Overhead | Yes | 2022-05-24 | 17:17 | Contact From Object | N/A | Vehicle | Chance Clamp | N/A
20220650 | PG&E | 2022-05-21 | 17:49 | 35.3413 | -119.166 | Other | Pole | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Bakersfield FD | 103901138 | No | 750 | Splice/Clamp/Connector | Overhead | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220642 | PG&E | 2022-05-20 | 05:18 | 39.4311 | -121.0727 | Vegetation | N/A | Conifer Forest | 10-99 Acres | Fire Agency | US Forest Service | 104067158 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-20 | 05:12 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220643 | PG&E | 2022-05-20 | 14:49 | 38.8741 | -123.6575 | Vegetation | N/A | Conifer Forest | 10-99 Acres | Fire Agency | CAL FIRE | 102180089 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-20 | 14:43 | Contact From Object | N/A | Vegetation | Conductor - Primary | Weather
20220640 | PG&E | 2022-05-20 | 09:13 | 39.0192 | -121.8229 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Grimes FD | 101604505 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-20 | 08:53 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220644 | PG&E | 2022-05-20 | 14:50 | 38.87 | -121.7033 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Robbins Volunteer FD | 103687940 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-05-20 | 16:39 | Contact From Object | N/A | Vegetation | Splice/Clamp/Connector | N/A
20220637 | PG&E | 2022-05-20 | 07:16 | 39.158 | -121.8195 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Sutter County FD | 101305724 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-20 | 06:31 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220626 | PG&E | 2022-05-19 | 12:55 | 39.9965 | -123.928 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100984733 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-19 | 12:47 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220630 | PG&E | 2022-05-19 | 16:56 | 36.849 | -121.6792 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101712796 | Yes | 750 | Conductor - Racked Secondary | Overhead | Yes | 2022-05-19 | 15:02 | Contact From Object | N/A | Vegetation | Conductor - Racked Secondary | N/A
20220627 | PG&E | 2022-05-19 | 14:33 | 38.6922 | -122.0392 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Esparto FD, Yoche Dehee FD, CAL FIRE | 103574471 | No | 21000 | Pole | Overhead | Yes | 2022-05-19 | 14:25 | Contact From Object | N/A | Vehicle | Pole | N/A
20220621 | PG&E | 2022-05-18 | 16:47 | 38.2431 | -122.0007 | Other | Underground splice | Urban | Less Than .25 Acres | Fire Agency | Suisun City Fire Department | 108120519 | No | 21000 | Splice/Clamp/Connector | Subsurface | Yes | 2022-05-18 | 16:42 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220623 | PG&E | 2022-05-18 | 15:26 | 36.7967 | -119.4248 | Vegetation | N/A | Agricultural | 10-99 Acres | Fire Agency | Fresno County FD | 40806889 | No | 115000 | Insulator | Overhead | Yes | 2022-05-18 | 15:28 | Contamination | N/A | N/A | N/A | N/A
20220618 | PG&E | 2022-05-18 | 08:54 | 37.705 | -121.5313 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Tracy FD | 102068155 | No | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-05-18 | 08:53 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220615 | PG&E | 2022-05-17 | 14:39 | 39.4544 | -121.7262 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 40660158 | No | 500000 | Other | Overhead | No | N/A | N/A | Contact From Object | N/A | Vehicle | Other | Human Error
20220613 | PG&E | 2022-05-17 | 13:46 | 37.9854 | -122.5658 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Ross Valley FD | 102242348 | Yes | 750 | Splice/Clamp/Connector | Overhead | Yes | 2022-05-17 | 13:45 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220609 | PG&E | 2022-05-16 | 18:18 | 38.7606 | -120.8862 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101378743 | Yes | 21000 | Recloser | Overhead | Yes | 2022-05-17 | 01:05 | Contact From Object | N/A | Animal | Recloser | Outside Force
20220608 | PG&E | 2022-05-16 | 16:17 | 35.3765 | -118.9507 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 100218002 | Yes | 12000 | Pole | Overhead | No | N/A | N/A | Contact From Object | N/A | Other | Pole | Outside Force
20220937 | PG&E | 2022-05-15 | 20:23 | 40.3677 | -122.2922 | Other | Capacitor Bank | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101507520 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2022-05-15 | 20:01 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20220599 | PG&E | 2022-05-15 | 16:45 | 38.2142 | -121.9771 | Vegetation | N/A | Herbaceous | 10-99 Acres | Fire Agency | Suisun FD | 103572239 | No | 21000 | Pothead | Overhead | Yes | 2022-05-15 | 16:09 | Contact From Object | N/A | Animal | Pothead | Outside Force
20220595 | PG&E | 2022-05-15 | 14:31 | 36.7851 | -119.934 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 100627289 | Yes | 750 | Service Drop | Overhead | Yes | 2022-05-15 | 14:30 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220592 | PG&E | 2022-05-14 | 23:44 | 36.6846 | -119.666 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno County FD | 100771916 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-15 | 00:57 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220588 | PG&E | 2022-05-13 | 17:32 | 37.2225 | -120.6584 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101071257 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-13 | 16:05 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220585 | PG&E | 2022-05-13 | 13:47 | 37.6811 | -121.8574 | Other | Insulator | Urban | 0.26-9.99 Acres | Fire Agency | Livermore Pleasanton FD | 100910253 | Yes | 21000 | Insulator | Overhead | Yes | 2022-05-13 | 13:42 | Contact From Object | N/A | Animal | Insulator | Outside Force
20220583 | PG&E | 2022-05-12 | 21:25 | 38.7789 | -122.1638 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Capay Valley FD | 101609296 | No | 21000 | Conductor - Primary | Overhead | Yes | 2022-05-13 | 21:16 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220574 | PG&E | 2022-05-11 | 13:20 | 36.6765 | -121.7868 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Marina FD | 101715041 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-05-11 | 13:14 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220576 | PG&E | 2022-05-11 | 16:32 | 34.6194 | -120.1048 | Vegetation | N/A | Agricultural | 0.26-9.99 Acres | Fire Agency | Santa Barbara FD | 101903915 | Yes | 750 | Service Drop | Overhead | Yes | 2022-05-11 | 16:17 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220568 | PG&E | 2022-05-09 | 16:05 | 39.509 | -121.3363 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100380643 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-09 | 16:42 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220559 | PG&E | 2022-05-07 | 14:21 | 36.6497 | -119.718 | Other | Mylar Balloon | Agricultural | 0.26-9.99 Acres | Fire Agency | Fresno County FD | 100785824 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-07 | 14:16 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220558 | PG&E | 2022-05-07 | 13:48 | 39.4686 | -121.5633 | Other | Tent | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 100359728 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-07 | 14:11 | Contact From Object | N/A | Other | Conductor - Primary | Outside Force
20220551 | PG&E | 2022-05-05 | 15:53 | 37.7048 | -121.2338 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Manteca FD | 102069366 | Yes | 17000 | Conductor - Primary | Overhead | Yes | 2022-05-05 | 15:46 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220547 | PG&E | 2022-05-05 | 03:58 | 36.5691 | -119.7864 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 100784690 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-05-05 | 03:41 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20220546 | PG&E | 2022-05-04 | 20:38 | 36.7679 | -119.7571 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Fresno FD | 100853949 | Yes | 750 | Service Drop | Overhead | Yes | 2022-05-05 | 20:36 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20220541 | PG&E | 2022-05-04 | 16:40 | 37.7175 | -121.1629 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Ripon FD | 102068832 | No | 17000 | Conductor - Primary | Overhead | Yes | 2022-05-04 | 16:34 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220538 | PG&E | 2022-05-04 | 15:38 | 40.4945 | -122.2986 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 103644732 | No | 12000 | Pole | Overhead | Yes | 2022-05-04 | 15:44 | Contact From Object | N/A | Vehicle | Pole | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220536 | PG&E | 2022-05-03 | 01:33 | 38.8238 | -121.4882 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | Placer County FD | 101340576 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-03 | 01:08 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220531 | PG&E | 2022-05-02 | 16:31 | 39.2978 | -121.0259 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | Nevada County Consolidated Fire District | 104007214 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-02 | 16:30 | Other | N/A | N/A | N/A | Human Error
20220530 | PG&E | 2022-05-02 | 16:01 | 37.2285 | -120.2541 | Building | N/A | Urban | Structure Only | Fire Agency | Merced County Fire Department | 107137721 | No | 750 | Service Drop | Subsurface | Yes | 2022-05-02 | 15:59 | Other | N/A | N/A | N/A | Human Error
20220532 | PG&E | 2022-05-02 | 20:40 | 37.7535 | -121.4741 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Tracy City FD | 103111038 | No | 750 | Pole | Overhead | Yes | 2022-05-03 | 20:39 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20220521 | PG&E | 2022-05-01 | 09:20 | 38.2418 | -122.4644 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Sonoma Valley FD | 101998952 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-05-01 | 09:16 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220522 | PG&E | 2022-05-01 | 21:24 | 38.2867 | -122.0031 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | Fairfield FD | 103948325 | No | 21000 | Fuse | Overhead | Yes | 2022-05-02 | 21:00 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20220517 | PG&E | 2022-04-30 | 16:14 | 38.1552 | -122.2494 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Vallejo FD | 102243672 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-30 | 16:07 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220526 | PG&E | 2022-04-30 | 10:35 | 37.1901 | -121.0993 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 40595212 | No | 500000 | Conductor - Transmission | Overhead | Yes | 2022-04-30 | 10:31 | Equipment/Facility Failure | Conductor - Transmission | N/A | N/A | N/A
20220502 | PG&E | 2022-04-27 | 15:21 | 38.2101 | -122.1437 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Cordelia FD | 103125543 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-27 | 14:31 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220500 | PG&E | 2022-04-27 | 12:39 | 38.9066 | -122.66 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102156992 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-27 | 12:29 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20220503 | PG&E | 2022-04-27 | 15:46 | 34.9164 | -120.5166 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101898097 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-27 | 15:11 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220483 | PG&E | 2022-04-23 | 14:51 | 40.0886 | -123.7891 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100988966 | Yes | 12000 | Insulator | Overhead | Yes | 2022-04-23 | 13:20 | Contact From Object | N/A | Animal | Insulator | Outside Force
20220462 | PG&E | 2022-04-21 | 15:11 | 37.2851 | -120.7785 | Other | Nest | Wetland | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 103952997 | No | 12000 | Transformer | Overhead | Yes | 2022-04-21 | 15:11 | Contact From Object | N/A | Animal | Transformer | Outside Force
20220458 | PG&E | 2022-04-20 | 15:01 | 35.5114 | -120.6332 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE, Templeton FD | 101887140 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-04-20 | 14:57 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220452 | PG&E | 2022-04-19 | 08:47 | 36.6276 | -119.5208 | Other | Insulator | Agricultural | Less Than .25 Acres | Fire Agency | Fresno County FD | 42738226 | Yes | 115000 | Conductor - Transmission | Overhead | Yes | 2022-04-19 | 05:38 | Contact From Object | N/A | Balloon | Conductor - Transmission | Outside Force
20220453 | PG&E | 2022-04-19 | 02:17 | 36.7134 | -119.8529 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Fresno FD | 100655619 | No | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-04-19 | 02:07 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20220450 | PG&E | 2022-04-18 | 18:17 | 39.5665 | -120.7099 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | Sierra City FD | 100111818 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2022-04-18 | 18:09 | Other | N/A | N/A | N/A | N/A
20220440 | PG&E | 2022-04-16 | 17:38 | 37.9089 | -120.6234 | Other | Conductor | Herbaceous | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101283568 | No | 17000 | Conductor - Primary | Overhead | Yes | 2022-04-16 | 17:34 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220438 | PG&E | 2022-04-15 | 20:04 | 38.1464 | -120.8613 | Other | Pole | Herbaceous | Less Than .25 Acres | Fire Agency | Calaveras Consolidated FD | 101247735 | Yes | 60000 | Pole | Overhead | Yes | 2022-04-15 | 19:15 | Contact From Object | N/A | Vehicle | Pole | N/A
20220431 | PG&E | 2022-04-14 | 15:54 | 34.5143 | -120.2199 | Other | Conductor | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Santa Barbara County FD | 101920768 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-14 | 15:43 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220427 | PG&E | 2022-04-13 | 11:09 | 38.7833 | -121.1734 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 100059587 | Yes | 12000 | Jumper | Overhead | Yes | 2022-04-13 | 11:06 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20220423 | PG&E | 2022-04-12 | 12:38 | 39.8089 | -121.8527 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Chico FD | 103344425 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-12 | 12:37 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220412 | PG&E | 2022-04-11 | 13:29 | 37.5459 | -122.0318 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Fremont FD | 100941651 | Yes | 750 | Service Drop | Overhead | Yes | 2022-04-11 | 16:51 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220413 | PG&E | 2022-04-11 | 12:14 | 39.733 | -121.8203 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Chico FD | 103655098 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-11 | 12:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220410 | PG&E | 2022-04-11 | 11:14 | 38.348 | -122.4984 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Sonoma Valley Fire Rescue FD | 102035508 | No | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-04-11 | 11:11 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20220417 | PG&E | 2022-04-11 | 21:16 | 38.5367 | -122.8347 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Windsor FD | 103143144 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-12 | 21:08 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220403 | PG&E | 2022-04-10 | 15:36 | 37.4414 | -121.91 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Milpitas FD | 100559572 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-04-10 | 15:34 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20220404 | PG&E | 2022-04-10 | 16:22 | 37.6641 | -122.4907 | Vegetation | N/A | Urban | 0.26-9.99 Acres | Fire Agency | San Mateo County FD | 100309063 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-04-10 | 16:18 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20220406 | PG&E | 2022-04-10 | 18:12 | 38.3887 | -122.6903 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Adobe FD | 101969010 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2022-04-11 | 18:10 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220400 | PG&E | 2022-04-09 | 23:53 | 36.9411 | -119.906 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101215411 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-10 | 23:35 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220395 | PG&E | 2022-04-09 | 13:23 | 40.9059 | -124.0645 | Vegetation | N/A | Conifer Forest | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 100973820 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-09 | 13:53 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220398 | PG&E | 2022-04-09 | 17:12 | 39.4481 | -123.7497 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102191786 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-10 | 16:51 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220397 | PG&E | 2022-04-09 | 17:08 | 39.0983 | -121.6535 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Yuba City FD | 101301023 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2022-04-10 | 17:02 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | N/A
20220399 | PG&E | 2022-04-09 | 20:35 | 38.1183 | -121.7089 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Montezuma FD | 101567309 | No | 750 | Service Drop | Overhead | Yes | 2022-04-09 | 20:35 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20220394 | PG&E | 2022-04-09 | 10:48 | 39.348 | -121.7447 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Gridley FD | 100379130 | No | 12000 | Pole | Overhead | Yes | 2022-04-09 | 09:41 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20220420 | PG&E | 2022-04-09 | 17:42 | 39.7147 | -121.8058 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 100346073 | Yes | 12000 | Transformer | Overhead | Yes | 2022-04-09 | 17:10 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20220383 | PG&E | 2022-04-08 | 05:36 | 39.9608 | -122.1784 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101540914 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-08 | 05:35 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220389 | PG&E | 2022-04-08 | 17:06 | 37.9747 | -121.2612 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Stockton FD | 103671984 | No | 750 | Service Drop | Overhead | Yes | 2022-04-09 | 17:04 | Contact From Object | N/A | Vegetation | Service Drop | N/A
20220379 | PG&E | 2022-04-07 | 21:40 | 39.2031 | -121.0894 | Vegetation | N/A | Conifer Forest | Less than three(3) meters of linear travel | Fire Agency | Grass Valley FD | 100107982 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-08 | 21:10 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220378 | PG&E | 2022-04-07 | 16:42 | 40.3939 | -122.4071 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101482214 | Yes | 12000 | Insulator | Overhead | Yes | 2022-04-07 | 16:36 | Equipment/Facility Failure | Insulator | N/A | N/A | N/A
20220374 | PG&E | 2022-04-06 | 08:40 | 35.0112 | -120.4619 | Other | Cardboard Boxes/Farming Equipment | Agricultural | 0.26-9.99 Acres | Fire Agency | CAL FIRE | 101894229 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-04-06 | 09:05 | Wire-Wire Contact | N/A | N/A | N/A | Weather | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220373 | PG&E | 2022-04-05 | 16:14 | 36.9301 | -119.7542 | Vegetation | N/A | Hardwood Woodland | 0.26-9.99 Acres | Fire Agency | Madera City FD, CAL FIRE | 101121486 | No | 21000 | Lightning Arrestor | Overhead | Yes | 2022-04-05 | 00:20 | Contact From Object | N/A | Balloon | Lightning Arrestor | Outside Force
20220362 | PG&E | 2022-04-03 | 12:04 | 37.7973 | -121.2756 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | Lathrop FD | 103107394 | No | 17000 | Bushing Mounted Cutout | Overhead | No | N/A | N/A | Equipment/Facility Failure | Bushing Mounted Cutout | N/A | N/A | N/A
20220361 | PG&E | 2022-04-01 | 23:12 | 37.4772 | -122.2014 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Redwood City FD, Menlo FD | 100298169 | Yes | 12000 | Crossarm | Overhead | Yes | 2022-04-02 | 23:21 | Contamination | N/A | N/A | N/A | N/A
20220351 | PG&E | 2022-03-29 | 15:04 | 38.2576 | -122.0192 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Suisun FD | 101559854 | No | 750 | Conductor - Insulated Secondary | Overhead | No | N/A | N/A | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20220331 | PG&E | 2022-03-27 | 11:33 | 38.975 | -122.743 | Other | Bird Nest | Urban | Less than three(3) meters of linear travel | Fire Agency | Kelseyville FD | 103381866 | Yes | 12000 | Pole | Overhead | Yes | 2022-03-27 | 11:16 | Contact From Object | N/A | Animal | Pole | Outside Force
20220330 | PG&E | 2022-03-27 | 08:38 | 35.3266 | -119.4077 | Other | Bird Nest | Desert Shrub | Less than three(3) meters of linear travel | Unknown | N/A | 103253260 | No | 12000 | Transformer | Overhead | Yes | 2022-03-27 | 08:29 | Contact From Object | N/A | Animal | Transformer | Outside Force
20220337 | PG&E | 2022-03-27 | 18:50 | 40.0193 | -123.936 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100984808 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-28 | 15:49 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220332 | PG&E | 2022-03-27 | 13:46 | 38.1409 | -121.1615 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Lockeford fire department | 103804884 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-27 | 13:37 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220328 | PG&E | 2022-03-26 | 18:53 | 40.3966 | -122.2743 | Vegetation | N/A | Herbaceous | Less than three(3) meters of linear travel | Fire Agency | Cottonwood FD | 101492991 | Yes | 12000 | Jumper | Overhead | Yes | 2022-03-26 | 18:21 | Contact From Object | N/A | Vehicle | Jumper | N/A
20220326 | PG&E | 2022-03-26 | 17:53 | 39.1732 | -121.0525 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Nevada County FD | 104087726 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-27 | 17:51 | Contact From Object | N/A | Vegetation | Conductor - Primary | N/A
20220312 | PG&E | 2022-03-24 | 03:49 | 39.1397 | -121.5912 | Vegetation | N/A | Urban | Less than three(3) meters of linear travel | Fire Agency | Marysville FD | 101336173 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-24 | 03:37 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220310 | PG&E | 2022-03-23 | 07:20 | 38.9535 | -121.0462 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 103945466 | No | 12000 | Fuse | Overhead | Yes | 2022-03-23 | 07:47 | Contact From Object | N/A | Animal | Fuse | Outside Force
20220308 | PG&E | 2022-03-22 | 20:57 | 38.5618 | -121.9848 | Vegetation | N/A | Herbaceous | 0.26-9.99 Acres | Fire Agency | Winters FD | 101652042 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-23 | 20:57 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20220307 | PG&E | 2022-03-22 | 15:18 | 35.9481 | -119.7515 | Other | Pole | Agricultural | 0.26-9.99 Acres | Fire Agency | Kings County FD | 100660485 | No | 12000 | Pole | Overhead | Yes | 2022-03-22 | 14:15 | Contamination | N/A | N/A | N/A | N/A
20220261 | PG&E | 2022-03-12 | 10:23 | 35.5716 | -119.6158 | Other | Nest | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Kern County FD | 44383827 | No | 12000 | Transformer | Overhead | Yes | 2022-03-12 | 10:22 | Contact From Object | N/A | Animal | Transformer | Outside Force
20220263 | PG&E | 2022-03-12 | 19:47 | 39.6364 | -121.5831 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 100375284 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-13 | 19:34 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220259 | PG&E | 2022-03-11 | 18:32 | 39.1252 | -121.4612 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Customer | N/A | 101329961 | No | 12000 | Lightning Arrestor | Overhead | Yes | 2022-03-12 | 18:31 | Equipment/Facility Failure | Lightning Arrestor | N/A | N/A | N/A
20220245 | PG&E | 2022-03-07 | 07:10 | 38.166 | -121.9741 | Vegetation | N/A | Wetland | 0.26-9.99 Acres | Fire Agency | Fairfield FD | 101560172 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-03-07 | 06:34 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20220214 | PG&E | 2022-03-02 | 15:08 | 35.8117 | -119.4646 | Other | Pole | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 103780907 | No | 12000 | Transformer | Overhead | Yes | 2022-03-02 | 16:09 | Contact From Object | N/A | Animal | Transformer | Outside Force
20220204 | PG&E | 2022-02-27 | 10:19 | 37.6288 | -122.0615 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Hayward FD | 100930636 | Yes | 750 | Service Drop | Overhead | Yes | 2022-02-27 | 10:15 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20220197 | PG&E | 2022-02-25 | 16:35 | 39.0694 | -121.5721 | Other | Balloons | Agricultural | Less than three(3) meters of linear travel | Customer | N/A | 101314406 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-26 | 16:32 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220182 | PG&E | 2022-02-22 | 15:32 | 37.4204 | -122.1772 | Other | Pole | Urban | Less than three(3) meters of linear travel | Fire Agency | Palo Alto FD | 100275529 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2022-02-22 | 15:27 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20220180 | PG&E | 2022-02-22 | 06:29 | 40.0693 | -122.2165 | Vegetation | N/A | Agricultural | Less Than .25 Acres | Fire Agency | CAL FIRE | 101545300 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-22 | 06:20 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220181 | PG&E | 2022-02-21 | 12:02 | 35.6557 | -120.6896 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 103392496 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-21 | 10:44 | Contact From Object | N/A | Other | Conductor - Primary | Outside Force
20220179 | PG&E | 2022-02-21 | 06:54 | 37.3428 | -121.8507 | Other | Pothead Riser | Urban | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 100569911 | Yes | 12000 | Riser | Overhead | Yes | 2022-02-21 | 06:45 | Equipment/Facility Failure | Riser | N/A | N/A | N/A
20220176 | PG&E | 2022-02-20 | 09:41 | 39.1645 | -121.0408 | Vegetation | N/A | Hardwood Forest | Less than three(3) meters of linear travel | Fire Agency | CAL FIRE | 100067478 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-20 | 09:39 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20220170 | PG&E | 2022-02-18 | 14:07 | 36.5475 | -119.2833 | Other | Balloons | Urban | Less than three(3) meters of linear travel | Fire Agency | Tulare County FD | 100752511 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-18 | 14:03 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220163 | PG&E | 2022-02-15 | 18:12 | 39.1885 | -120.9732 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | Peardale Chicago Park FPD, CAL FIRE | 104030641 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-16 | 18:10 | Contact Between Third Party Facility on Pole and Supply Lines | N/A | N/A | N/A | Human Error
20220133 | PG&E | 2022-02-08 | 13:33 | 39.2058 | -121.0918 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | Grass Valley FD | 100077423 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-08 | 13:22 | Other | N/A | N/A | N/A | Human Error
20220118 | PG&E | 2022-02-05 | 16:10 | 37.1658 | -121.9554 | Other | Balloons | Shrub | Less Than .25 Acres | Fire Agency | Unknown Fire Department | 100538652 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-06 | 15:13 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20220119 | PG&E | 2022-02-05 | 16:36 | 36.6151 | -120.1792 | Other | Car | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 103812042 | No | 12000 | Conductor - Primary | Overhead | Yes | 2022-02-06 | 16:35 | Contact From Object | N/A | Vehicle | Conductor - Primary | N/A
20220125 | PG&E | 2022-02-05 | 03:23 | 36.923 | -119.8129 | Other | Riser | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Unknown Fire Department | 103210196 | No | 12000 | Riser | Overhead | Yes | 2022-02-04 | 09:24 | Contact From Object | N/A | Vehicle | Riser | N/A
20220115 | PG&E | 2022-02-04 | 13:38 | 37.8298 | -122.2452 | Other | Service Drop | Urban | Structure Only | Fire Agency | Oakland FD | 101371826 | No | 750 | Service Drop | Overhead | Yes | 2022-02-04 | 09:16 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220108 | PG&E | 2022-02-02 | 11:03 | 37.2969 | -121.8325 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100592476 | No | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2022-02-02 | 11:02 | Contact From Object | N/A | Vegetation | Conductor - Insulated Secondary | N/A
20220103 | PG&E | 2022-02-02 | 12:49 | 37.2688 | -121.8104 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100618473 | Yes | 750 | Conductor - Racked Secondary | Overhead | Yes | 2022-02-02 | 12:47 | Contact From Object | N/A | Vegetation | Conductor - Racked Secondary | N/A
20220143 | PG&E | 2022-02-01 | 01:34 | 37.4325 | -122.246 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Woodside FD | 103558343 | Yes | 60000 | Conductor - Transmission | Overhead | No | N/A | N/A | Contact From Object | N/A | Vehicle | Conductor - Transmission | N/A
20220056 | PG&E | 2022-01-22 | 06:00 | 37.8397 | -122.2106 | Vegetation | N/A | Urban | Structure Only | Fire Agency | Oakland FD | 101362286 | Yes | 750 | Service Drop | Overhead | No | N/A | N/A | Contact From Object | N/A | Vegetation | Service Drop | N/A | PG&E has included this ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition.
20220057 | PG&E | 2022-01-22 | 07:45 | 37.8 | -122.2208 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Oakland FD | 101354611 | Yes | 12000 | Fuse | Overhead | Yes | 2022-01-22 | 00:17 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20220054 | PG&E | 2022-01-22 | 07:08 | 38.6293 | -122.7717 | Other | Conductor | Herbaceous | Less Than .25 Acres | Fire Agency | Healdsburg FD | 102031990 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2022-01-22 | 06:22 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20220142 | PG&E | 2022-01-16 | 12:36 | 35.9425 | -119.3806 | Vegetation | N/A | Agricultural | Less than three(3) meters of linear travel | Fire Agency | Tulare County FD | 100671828 | No | 12000 | Capacitor Bank | Overhead | Yes | 2022-01-16 | 12:36 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A