## Dictionary
Column | Description
Outage ID | Unique event identification number
County | County
Circuit | Overhead Distribution Circuit Name
Cause | Outage Suspected Initiating Cause
3rd | Third Party
AN | Animal
CI | Company Initiated
EF | Equipment Failure
ENV | Environmental
UNK | Unknown
VEG | Vegetation
FNL_Date_Time | "First No Light"; Outage Start Day & Time
Week | Reporting Week by FNL
End_Date_Time | Outage End Day & Time
EPSS Outage Type | FTS or HLT
FTS | "Fast Trip Setting"; Post-Optimized Circuit Settings
HLT | "Hot Line Tag"; Pre-Optimized Circuit Settings
Duration | Outage Duration in minutes
CESO | Count of Customers Experiencing Sustained Outages
Medical_Baseline | Count of Medical Baseline customer service points
Life_Support | Count of Life Support customer service points
Critical_Customer | Count of Critical Customer service points
Schools | Count of School customer service points
Hospitals | Count of Hospital customer service points
Customer Minutes | Sum of total outage customer minutes
CAIDI | Customer Average Interruption Duration Index, in minutes
Comments | Flag for outage data under additional review

## Outages 072821_113021
Outage ID | County | Circuit | Cause | FNL | Week | End_Date_Time | EPSS Outage Type | Customer Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Duration | CAIDI | Comments
21-0143043 | MONTEREY | LOS OSITOS 2103 | UNK | 2021-11-06 12:55 | 11/1 to 11/7 | 2021-11-06 14:36 | FTS | 808 | 8 | 0 | 0 | 1 | 0 | 0 | 101 | 101
21-0142951 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-11-05 16:00 | 11/1 to 11/7 | 2021-11-05 17:59 | FTS | 524037 | 5510 | 274 | 189 | 84 | 9 | 1 | 119 | 95.1065
21-0142562 | SAN LUIS OBISPO | CAYUCOS 1102 | UNK | 2021-11-04 20:15 | 11/1 to 11/7 | 2021-11-04 20:40 | FTS | 2600 | 104 | 1 | 1 | 0 | 0 | 0 | 25 | 25
21-0142460 | SANTA BARBARA | SISQUOC 1103 | UNK | 2021-11-04 15:42 | 11/1 to 11/7 | 2021-11-04 16:30 | FTS | 1824 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 48
21-0141991 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-11-03 19:41 | 11/1 to 11/7 | 2021-11-03 20:07 | FTS | 40950 | 1575 | 66 | 43 | 10 | 0 | 0 | 26 | 26
21-0141902 | SANTA BARBARA | SISQUOC 1103 | UNK | 2021-11-03 15:29 | 11/1 to 11/7 | 2021-11-03 15:36 | FTS | 266 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 7
21-0141398 | SAN LUIS OBISPO | TEMPLETON 2110 | VEG | 2021-11-02 17:04 | 11/1 to 11/7 | 2021-11-03 04:40 | FTS | 152645 | 1604 | 47 | 33 | 23 | 0 | 0 | 696 | 95.1652
21-0141204 | FRESNO | DUNLAP 1102 | EF | 2021-11-02 12:13 | 11/1 to 11/7 | 2021-11-03 12:34 | FTS | 77976 | 308 | 6 | 4 | 7 | 0 | 0 | 1408 | 253.1688
21-0140718 | SAN LUIS OBISPO | TEMPLETON 2113 | 3RD | 2021-11-01 14:13 | 11/1 to 11/7 | 2021-11-01 14:19 | FTS | 984 | 164 | 10 | 4 | 4 | 0 | 1 | 6 | 6
21-0140330 | SAN LUIS OBISPO | TEMPLETON 2110 | UNK | 2021-10-31 07:47 | 10/25 to 10/31 | 2021-10-31 08:33 | FTS | 57441 | 1323 | 39 | 27 | 17 | 0 | 0 | 46 | 43.4172
21-0140328 | TULARE | SAND CREEK 1103 | UNK | 2021-10-31 07:23 | 10/25 to 10/31 | 2021-10-31 12:33 | FTS | 88660 | 286 | 8 | 5 | 4 | 1 | 0 | 310 | 310
21-0140315 | SAN BENITO | HOLLISTER 2105 | 3RD | 2021-10-31 00:49 | 10/25 to 10/31 | 2021-10-31 05:50 | HLT | 179396 | 596 | 10 | 8 | 15 | 6 | 0 | 301 | 301
21-0140290 | CALAVERAS | WEST POINT 1102 | UNK | 2021-10-30 18:26 | 10/25 to 10/31 | 2021-10-30 18:45 | FTS | 8493 | 447 | 30 | 24 | 8 | 0 | 0 | 19 | 19
21-0140207 | MONTEREY | LOS OSITOS 2103 | UNK | 2021-10-30 13:53 | 10/25 to 10/31 | 2021-10-30 15:17 | FTS | 667 | 8 | 0 | 0 | 1 | 0 | 0 | 84 | 83.375
21-0140188 | TUOLUMNE | PEORIA 1701 | UNK | 2021-10-30 11:34 | 10/25 to 10/31 | 2021-10-30 12:20 | FTS | 56040 | 1260 | 72 | 56 | 14 | 0 | 0 | 46 | 44.4762
21-0139604 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-10-29 06:57 | 10/25 to 10/31 | 2021-10-29 07:35 | FTS | 5567 | 147 | 4 | 4 | 2 | 0 | 0 | 38 | 37.8707
21-0139596 | TUOLUMNE | MIWUK 1702 | UNK | 2021-10-29 03:34 | 10/25 to 10/31 | 2021-10-29 04:18 | FTS | 107317 | 2890 | 207 | 147 | 28 | 1 | 0 | 44 | 37.1339
21-0139563 | CALAVERAS | STANISLAUS 1702 | EF | 2021-10-28 18:37 | 10/25 to 10/31 | 2021-10-29 08:30 | HLT | 1033295 | 2998 | 62 | 45 | 51 | 2 | 0 | 833 | 344.6614
21-0139494 | SANTA CLARA | SWIFT 2110 | UNK | 2021-10-28 15:51 | 10/25 to 10/31 | 2021-10-28 16:07 | FTS | 1520 | 95 | 4 | 3 | 6 | 0 | 0 | 16 | 16
21-0139293 | AMADOR | OLETA 1102 | UNK | 2021-10-28 10:13 | 10/25 to 10/31 | 2021-10-28 11:54 | FTS | 1845 | 19 | 0 | 0 | 0 | 0 | 0 | 101 | 97.1053
21-0134083 |  | SOBRANTE 1101 | VEG | 2021-10-20 20:15 | 10/18 to 10/24 | 2021-10-20 22:05 | FTS | 34200 | 368 | 25 | 19 | 7 | 1 | 0 | 85 | 92.9348
21-0134068 | SANTA CLARA | LOS GATOS 1106 | UNK | 2021-10-20 19:38 | 10/18 to 10/24 | 2021-10-21 08:34 | FTS | 67143 | 124 | 6 | 2 | 4 | 0 | 0 | 776 | 541.4758
21-0134020 | SANTA CLARA | HICKS 2101 | UNK | 2021-10-20 17:35 | 10/18 to 10/24 | 2021-10-20 20:45 | FTS | 29519 | 179 | 13 | 7 | 10 | 1 | 0 | 190 | 164.9106
21-0133998 | SANTA CRUZ | CAMP EVERS 2106 | VEG | 2021-10-20 17:11 | 10/18 to 10/24 | 2021-10-20 19:05 | FTS | 401716 | 3577 | 276 | 209 | 57 | 8 | 0 | 114 | 112.3053
21-0133994 | SANTA CLARA | MORGAN HILL 2105 | EF | 2021-10-20 17:08 | 10/18 to 10/24 | 2021-10-21 12:59 | FTS | 263751 | 1100 | 64 | 50 | 17 | 3 | 0 | 1105 | 239.7736
21-0133910 | SANTA BARBARA | SANTA YNEZ 1104 | UNK | 2021-10-20 15:15 | 10/18 to 10/24 | 2021-10-21 10:06 | FTS | 109239 | 141 | 1 | 0 | 2 | 0 | 0 | 1131 | 774.7447
21-0133901 | SANTA CRUZ | PAUL SWEET 2106 | VEG | 2021-10-20 15:00 | 10/18 to 10/24 | 2021-10-20 20:04 | FTS | 53874 | 268 | 28 | 26 | 4 | 0 | 0 | 304 | 201.0224
21-0133673 | MONTEREY | HATTON 1101 | EF | 2021-10-20 11:19 | 10/18 to 10/24 | 2021-10-20 13:05 | FTS | 215034 | 2103 | 41 | 23 | 55 | 8 | 0 | 106 | 102.2511
21-0133509 | NEVADA | NARROWS 2105 | UNK | 2021-10-20 08:05 | 10/18 to 10/24 | 2021-10-20 15:16 | FTS | 691681 | 2111 | 175 | 101 | 28 | 5 | 0 | 431 | 327.6556
21-0133493 | SAN MATEO | HALF MOON BAY 1103 | UNK | 2021-10-20 07:54 | 10/18 to 10/24 | 2021-10-20 16:27 | FTS | 512626 | 1002 | 27 | 24 | 24 | 7 | 0 | 513 | 511.6028
21-0133436 | AMADOR | OLETA 1102 | VEG | 2021-10-20 04:32 | 10/18 to 10/24 | 2021-10-20 10:15 | FTS | 306600 | 934 | 36 | 22 | 19 | 1 | 0 | 343 | 328.2655
21-0133435 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-10-20 04:12 | 10/18 to 10/24 | 2021-10-20 07:58 | FTS | 659580 | 2999 | 227 | 173 | 45 | 4 | 0 | 226 | 219.9333
21-0133412 | GLENN | ELK CREEK 1101 | EF | 2021-10-19 23:42 | 10/18 to 10/24 | 2021-10-21 05:43 | FTS | 591023 | 569 | 35 | 24 | 27 | 3 | 0 | 1801 | 1038.7047
21-0133413 | SONOMA | FORT ROSS 1121 | UNK | 2021-10-19 23:40 | 10/18 to 10/24 | 2021-10-20 09:24 | FTS | 130782 | 221 | 9 | 5 | 6 | 0 | 0 | 584 | 591.7738
21-0133411 | SANTA CLARA | MENLO 1103 | UNK | 2021-10-19 23:30 | 10/18 to 10/24 | 2021-10-20 02:35 | FTS | 34561 | 300 | 14 | 11 | 5 | 0 | 0 | 185 | 115.2033
21-0133381 | SHASTA | DESCHUTES 1104 | UNK | 2021-10-19 22:16 | 10/18 to 10/24 | 2021-10-20 10:30 | FTS | 333236 | 454 | 32 | 17 | 4 | 0 | 0 | 734 | 734
21-0133354 | SONOMA | FORT ROSS 1121 | VEG | 2021-10-19 19:29 | 10/18 to 10/24 | 2021-10-20 09:07 | FTS | 189564 | 233 | 7 | 6 | 8 | 0 | 0 | 818 | 813.5794
21-0133313 | MARIPOSA | MARIPOSA 2101 | EF | 2021-10-19 18:00 | 10/18 to 10/24 | 2021-10-19 22:25 | FTS | 120265 | 3583 | 292 | 198 | 60 | 0 | 9 | 265 | 33.5654
21-0133402 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-10-19 18:00 | 10/18 to 10/24 | 2021-10-20 03:28 | FTS | 127232 | 224 | 18 | 8 | 7 | 0 | 0 | 568 | 568
21-0133031 | SANTA CLARA | LOS GATOS 1107 | AN | 2021-10-19 11:01 | 10/18 to 10/24 | 2021-10-19 17:56 | FTS | 216981 | 897 | 59 | 37 | 28 | 0 | 0 | 415 | 241.8963
21-0132954 | SONOMA | GEYSERVILLE 1102 | UNK | 2021-10-19 09:20 | 10/18 to 10/24 | 2021-10-19 13:49 | FTS | 146793 | 589 | 8 | 6 | 20 | 3 | 0 | 269 | 249.2241
21-0132945 | HUMBOLDT | HOOPA 1101 | UNK | 2021-10-19 09:11 | 10/18 to 10/24 | 2021-10-20 13:29 | HLT | 604179 | 668 | 17 | 15 | 24 | 5 | 0 | 1698 | 904.4596
21-0132886 | NEVADA | NARROWS 2105 | AN | 2021-10-19 08:04 | 10/18 to 10/24 | 2021-10-19 12:48 | FTS | 326968 | 2111 | 175 | 101 | 28 | 5 | 0 | 284 | 154.8877
21-0132800 | MENDOCINO | MENDOCINO 1101 | 3RD | 2021-10-18 23:05 | 10/18 to 10/24 | 2021-10-19 08:59 | FTS | 253308 | 593 | 39 | 28 | 8 | 0 | 0 | 594 | 427.1636
21-0132413 | TEHAMA | VOLTA 1101 | UNK | 2021-10-18 09:35 | 10/18 to 10/24 | 2021-10-18 17:05 | FTS | 228622 | 782 | 38 | 28 | 14 | 1 | 0 | 450 | 292.3555
21-0132378 | NEVADA | NARROWS 2105 | UNK | 2021-10-18 08:47 | 10/18 to 10/24 | 2021-10-18 13:25 | FTS | 252637 | 894 | 59 | 36 | 8 | 0 | 0 | 278 | 282.5917
21-0132293 | BUTTE | ORO FINO 1102 | EF | 2021-10-18 03:55 | 10/18 to 10/24 | 2021-10-18 15:43 | FTS | 397932 | 566 | 35 | 27 | 6 | 0 | 0 | 708 | 703.0601
21-0132254 | MARIPOSA | BEAR VALLEY 2101 | UNK | 2021-10-18 00:32 | 10/18 to 10/24 | 2021-10-18 10:56 | FTS | 338832 | 543 | 28 | 18 | 14 | 3 | 0 | 624 | 624
21-0132188 | YUBA | CHALLENGE 1102 | EF | 2021-10-17 20:58 | 10/11 to 10/17 | 2021-10-18 03:45 | FTS | 145162 | 898 | 75 | 55 | 17 | 2 | 0 | 407 | 161.6503
21-0132181 | PLUMAS | GANSNER 1101 | UNK | 2021-10-17 20:47 | 10/11 to 10/17 | 2021-10-18 12:23 | HLT | 190944 | 204 | 11 | 8 | 4 | 0 | 0 | 936 | 936
21-0132049 | SHASTA | GIRVAN 1102 | VEG | 2021-10-17 15:40 | 10/11 to 10/17 | 2021-10-18 01:09 | FTS | 660509 | 1695 | 143 | 107 | 20 | 3 | 0 | 569 | 389.6808
21-0132038 | SHASTA | VOLTA 1101 | UNK | 2021-10-17 14:19 | 10/11 to 10/17 | 2021-10-17 20:15 | FTS | 32040 | 90 | 6 | 4 | 1 | 0 | 0 | 356 | 356
21-0132022 | MARIPOSA | MERCED FALLS 1102 | UNK | 2021-10-17 12:50 | 10/11 to 10/17 | 2021-10-17 17:42 | FTS | 227552 | 968 | 101 | 68 | 12 | 3 | 0 | 292 | 235.0744
21-0132008 | MONTEREY | LOS OSITOS 2103 | EF | 2021-10-17 11:16 | 10/11 to 10/17 | 2021-10-17 21:42 | HLT | 185228 | 838 | 13 | 9 | 13 | 2 | 0 | 626 | 221.0358
21-0132002 | SANTA CRUZ | BIG BASIN 1102 | AN | 2021-10-17 10:11 | 10/11 to 10/17 | 2021-10-17 12:50 | FTS | 74782 | 474 | 34 | 24 | 4 | 0 | 0 | 159 | 157.7679
21-0131999 | FRESNO | TIVY VALLEY 1107 | UNK | 2021-10-17 09:54 | 10/11 to 10/17 | 2021-10-17 13:17 | FTS | 147582 | 747 | 54 | 32 | 16 | 0 | 0 | 203 | 197.5663
21-0131998 | PLACER | SHADY GLEN 1101 | AN | 2021-10-17 09:52 | 10/11 to 10/17 | 2021-10-17 14:15 | FTS | 246375 | 986 | 63 | 41 | 13 | 1 | 0 | 263 | 249.8732
21-0131989 | SANTA CLARA | MORGAN HILL 2105 | EF | 2021-10-17 07:56 | 10/11 to 10/17 | 2021-10-18 02:32 | FTS | 681952 | 4292 | 278 | 197 | 47 | 9 | 1 | 1116 | 158.8891
21-0131982 | EL DORADO | PLACERVILLE 2106 | VEG | 2021-10-17 06:59 | 10/11 to 10/17 | 2021-10-17 13:42 | FTS | 415896 | 1032 | 85 | 62 | 18 | 5 | 0 | 403 | 403
21-0131984 | FRESNO | AUBERRY 1101 | UNK | 2021-10-17 06:51 | 10/11 to 10/17 | 2021-10-17 13:48 | FTS | 467168 | 1376 | 121 | 81 | 17 | 4 | 0 | 416 | 339.5116
21-0131981 | MARIPOSA | BEAR VALLEY 2105 | UNK | 2021-10-17 06:36 | 10/11 to 10/17 | 2021-10-17 10:41 | FTS | 138730 | 590 | 39 | 30 | 16 | 2 | 0 | 245 | 235.1356
21-0131980 | SAN BENITO | PANOCHE 1103 | AN | 2021-10-17 06:28 | 10/11 to 10/17 | 2021-10-17 08:34 | HLT | 26208 | 208 | 2 | 2 | 8 | 1 | 0 | 126 | 126
21-0131978 | SAN BENITO | PANOCHE 1103 | AN | 2021-10-17 06:27 | 10/11 to 10/17 | 2021-10-17 08:33 | HLT | 14993 | 134 | 0 | 0 | 6 | 0 | 0 | 126 | 111.8881
21-0131970 | SANTA CLARA | LLAGAS 2101 | 3RD | 2021-10-16 23:02 | 10/11 to 10/17 | 2021-10-17 18:25 | HLT | 943386 | 1001 | 49 | 33 | 16 | 2 | 0 | 1160 | 942.4436
21-0131914 | HUMBOLDT | HOOPA 1101 | UNK | 2021-10-16 14:08 | 10/11 to 10/17 | 2021-10-17 12:16 | HLT | 677052 | 669 | 17 | 15 | 24 | 5 | 0 | 1328 | 1012.0359
21-0131896 | TUOLUMNE | CURTIS 1703 | EF | 2021-10-16 11:24 | 10/11 to 10/17 | 2021-10-16 19:54 | FTS | 141388 | 378 | 35 | 29 | 4 | 0 | 0 | 510 | 374.0423
21-0131867 | CALAVERAS | WEST POINT 1102 | UNK | 2021-10-16 07:50 | 10/11 to 10/17 | 2021-10-16 15:24 | FTS | 893018 | 1967 | 131 | 93 | 27 | 0 | 0 | 454 | 454
21-0131845 | SANTA CRUZ | GREEN VALLEY 2101 | UNK | 2021-10-15 22:50 | 10/11 to 10/17 | 2021-10-16 01:16 | FTS | 85067 | 1012 | 85 | 69 | 9 | 1 | 0 | 146 | 84.0583
21-0131816 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-10-15 16:36 | 10/11 to 10/17 | 2021-10-16 09:45 | FTS | 242844 | 236 | 7 | 5 | 3 | 0 | 0 | 1029 | 1029
21-0131811 | SAN BENITO | PANOCHE 1103 | EF | 2021-10-15 16:35 | 10/11 to 10/17 | 2021-10-15 23:56 | HLT | 11417 | 134 | 0 | 0 | 6 | 0 | 0 | 441 | 85.2015
21-0131824 | SAN BENITO | PANOCHE 1103 | EF | 2021-10-15 16:35 | 10/11 to 10/17 | 2021-10-15 18:20 | HLT | 21840 | 208 | 2 | 2 | 8 | 1 | 0 | 105 | 105
21-0131740 | MONTEREY | DEL MONTE 2104 | UNK | 2021-10-15 14:31 | 10/11 to 10/17 | 2021-10-15 17:32 | FTS | 591553 | 5439 | 215 | 149 | 183 | 9 | 1 | 181 | 108.7614
21-0131186 | SANTA BARBARA | SISQUOC 1103 | UNK | 2021-10-14 13:56 | 10/11 to 10/17 | 2021-10-14 16:50 | FTS | 6438 | 37 | 0 | 0 | 0 | 0 | 0 | 174 | 174
21-0131098 | SANTA CRUZ | PAUL SWEET 2106 | VEG | 2021-10-14 12:04 | 10/11 to 10/17 | 2021-10-14 19:21 | FTS | 55131 | 268 | 28 | 26 | 4 | 0 | 0 | 437 | 205.7127
21-0131045 | YUBA | CHALLENGE 1102 | 3RD | 2021-10-14 10:58 | 10/11 to 10/17 | 2021-10-14 17:13 | FTS | 54735 | 200 | 18 | 13 | 0 | 0 | 0 | 375 | 273.675
21-0130971 | TEHAMA | CORNING 1102 | UNK | 2021-10-14 09:45 | 10/11 to 10/17 | 2021-10-14 13:24 | FTS | 60337 | 379 | 21 | 14 | 10 | 3 | 0 | 219 | 159.2005
21-0130848 | SAN LUIS OBISPO | SAN LUIS OBISPO 1104 | UNK | 2021-10-14 06:45 | 10/11 to 10/17 | 2021-10-14 10:29 | FTS | 64628 | 535 | 22 | 17 | 12 | 2 | 0 | 224 | 120.8
21-0130767 | FRESNO | TIVY VALLEY 1107 | UNK | 2021-10-13 20:07 | 10/11 to 10/17 | 2021-10-14 09:48 | FTS | 422667 | 516 | 49 | 29 | 3 | 0 | 0 | 821 | 819.1221
21-0130254 | LAKE | HIGHLANDS 1103 | UNK | 2021-10-13 07:38 | 10/11 to 10/17 | 2021-10-13 11:44 | FTS | 321957 | 1314 | 105 | 65 | 16 | 0 | 0 | 246 | 245.0205
21-0130251 | NAPA | SILVERADO 2104 | UNK | 2021-10-13 07:36 | 10/11 to 10/17 | 2021-10-13 12:53 | FTS | 207934 | 733 | 29 | 17 | 17 | 3 | 0 | 317 | 283.6753
21-0130228 | SANTA CRUZ | PAUL SWEET 2106 | UNK | 2021-10-13 06:57 | 10/11 to 10/17 | 2021-10-13 12:21 | FTS | 77291 | 268 | 28 | 26 | 4 | 0 | 0 | 324 | 288.3993
21-0130227 | SANTA BARBARA | SISQUOC 1102 | UNK | 2021-10-13 06:54 | 10/11 to 10/17 | 2021-10-13 20:51 | FTS | 36524 | 129 | 0 | 0 | 1 | 0 | 0 | 837 | 283.1318
21-0130198 | CONTRA COSTA | SOBRANTE 1102 | EF | 2021-10-13 00:21 | 10/11 to 10/17 | 2021-10-18 22:55 | FTS | 1650667 | 2679 | 166 | 119 | 43 | 5 | 0 | 834 | 616.1504
21-0130184 | SAN MATEO | MENLO 1102 | VEG | 2021-10-12 21:55 | 10/11 to 10/17 | 2021-10-13 14:42 | HLT | 1074165 | 1173 | 46 | 36 | 32 | 2 | 0 | 1007 | 915.7417
21-0130069 | MARIN | WOODACRE 1101 | UNK | 2021-10-12 16:24 | 10/11 to 10/17 | 2021-10-13 09:51 | FTS | 92170 | 270 | 7 | 3 | 4 | 2 | 0 | 1047 | 341.3704
21-0129944 | PLACER | SHADY GLEN 1101 | UNK | 2021-10-12 14:16 | 10/11 to 10/17 | 2021-10-12 18:35 | FTS | 182749 | 986 | 63 | 41 | 13 | 1 | 0 | 259 | 185.3438
21-0129564 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-10-12 07:01 | 10/11 to 10/17 | 2021-10-12 10:38 | FTS | 1229196 | 3380 | 125 | 87 | 36 | 3 | 3 | 217 | 363.6675
21-0129544 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-10-12 06:31 | 10/11 to 10/17 | 2021-10-12 12:33 | FTS | 945585 | 2909 | 225 | 156 | 45 | 0 | 0 | 362 | 325.055
21-0129518 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-10-12 01:58 | 10/11 to 10/17 | 2021-10-12 12:14 | FTS | 262126 | 430 | 38 | 27 | 11 | 0 | 0 | 616 | 609.5953
21-0129505 | CALAVERAS | SALT SPRINGS 2102 | VEG | 2021-10-11 23:20 | 10/11 to 10/17 | 2021-10-12 15:16 | FTS | 2637835 | 4470 | 134 | 97 | 65 | 3 | 2 | 944 | 590.1197
21-0129469 | FRESNO | AUBERRY 1101 | VEG | 2021-10-11 21:12 | 10/11 to 10/17 | 2021-10-12 16:43 | FTS | 842904 | 823 | 37 | 24 | 23 | 3 | 0 | 1171 | 1024.1847
21-0129330 | SONOMA | FORT ROSS 1121 | VEG | 2021-10-11 17:46 | 10/11 to 10/17 | 2021-10-12 11:28 | FTS | 216372 | 220 | 9 | 5 | 6 | 0 | 0 | 1062 | 983.5091
21-0129288 | NAPA | SILVERADO 2102 | UNK | 2021-10-11 17:14 | 10/11 to 10/17 | 2021-10-12 17:23 | FTS | 667401 | 465 | 1 | 1 | 12 | 0 | 0 | 1449 | 1435.271
21-0129266 | SANTA CRUZ | ROB ROY 2104 | EF | 2021-10-11 16:49 | 10/11 to 10/17 | 2021-10-13 02:08 | FTS | 1637572 | 2435 | 149 | 124 | 34 | 6 | 0 | 1400 | 672.5142
21-0129258 | NEVADA | NARROWS 2105 | VEG | 2021-10-11 16:39 | 10/11 to 10/17 | 2021-10-12 19:01 | FTS | 302608 | 260 | 7 | 3 | 5 | 0 | 0 | 1582 | 1163.8769
21-0129259 | TUOLUMNE | CURTIS 1703 | VEG | 2021-10-11 16:30 | 10/11 to 10/17 | 2021-10-12 10:49 | FTS | 2802043 | 2559 | 157 | 121 | 44 | 1 | 0 | 1099 | 1094.9758
21-0129238 | FRESNO | SAND CREEK 1103 | UNK | 2021-10-11 16:24 | 10/11 to 10/17 | 2021-10-12 12:28 | FTS | 1043868 | 867 | 94 | 59 | 8 | 0 | 0 | 1204 | 1204
21-0129230 | HUMBOLDT | HOOPA 1101 | VEG | 2021-10-11 16:19 | 10/11 to 10/17 | 2021-10-12 12:50 | HLT | 102995 | 245 | 10 | 7 | 8 | 0 | 0 | 1231 | 420.3878
21-0129153 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-10-11 15:20 | 10/11 to 10/17 | 2021-10-11 21:28 | FTS | 126928 | 371 | 17 | 11 | 7 | 0 | 0 | 368 | 342.124
21-0129115 | SANTA CRUZ | CAMP EVERS 2106 | VEG | 2021-10-11 15:01 | 10/11 to 10/17 | 2021-10-11 20:20 | FTS | 916881 | 3718 | 277 | 208 | 57 | 4 | 0 | 319 | 246.606
21-0129094 | BUTTE | ORO FINO 1102 | VEG | 2021-10-11 14:51 | 10/11 to 10/17 | 2021-10-11 18:33 | FTS | 126540 | 570 | 79 | 52 | 5 | 0 | 0 | 222 | 222
21-0129056 | MARIPOSA | BEAR VALLEY 2101 | UNK | 2021-10-11 14:13 | 10/11 to 10/17 | 2021-10-11 18:56 | FTS | 192409 | 803 | 44 | 30 | 19 | 3 | 0 | 283 | 239.6127
21-0129015 | SANTA CRUZ | PAUL SWEET 2106 | UNK | 2021-10-11 13:59 | 10/11 to 10/17 | 2021-10-12 12:54 | FTS | 477125 | 347 | 38 | 34 | 5 | 1 | 0 | 1375 | 1375
21-0129013 | TUOLUMNE | PEORIA 1701 | UNK | 2021-10-11 13:55 | 10/11 to 10/17 | 2021-10-11 17:50 | FTS | 442636 | 1912 | 99 | 76 | 30 | 3 | 0 | 235 | 231.5042
21-0128985 | SAN LUIS OBISPO | CAMBRIA 1102 | VEG | 2021-10-11 13:40 | 10/11 to 10/17 | 2021-10-12 14:09 | FTS | 318571 | 1223 | 38 | 29 | 19 | 0 | 0 | 1469 | 260.4832
21-0128999 | BUTTE | ORO FINO 1102 | UNK | 2021-10-11 13:37 | 10/11 to 10/17 | 2021-10-12 16:42 | FTS | 899155 | 569 | 42 | 29 | 6 | 0 | 0 | 1625 | 1580.2373
21-0128951 | CONTRA COSTA | SAN RAMON 2108 | EF | 2021-10-11 13:20 | 10/11 to 10/17 | 2021-10-11 19:13 | FTS | 381207 | 3806 | 159 | 114 | 40 | 5 | 0 | 353 | 100.1595
21-0128898 | EL DORADO | SHINGLE SPRINGS 2110 | VEG | 2021-10-11 12:47 | 10/11 to 10/17 | 2021-10-11 20:16 | FTS | 214783 | 1005 | 78 | 50 | 15 | 7 | 0 | 449 | 213.7144
21-0128937 | NAPA | PUEBLO 2103 | UNK | 2021-10-11 12:03 | 10/11 to 10/17 | 2021-10-12 14:39 | FTS | 398385 | 1560 | 98 | 71 | 18 | 1 | 0 | 1596 | 255.375
21-0128841 | NAPA | PUEBLO 2103 | UNK | 2021-10-11 12:01 | 10/11 to 10/17 | 2021-10-12 15:05 | FTS | 319944 | 586 | 35 | 22 | 8 | 0 | 0 | 1624 | 545.9795
21-0128833 | CALAVERAS | FROGTOWN 1702 | 3RD | 2021-10-11 11:46 | 10/11 to 10/17 | 2021-10-11 16:29 | FTS | 230079 | 813 | 37 | 23 | 29 | 2 | 0 | 283 | 283
21-0128794 | SANTA CRUZ | ROB ROY 2104 | VEG | 2021-10-11 11:30 | 10/11 to 10/17 | 2021-10-11 15:20 | FTS | 105570 | 459 | 26 | 25 | 10 | 0 | 0 | 230 | 230
21-0128789 | SANTA CRUZ | CAMP EVERS 2106 | VEG | 2021-10-11 11:16 | 10/11 to 10/17 | 2021-10-12 11:11 | FTS | 1527136 | 2851 | 223 | 176 | 44 | 8 | 0 | 1435 | 535.6492
21-0128903 | SANTA CRUZ | CAMP EVERS 2106 | UNK | 2021-10-11 11:16 | 10/11 to 10/17 | 2021-10-11 16:50 | HLT | 217447 | 723 | 53 | 33 | 13 | 0 | 0 | 334 | 300.7566
21-0128765 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-10-11 10:59 | 10/11 to 10/17 | 2021-10-11 15:58 | FTS | 127652 | 430 | 38 | 27 | 11 | 0 | 0 | 299 | 296.8651
21-0128738 | SONOMA | GEYSERVILLE 1101 | UNK | 2021-10-11 10:36 | 10/11 to 10/17 | 2021-10-11 13:10 | FTS | 32648 | 212 | 4 | 2 | 3 | 0 | 0 | 154 | 154
21-0128730 | SANTA CRUZ | BIG BASIN 1102 | VEG | 2021-10-11 10:34 | 10/11 to 10/17 | 2021-10-11 17:05 | FTS | 559642 | 1682 | 105 | 74 | 25 | 1 | 0 | 391 | 332.7241
21-0128746 | SOLANO | VACA DIXON 1105 | UNK | 2021-10-11 10:32 | 10/11 to 10/17 | 2021-10-11 17:36 | FTS | 259912 | 613 | 61 | 40 | 11 | 0 | 0 | 424 | 424
21-0128609 | EL DORADO | APPLE HILL 2102 | UNK | 2021-10-11 09:02 | 10/11 to 10/17 | 2021-10-11 13:00 | FTS | 177996 | 751 | 55 | 34 | 8 | 0 | 0 | 238 | 237.012
21-0113254 | MONTEREY | DEL MONTE 2104 | CI | 2021-10-11 07:57 | 10/11 to 10/17 | 2021-10-11 09:22 | FTS | 156102 | 1954 | 72 | 47 | 62 | 5 | 0 | 85 | 79.8884
21-0128522 | SONOMA | CALISTOGA 1101 | UNK | 2021-10-11 04:20 | 10/11 to 10/17 | 2021-10-11 12:20 | FTS | 27840 | 58 | 0 | 0 | 0 | 0 | 0 | 480 | 480
21-0128517 | NEVADA | NARROWS 2102 | 3RD | 2021-10-11 02:43 | 10/11 to 10/17 | 2021-10-12 15:31 | FTS | 959565 | 887 | 47 | 29 | 20 | 7 | 0 | 2208 | 1081.8095
21-0128394 | SHASTA | JESSUP 1102 | EF | 2021-10-10 10:57 | 10/4 to 10/10 | 2021-10-11 03:04 | FTS | 86815 | 393 | 46 | 36 | 1 | 0 | 0 | 967 | 220.9033
21-0128388 | TUOLUMNE | CURTIS 1703 | AN | 2021-10-10 10:14 | 10/4 to 10/10 | 2021-10-10 16:24 | FTS | 165082 | 605 | 39 | 34 | 17 | 0 | 0 | 370 | 272.8628
21-0128379 | SANTA CLARA | SARATOGA 1107 | UNK | 2021-10-10 09:18 | 10/4 to 10/10 | 2021-10-10 13:09 | FTS | 206048 | 2458 | 95 | 58 | 45 | 10 | 0 | 159 | 83.8275
21-0128351 | MONTEREY | LOS OSITOS 2103 | EF | 2021-10-10 06:34 | 10/4 to 10/10 | 2021-10-10 19:34 | HLT | 10908 | 57 | 0 | 0 | 2 | 0 | 0 | 780 | 191.3684
21-0128333 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-10-09 23:53 | 10/4 to 10/10 | 2021-10-10 05:23 | HLT | 276237 | 1575 | 66 | 43 | 10 | 0 | 0 | 330 | 175.3886
21-0128087 | SAN LUIS OBISPO | TEMPLETON 2113 | 3RD | 2021-10-09 03:17 | 10/4 to 10/10 | 2021-10-09 14:27 | FTS | 1221824 | 3117 | 161 | 113 | 50 | 2 | 1 | 670 | 391.9872
21-0128082 | SAN BENITO | PANOCHE 1103 | 3RD | 2021-10-09 01:36 | 10/4 to 10/10 | 2021-10-09 10:51 | HLT | 18871 | 134 | 0 | 0 | 6 | 0 | 0 | 555 | 140.8284
21-0128084 | SAN BENITO | PANOCHE 1103 | 3RD | 2021-10-09 01:36 | 10/4 to 10/10 | 2021-10-09 03:34 | HLT | 24544 | 208 | 2 | 2 | 8 | 1 | 0 | 118 | 118
21-0128070 | SANTA CLARA | SWIFT 2110 | UNK | 2021-10-08 22:06 | 10/4 to 10/10 | 2021-10-09 14:18 | FTS | 92268 | 95 | 4 | 3 | 6 | 0 | 0 | 972 | 971.2421
21-0128061 | LAKE | CLEAR LAKE 1101 | EF | 2021-10-08 20:31 | 10/4 to 10/10 | 2021-10-09 12:17 | FTS | 320849 | 523 | 35 | 21 | 8 | 0 | 1 | 946 | 613.478
21-0128053 | CONTRA COSTA | CLAYTON 2212 | EF | 2021-10-08 19:30 | 10/4 to 10/10 | 2021-10-09 15:07 | HLT | 831405 | 3427 | 287 | 190 | 84 | 8 | 0 | 1177 | 242.6043
21-0127806 | MENDOCINO | MENDOCINO 1101 | UNK | 2021-10-08 12:46 | 10/4 to 10/10 | 2021-10-08 15:00 | FTS | 99830 | 745 | 44 | 31 | 10 | 0 | 0 | 134 | 134
21-0127705 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-10-08 10:50 | 10/4 to 10/10 | 2021-10-08 14:46 | FTS | 677077 | 2999 | 227 | 173 | 45 | 4 | 0 | 236 | 225.7676
21-0127569 | MARIN | ALTO 1124 | UNK | 2021-10-08 08:52 | 10/4 to 10/10 | 2021-10-08 13:51 | FTS | 179426 | 685 | 20 | 12 | 7 | 0 | 0 | 299 | 261.9358
21-0127546 | MARIN | ALTO 1125 | UNK | 2021-10-08 08:27 | 10/4 to 10/10 | 2021-10-08 14:42 | FTS | 144715 | 831 | 32 | 21 | 3 | 1 | 0 | 375 | 174.1456
21-0127216 | EL DORADO | EL DORADO PH 2101 | UNK | 2021-10-07 11:15 | 10/4 to 10/10 | 2021-10-07 15:39 | FTS | 288104 | 2084 | 174 | 128 | 33 | 3 | 0 | 264 | 138.2457
21-0127088 | HUMBOLDT | HOOPA 1101 | UNK | 2021-10-07 08:25 | 10/4 to 10/10 | 2021-10-07 16:16 | HLT | 97497 | 207 | 4 | 4 | 8 | 1 | 0 | 471 | 471
21-0127077 | SOLANO | VACA DIXON 1105 | UNK | 2021-10-07 08:08 | 10/4 to 10/10 | 2021-10-07 11:58 | FTS | 21023 | 526 | 60 | 37 | 3 | 0 | 0 | 230 | 39.9677
21-0127050 | AMADOR | WEST POINT 1101 | UNK | 2021-10-07 07:33 | 10/4 to 10/10 | 2021-10-07 09:20 | FTS | 184979 | 1761 | 139 | 102 | 17 | 0 | 0 | 107 | 105.042
21-0127022 | CALAVERAS | FROGTOWN 1702 | UNK | 2021-10-07 06:46 | 10/4 to 10/10 | 2021-10-07 11:42 | FTS | 232180 | 812 | 36 | 22 | 29 | 2 | 0 | 296 | 285.936
21-0127007 | SHASTA | JESSUP 1102 | UNK | 2021-10-07 05:56 | 10/4 to 10/10 | 2021-10-07 08:06 | FTS | 39390 | 303 | 27 | 21 | 0 | 0 | 0 | 130 | 130
21-0126839 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-10-06 15:14 | 10/4 to 10/10 | 2021-10-06 18:08 | FTS | 7656 | 44 | 1 | 0 | 0 | 0 | 0 | 174 | 174
21-0126736 | NAPA | SILVERADO 2104 | UNK | 2021-10-06 13:30 | 10/4 to 10/10 | 2021-10-06 16:12 | FTS | 116738 | 734 | 29 | 17 | 17 | 3 | 0 | 162 | 159.0436
21-0126646 | CALAVERAS | WEST POINT 1102 | UNK | 2021-10-06 11:46 | 10/4 to 10/10 | 2021-10-06 14:36 | FTS | 76330 | 449 | 30 | 24 | 8 | 0 | 0 | 170 | 170
21-0126564 | TUOLUMNE | MIWUK 1702 | EF | 2021-10-06 10:20 | 10/4 to 10/10 | 2021-10-06 16:44 | FTS | 80120 | 438 | 39 | 30 | 2 | 1 | 0 | 384 | 182.9224
21-0126482 | SANTA CRUZ | PAUL SWEET 2106 | UNK | 2021-10-06 08:58 | 10/4 to 10/10 | 2021-10-06 12:34 | FTS | 74952 | 347 | 38 | 34 | 5 | 1 | 0 | 216 | 216
21-0126393 | MARIN | SAN RAFAEL 1108 | AN | 2021-10-06 06:35 | 10/4 to 10/10 | 2021-10-06 09:43 | FTS | 943293 | 6249 | 170 | 91 | 92 | 34 | 0 | 188 | 150.951
21-0126392 | NEVADA | BRUNSWICK 1105 | VEG | 2021-10-06 06:22 | 10/4 to 10/10 | 2021-10-06 10:31 | FTS | 361996 | 939 | 48 | 36 | 12 | 0 | 0 | 249 | 385.5122
21-0126384 | CALAVERAS | SALT SPRINGS 2102 | UNK | 2021-10-06 04:00 | 10/4 to 10/10 | 2021-10-06 06:09 | FTS | 61662 | 478 | 11 | 6 | 7 | 0 | 0 | 129 | 129
21-0126325 | MADERA | COARSEGOLD 2104 | UNK | 2021-10-05 19:44 | 10/4 to 10/10 | 2021-10-06 10:54 | FTS | 613021 | 1584 | 163 | 123 | 21 | 1 | 0 | 910 | 387.0082
21-0126274 | SANTA CLARA | HICKS 2101 | CI | 2021-10-05 16:50 | 10/4 to 10/10 | 2021-10-05 17:22 | FTS | 34496 | 1078 | 71 | 51 | 19 | 1 | 0 | 32 | 32
21-0126220 | CALAVERAS | WEST POINT 1102 | 3RD | 2021-10-05 15:07 | 10/4 to 10/10 | 2021-10-05 20:11 | FTS | 79642 | 449 | 30 | 24 | 8 | 0 | 0 | 304 | 177.3764
21-0126217 | SAN LUIS OBISPO | ATASCADERO 1103 | UNK | 2021-10-05 15:01 | 10/4 to 10/10 | 2021-10-05 22:35 | FTS | 173636 | 804 | 21 | 15 | 12 | 1 | 0 | 454 | 215.9652
21-0126211 | SHASTA | DESCHUTES 1104 | 3RD | 2021-10-05 14:49 | 10/4 to 10/10 | 2021-10-05 17:17 | HLT | 105256 | 714 | 59 | 42 | 4 | 0 | 0 | 148 | 147.4174
21-0126018 | SANTA CLARA | LOS GATOS 1107 | UNK | 2021-10-05 10:12 | 10/4 to 10/10 | 2021-10-05 18:10 | FTS | 292824 | 935 | 61 | 39 | 28 | 0 | 0 | 478 | 313.1807
21-0125988 | EL DORADO | APPLE HILL 2102 | UNK | 2021-10-05 09:32 | 10/4 to 10/10 | 2021-10-05 13:31 | FTS | 90103 | 377 | 29 | 20 | 3 | 0 | 0 | 239 | 239
21-0125813 | SONOMA | GEYSERVILLE 1102 | CI | 2021-10-04 18:21 | 10/4 to 10/10 | 2021-10-04 18:50 | FTS | 11674 | 416 | 11 | 3 | 9 | 2 | 0 | 29 | 28.0625
21-0125717 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-10-04 15:16 | 10/4 to 10/10 | 2021-10-05 09:41 | FTS | 215356 | 430 | 38 | 27 | 11 | 0 | 0 | 1105 | 500.8279
21-0125648 | BUTTE | KANAKA 1101 | UNK | 2021-10-04 14:02 | 10/4 to 10/10 | 2021-10-04 17:00 | FTS | 66978 | 379 | 29 | 21 | 12 | 0 | 0 | 178 | 176.723
21-0125553 | SANTA CRUZ | GREEN VALLEY 2101 | UNK | 2021-10-04 12:11 | 10/4 to 10/10 | 2021-10-04 14:28 | FTS | 20413 | 149 | 4 | 4 | 0 | 0 | 0 | 137 | 137
21-0125444 | SHASTA | DESCHUTES 1104 | UNK | 2021-10-04 09:48 | 10/4 to 10/10 | 2021-10-04 15:33 | HLT | 239674 | 714 | 59 | 42 | 4 | 0 | 0 | 345 | 335.6779
21-0125356 | NAPA | SILVERADO 2102 | UNK | 2021-10-04 07:31 | 10/4 to 10/10 | 2021-10-04 11:36 | FTS | 76232 | 328 | 3 | 3 | 5 | 0 | 0 | 245 | 232.4146
21-0125265 | SANTA CLARA | LOS GATOS 1106 | VEG | 2021-10-03 07:52 | 9/27 to 10/3 | 2021-10-04 01:45 | FTS | 329281 | 955 | 73 | 55 | 17 | 3 | 0 | 1073 | 344.7969
21-0125261 | AMADOR | OLETA 1102 | UNK | 2021-10-03 06:53 | 9/27 to 10/3 | 2021-10-03 11:55 | FTS | 270531 | 961 | 36 | 22 | 19 | 1 | 0 | 302 | 281.5099
21-0125216 | MARIPOSA | BEAR VALLEY 2105 | UNK | 2021-10-02 17:02 | 9/27 to 10/3 | 2021-10-03 09:41 | FTS | 588839 | 591 | 39 | 30 | 16 | 2 | 0 | 999 | 996.3435
21-0125209 | MONTEREY | RESERVATION ROAD 1101 | EF | 2021-10-02 16:23 | 9/27 to 10/3 | 2021-10-04 04:18 | FTS | 552270 | 710 | 51 | 29 | 18 | 2 | 0 | 1102 | 777.8451
21-0125204 | SAN BENITO | SAN JUSTO 1101 | EF | 2021-10-02 15:35 | 9/27 to 10/3 | 2021-10-03 09:00 | HLT | 36850 | 166 | 9 | 8 | 3 | 0 | 0 | 1045 | 221.988
21-0125148 | SANTA CRUZ | BIG BASIN 1102 | AN | 2021-10-02 08:43 | 9/27 to 10/3 | 2021-10-02 11:57 | FTS | 62860 | 476 | 34 | 24 | 4 | 0 | 0 | 194 | 132.0588
21-0125143 | SANTA BARBARA | ZACA 1102 | UNK | 2021-10-02 08:26 | 9/27 to 10/3 | 2021-10-02 15:23 | FTS | 172457 | 545 | 17 | 8 | 9 | 1 | 0 | 417 | 316.4349
21-0125137 | NEVADA | BRUNSWICK 1105 | AN | 2021-10-02 07:59 | 9/27 to 10/3 | 2021-10-02 14:59 | FTS | [9 empty] | Outage data under further review
21-0125090 | SANTA CRUZ | BIG BASIN 1102 | CI | 2021-10-01 23:19 | 9/27 to 10/3 | 2021-10-01 23:59 | FTS | 280 | 7 | 0 | 0 | 0 | 0 | 0 | 40 | 40
21-0125081 | SANTA CRUZ | BIG BASIN 1102 | CI | 2021-10-01 19:13 | 9/27 to 10/3 | 2021-10-01 23:06 | FTS | 1631 | 7 | 0 | 0 | 0 | 0 | 0 | 233 | 233
21-0124938 | SANTA CLARA | LLAGAS 2101 | UNK | 2021-10-01 14:16 | 9/27 to 10/3 | 2021-10-02 09:25 | HLT | 581712 | 1001 | 49 | 33 | 16 | 2 | 0 | 1097 | 581.1309
21-0124866 | SAN MATEO | MENLO 1102 | 3RD | 2021-10-01 12:39 | 9/27 to 10/3 | 2021-10-02 01:26 | HLT | 51229 | 277 | 10 | 2 | 7 | 0 | 0 | 767 | 184.9422
21-0124750 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-10-01 09:30 | 9/27 to 10/3 | 2021-10-01 15:37 | FTS | 309988 | 994 | 72 | 56 | 42 | 11 | 0 | 367 | 311.8592
21-0124613 | MARIPOSA | INDIAN FLAT 1104 | UNK | 2021-09-30 21:04 | 9/27 to 10/3 | 2021-09-30 23:24 | FTS | 29084 | 208 | 4 | 4 | 3 | 0 | 0 | 140 | 139.8269
21-0124563 | BUTTE | ORO FINO 1102 | UNK | 2021-09-30 17:05 | 9/27 to 10/3 | 2021-10-01 09:39 | FTS | 345411 | 348 | 22 | 15 | 12 | 2 | 0 | 994 | 992.5603
21-0124557 | BUTTE | ORO FINO 1102 | AN | 2021-09-30 17:04 | 9/27 to 10/3 | 2021-10-01 14:26 | FTS | 500846 | 1087 | 78 | 49 | 13 | 1 | 0 | 1282 | 460.7599
21-0124444 | FRESNO | DUNLAP 1102 | 3RD | 2021-09-30 13:04 | 9/27 to 10/3 | 2021-10-01 13:00 | FTS | 30800 | 308 | 6 | 4 | 7 | 0 | 0 | 1436 | 100
21-0124258 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-09-30 10:12 | 9/27 to 10/3 | 2021-09-30 13:41 | FTS | 207860 | 1564 | 64 | 42 | 10 | 0 | 0 | 209 | 132.9028
21-0124222 | CONTRA COSTA | SAN RAMON 2108 | VEG | 2021-09-30 09:07 | 9/27 to 10/3 | 2021-10-01 08:22 | FTS | 120990 | 91 | 2 | 1 | 5 | 3 | 0 | 1395 | 1329.5604
21-0124128 | SAN MATEO | HALF MOON BAY 1103 | UNK | 2021-09-30 06:50 | 9/27 to 10/3 | 2021-09-30 11:10 | FTS | 147195 | 574 | 23 | 18 | 17 | 1 | 0 | 260 | 256.4373
21-0124032 | BUTTE | ORO FINO 1102 | UNK | 2021-09-29 17:00 | 9/27 to 10/3 | 2021-09-29 20:37 | FTS | 63812 | 348 | 22 | 15 | 12 | 2 | 0 | 217 | 183.3678
21-0124030 | BUTTE | ORO FINO 1102 | AN | 2021-09-29 16:59 | 9/27 to 10/3 | 2021-09-30 09:59 | FTS | 1087753 | 1087 | 78 | 49 | 13 | 1 | 0 | 1020 | 1000.6927
21-0123654 | BUTTE | WYANDOTTE 1107 | AN | 2021-09-29 08:00 | 9/27 to 10/3 | 2021-09-29 13:59 | FTS | 66858 | 274 | 24 | 18 | 3 | 0 | 0 | 359 | 244.0073
21-0123630 | TUOLUMNE | MIWUK 1702 | AN | 2021-09-29 07:15 | 9/27 to 10/3 | 2021-09-29 09:30 | FTS | 59130 | 438 | 39 | 30 | 2 | 1 | 0 | 135 | 135
21-0123546 | SANTA BARBARA | SISQUOC 1102 | EF | 2021-09-28 19:08 | 9/27 to 10/3 | 2021-09-29 16:33 | FTS | 106465 | 129 | 0 | 0 | 1 | 0 | 0 | 1285 | 825.3101
21-0123527 | MENDOCINO | MENDOCINO 1101 | UNK | 2021-09-28 17:07 | 9/27 to 10/3 | 2021-09-28 19:46 | FTS | 118296 | 744 | 44 | 31 | 10 | 0 | 0 | 159 | 159
21-0123445 | SANTA BARBARA | SANTA YNEZ 1101 | UNK | 2021-09-28 15:02 | 9/27 to 10/3 | 2021-09-29 10:20 | FTS | 85035 | 192 | 1 | 1 | 26 | 0 | 0 | 1158 | 442.8906
21-0123290 | SAN MATEO | HALF MOON BAY 1103 | VEG | 2021-09-28 11:29 | 9/27 to 10/3 | 2021-09-28 15:30 | FTS | 480519 | 1901 | 55 | 45 | 54 | 10 | 0 | 241 | 252.7717
21-0123031 | SOLANO | VACAVILLE 1108 | UNK | 2021-09-28 03:29 | 9/27 to 10/3 | 2021-09-28 09:43 | HLT | 166940 | 418 | 20 | 14 | 14 | 1 | 0 | 374 | 399.378
21-0122942 | MARIPOSA | BEAR VALLEY 2105 | UNK | 2021-09-27 18:41 | 9/27 to 10/3 | 2021-09-28 02:13 | FTS | 84284 | 202 | 16 | 12 | 5 | 0 | 0 | 452 | 417.2475
21-0122910 | SAN MATEO | SAN CARLOS 1104 | EF | 2021-09-27 16:14 | 9/27 to 10/3 | 2021-09-27 18:46 | FTS | 29184 | 192 | 12 | 10 | 2 | 0 | 0 | 152 | 152
21-0122854 | EL DORADO | PLACERVILLE 2106 | 3RD | 2021-09-27 14:34 | 9/27 to 10/3 | 2021-09-27 19:48 | FTS | 295666 | 994 | 72 | 56 | 42 | 11 | 0 | 314 | 297.4507
21-0122720 | MARIPOSA | MARIPOSA 2102 | CI | 2021-09-27 11:42 | 9/27 to 10/3 | 2021-09-27 16:59 | HLT | 734796 | 2598 | 196 | 138 | 42 | 6 | 0 | 317 | 282.8314
21-0122531 | FRESNO | PANOCHE 1103 | AN | 2021-09-26 22:42 | 9/20 to 9/26 | 2021-09-27 09:29 | HLT | 1941 | 3 | 0 | 0 | 0 | 0 | 0 | 647 | 647
21-0122534 | FRESNO | PANOCHE 1103 | AN | 2021-09-26 22:41 | 9/20 to 9/26 | 2021-09-27 10:42 | HLT | 149680 | 208 | 2 | 2 | 8 | 1 | 0 | 721 | 719.6154
21-0122525 | SAN MATEO | HALF MOON BAY 1103 | VEG | 2021-09-26 20:10 | 9/20 to 9/26 | 2021-09-27 20:18 | HLT | 2740859 | 2984 | 89 | 69 | 64 | 12 | 0 | 1381 | 918.5184
21-0122519 | SANTA CLARA | LLAGAS 2101 | 3RD | 2021-09-26 19:09 | 9/20 to 9/26 | 2021-09-27 11:28 | HLT | 252314 | 1002 | 49 | 33 | 16 | 2 | 0 | 979 | 251.8104
21-0122510 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-09-26 17:59 | 9/20 to 9/26 | 2021-09-27 13:39 | FTS | 1573658 | 3117 | 161 | 113 | 50 | 2 | 1 | 1180 | 504.863
21-0122507 | SIERRA | ALLEGHANY 1101 | UNK | 2021-09-26 17:32 | 9/20 to 9/26 | 2021-09-27 15:02 | FTS | 1023103 | 908 | 28 | 23 | 19 | 1 | 0 | 1290 | 1126.7654
21-0122429 | EL DORADO | SHINGLE SPRINGS 2110 | UNK | 2021-09-26 06:05 | 9/20 to 9/26 | 2021-09-26 10:23 | FTS | 307797 | 1293 | 93 | 61 | 23 | 8 | 0 | 258 | 238.0487
21-0122425 | SHASTA | JESSUP 1101 | 3RD | 2021-09-26 01:47 | 9/20 to 9/26 | 2021-09-26 12:54 | FTS | 370861 | 1794 | 175 | 123 | 19 | 4 | 0 | 667 | 206.723
21-0122381 | SANTA CRUZ | BEN LOMOND 0401 | VEG | 2021-09-25 13:54 | 9/20 to 9/26 | 2021-09-25 22:34 | FTS | 21640 | 124 | 14 | 10 | 2 | 0 | 0 | 520 | 174.5161
21-0122316 | TEHAMA | RED BLUFF 1103 | UNK | 2021-09-25 09:43 | 9/20 to 9/26 | 2021-09-25 12:52 | HLT | 359809 | 2723 | 222 | 153 | 30 | 12 | 1 | 189 | 132.137
21-0122304 | NEVADA | BRUNSWICK 1105 | UNK | 2021-09-25 09:15 | 9/20 to 9/26 | 2021-09-25 18:00 | FTS | 557504 | 1083 | 65 | 41 | 24 | 0 | 0 | 525 | 514.7775
21-0122342 | SONOMA | GEYSERVILLE 1101 | UNK | 2021-09-25 09:02 | 9/20 to 9/26 | 2021-09-25 13:47 | HLT | 26729 | 120 | 3 | 2 | 1 | 0 | 0 | 285 | 222.7417
21-0122301 | SONOMA | GEYSERVILLE 1101 | UNK | 2021-09-25 08:59 | 9/20 to 9/26 | 2021-09-25 13:28 | HLT | 92240 | 414 | 9 | 6 | 4 | 0 | 0 | 269 | 222.8019
21-0122279 | BUTTE | ORO FINO 1102 | AN | 2021-09-25 07:16 | 9/20 to 9/26 | 2021-09-25 14:23 | FTS | 76003 | 377 | 28 | 16 | 4 | 0 | 0 | 427 | 201.5995
21-0122255 | SANTA CRUZ | GREEN VALLEY 2101 | UNK | 2021-09-24 21:39 | 9/20 to 9/26 | 2021-09-25 00:31 | FTS | 81161 | 1013 | 85 | 69 | 9 | 1 | 0 | 172 | 80.1194
21-0122159 | MENDOCINO | MENDOCINO 1101 | 3RD | 2021-09-24 14:21 | 9/20 to 9/26 | 2021-09-24 22:22 | FTS | 133213 | 744 | 44 | 31 | 10 | 0 | 0 | 481 | 179.0497
21-0121891 | BUTTE | ORO FINO 1102 | UNK | 2021-09-24 08:54 | 9/20 to 9/26 | 2021-09-24 12:40 | FTS | 78147 | 348 | 22 | 15 | 12 | 2 | 0 | 226 | 224.5603
21-0121885 |  | LOW GAP 1101 | UNK | 2021-09-24 08:49 | 9/20 to 9/26 | 2021-09-24 15:44 | HLT | 268146 | 734 | 27 | 19 | 12 | 3 | 0 | 415 | 365.3215
21-0121856 | SANTA CRUZ | ROB ROY 2104 | UNK | 2021-09-24 07:52 | 9/20 to 9/26 | 2021-09-24 13:38 | FTS | 776909 | 2389 | 153 | 127 | 34 | 6 | 0 | 346 | 325.2026
21-0121833 | SHASTA | GIRVAN 1101 | EF | 2021-09-24 06:43 | 9/20 to 9/26 | 2021-09-24 13:37 | HLT | 308351 | 1176 | 86 | 56 | 30 | 6 | 0 | 414 | 262.2032
21-0121815 | LAKE | KONOCTI 1102 | UNK | 2021-09-24 02:00 | 9/20 to 9/26 | 2021-09-24 12:17 | HLT | 422386 | 774 | 42 | 30 | 13 | 0 | 0 | 617 | 545.7183
21-0121724 | SAN MATEO | HALF MOON BAY 1103 | 3RD | 2021-09-23 15:32 | 9/20 to 9/26 | 2021-09-24 10:04 | HLT | 94213 | 355 | 15 | 13 | 7 | 0 | 0 | 1112 | 265.3887
21-0121723 | EL DORADO | EL DORADO PH 2101 | 3RD | 2021-09-23 15:19 | 9/20 to 9/26 | 2021-09-23 23:31 | FTS | 358524 | 2082 | 174 | 128 | 33 | 3 | 0 | 492 | 172.2017
21-0121654 |  | LOW GAP 1101 | EF | 2021-09-23 14:01 | 9/20 to 9/26 | 2021-09-23 14:36 | HLT | 25760 | 736 | 27 | 19 | 12 | 3 | 0 | 35 | 35
21-0121635 | STANISLAUS | WESTLEY 1103 | UNK | 2021-09-23 13:49 | 9/20 to 9/26 | 2021-09-23 15:42 | HLT | 7797 | 69 | 0 | 0 | 0 | 0 | 0 | 113 | 113
21-0121326 | SANTA CLARA | LOS GATOS 1107 | UNK | 2021-09-23 07:02 | 9/20 to 9/26 | 2021-09-23 10:57 | FTS | 164764 | 934 | 61 | 39 | 28 | 0 | 0 | 235 | 176.4069
21-0121302 | TULARE | SAND CREEK 1103 | UNK | 2021-09-23 02:02 | 9/20 to 9/26 | 2021-09-23 11:02 | FTS | 159210 | 296 | 8 | 5 | 12 | 1 | 0 | 540 | 537.8716
21-0121242 | KERN | TEJON 1102 | AN | 2021-09-22 18:58 | 9/20 to 9/26 | 2021-09-22 22:00 | HLT | 4004 | 22 | 0 | 0 | 4 | 0 | 0 | 182 | 182
21-0121166 | NAPA | SILVERADO 2102 | CI | 2021-09-22 14:36 | 9/20 to 9/26 | 2021-09-22 17:03 | HLT | 40425 | 275 | 1 | 1 | 6 | 0 | 0 | 147 | 147
21-0121024 | NAPA | SILVERADO 2104 | UNK | 2021-09-22 12:08 | 9/20 to 9/26 | 2021-09-22 16:27 | FTS | 191142 | 738 | 29 | 17 | 17 | 3 | 0 | 259 | 259
21-0120921 | EL DORADO | EL DORADO PH 2101 | UNK | 2021-09-22 09:57 | 9/20 to 9/26 | 2021-09-22 13:43 | FTS | 99984 | 436 | 10 | 6 | 38 | 1 | 0 | 226 | 229.3211
21-0120882 | NAPA | SILVERADO 2104 | UNK | 2021-09-22 09:42 | 9/20 to 9/26 | 2021-09-22 14:24 | FTS | 119460 | 522 | 32 | 22 | 15 | 1 | 3 | 282 | 228.8506
21-0120849 | SANTA CRUZ | BEN LOMOND 1101 | AN | 2021-09-22 08:57 | 9/20 to 9/26 | 2021-09-22 12:00 | FTS | 51240 | 280 | 18 | 15 | 7 | 0 | 0 | 183 | 183
21-0120834 | SHASTA | GIRVAN 1102 | UNK | 2021-09-22 08:39 | 9/20 to 9/26 | 2021-09-22 11:22 | HLT | 57213 | 351 | 32 | 25 | 4 | 0 | 0 | 163 | 163
21-0120763 | CALAVERAS | FROGTOWN 1702 | UNK | 2021-09-22 07:16 | 9/20 to 9/26 | 2021-09-22 10:03 | FTS | 26052 | 156 | 4 | 3 | 3 | 0 | 0 | 167 | 167
21-0120753 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-09-22 06:59 | 9/20 to 9/26 | 2021-09-22 13:58 | HLT | 216380 | 926 | 51 | 33 | 19 | 0 | 0 | 419 | 233.6717
21-0120751 | CONTRA COSTA | SAN RAMON 2108 | AN | 2021-09-22 06:47 | 9/20 to 9/26 | 2021-09-22 11:25 | FTS | 405152 | 3806 | 159 | 114 | 40 | 5 | 0 | 278 | 106.4509
21-0120749 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-09-22 06:42 | 9/20 to 9/26 | 2021-09-22 11:56 | HLT | 629502 | 2025 | 157 | 118 | 60 | 16 | 0 | 314 | 310.8652
21-0120384 | TEHAMA | RED BLUFF 1103 | AN | 2021-09-21 10:05 | 9/20 to 9/26 | 2021-09-21 22:37 | HLT | 484784 | 2723 | 222 | 153 | 30 | 12 | 1 | 752 | 178.0331
21-0120335 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-09-21 09:23 | 9/20 to 9/26 | 2021-09-21 12:39 | FTS | 178007 | 1114 | 91 | 70 | 22 | 0 | 0 | 196 | 159.7908
21-0120333 | SAN BENITO | SAN JUSTO 1101 | UNK | 2021-09-21 09:22 | 9/20 to 9/26 | 2021-09-21 14:06 | FTS | 25677 | 170 | 8 | 4 | 13 | 0 | 0 | 284 | 151.0412
21-0120332 | SHASTA | GIRVAN 1102 | UNK | 2021-09-21 09:12 | 9/20 to 9/26 | 2021-09-21 13:26 | HLT | 89154 | 351 | 32 | 25 | 4 | 0 | 0 | 254 | 254
21-0120319 | BUTTE | BANGOR 1101 | EF | 2021-09-21 09:00 | 9/20 to 9/26 | 2021-09-21 15:34 | FTS | 146702 | 425 | 39 | 25 | 2 | 0 | 0 | 394 | 345.1812
21-0120250 | SAN MATEO | WOODSIDE 1104 | UNK | 2021-09-21 06:56 | 9/20 to 9/26 | 2021-09-21 12:04 | FTS | 20020 | 65 | 0 | 0 | 1 | 0 | 0 | 308 | 308
21-0120253 | SAN MATEO | WOODSIDE 1104 | UNK | 2021-09-21 06:56 | 9/20 to 9/26 | 2021-09-21 11:52 | FTS | 83672 | 351 | 14 | 8 | 13 | 1 | 0 | 296 | 238.3818
21-0120241 | SANTA CRUZ | CAMP EVERS 2106 | UNK | 2021-09-21 06:36 | 9/20 to 9/26 | 2021-09-21 10:23 | HLT | 64499 | 451 | 0 | 0 | 0 | 0 | 0 | 227 | 143.0133
21-0120158 | SAN MATEO | HALF MOON BAY 1101 | VEG | 2021-09-20 16:32 | 9/20 to 9/26 | 2021-09-21 17:03 | FTS | 47782 | 41 | 1 | 1 | 1 | 1 | 0 | 1262 | 1165.4146
21-0120133 | EL DORADO | APPLE HILL 2102 | UNK | 2021-09-20 15:56 | 9/20 to 9/26 | 2021-09-21 11:24 | HLT | 594944 | 674 | 54 | 34 | 7 | 0 | 0 | 1168 | 882.7062
21-0120059 | SHASTA | DESCHUTES 1104 | 3RD | 2021-09-20 14:27 | 9/20 to 9/26 | 2021-09-21 01:05 | HLT | 97664 | 453 | 32 | 17 | 4 | 0 | 0 | 638 | 215.5938
21-0119895 | SANTA CLARA | MENLO 1103 | 3RD | 2021-09-20 10:49 | 9/20 to 9/26 | 2021-09-20 19:57 | HLT | 100231 | 300 | 14 | 11 | 5 | 0 | 0 | 548 | 334.1033
21-0119809 | SANTA CRUZ | CAMP EVERS 2105 | AN | 2021-09-20 09:05 | 9/20 to 9/26 | 2021-09-20 19:34 | FTS | 2590190 | 5648 | 465 | 367 | 89 | 8 | 0 | 629 | 458.603
21-0119783 | EL DORADO | EL DORADO PH 2101 | UNK | 2021-09-20 08:10 | 9/20 to 9/26 | 2021-09-20 13:22 | HLT | 235732 | 620 | 25 | 16 | 54 | 1 | 0 | 312 | 380.2129
21-0119773 | YOLO | PUTAH CREEK 1102 | AN | 2021-09-20 07:50 | 9/20 to 9/26 | 2021-09-20 13:10 | HLT | 85896 | 271 | 8 | 5 | 5 | 0 | 0 | 320 | 316.9594
21-0119519 | TUOLUMNE | SPRING GAP 1702 | UNK | 2021-09-19 07:07 | 9/13 to 9/19 | 2021-09-19 13:03 | HLT | 519774 | 1538 | 29 | 20 | 18 | 2 | 0 | 356 | 337.9545
21-0119483 | NAPA | PUEBLO 2103 | VEG | 2021-09-19 01:30 | 9/13 to 9/19 | 2021-09-19 14:46 | HLT | 58216 | 76 | 1 | 1 | 0 | 0 | 0 | 755 | 766
21-0119438 | SONOMA | GEYSERVILLE 1101 | 3RD | 2021-09-18 20:18 | 9/13 to 9/19 | 2021-09-18 22:12 | HLT | 49818 | 437 | 10 | 7 | 4 | 0 | 0 | 114 | 114
21-0119427 | SONOMA | MONTE RIO 1111 | VEG | 2021-09-18 19:02 | 9/13 to 9/19 | 2021-09-18 20:10 | HLT | 94842 | 1483 | 72 | 43 | 33 | 3 | 0 | 68 | 63.9528
21-0119424 | EL DORADO | SHINGLE SPRINGS 2110 | UNK | 2021-09-18 18:23 | 9/13 to 9/19 | 2021-09-18 21:22 | FTS | 710713 | 1005 | 78 | 50 | 15 | 7 | 0 | 179 | 707.1771
21-0119362 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-09-18 11:52 | 9/13 to 9/19 | 2021-09-18 15:44 | HLT | 69600 | 300 | 15 | 10 | 3 | 0 | 0 | 232 | 232
21-0119345 | SAN MATEO | HALF MOON BAY 1103 | UNK | 2021-09-18 11:11 | 9/13 to 9/19 | 2021-09-19 16:45 | HLT | 3694000 | 2984 | 89 | 69 | 64 | 12 | 0 | 1774 | 1237.9357
21-0119250 | HUMBOLDT | WILLOW CREEK 1103 | UNK | 2021-09-18 08:32 | 9/13 to 9/19 | 2021-09-19 07:55 | HLT | 730504 | 1271 | 77 | 56 | 13 | 3 | 0 | 1403 | 574.7474
21-0119239 | MENDOCINO | POTTER VALLEY P H 1105 | EF | 2021-09-18 08:16 | 9/13 to 9/19 | 2021-09-18 18:25 | HLT | 482660 | 1119 | 56 | 37 | 17 | 7 | 0 | 609 | 431.3315
21-0119227 | SONOMA | MOLINO 1102 | UNK | 2021-09-18 06:49 | 9/13 to 9/19 | 2021-09-18 20:02 | HLT | 1105127 | 2095 | 116 | 77 | 26 | 1 | 0 | 792 | 527.5069
21-0119189 | ALAMEDA | VASCO 1102 | 3RD | 2021-09-17 19:06 | 9/13 to 9/19 | 2021-09-18 10:38 | FTS | 247062 | 277 | 13 | 12 | 3 | 0 | 0 | 932 | 891.9206
21-0118783 | SAN LUIS OBISPO | TEMPLETON 2110 | UNK | 2021-09-17 09:07 | 9/13 to 9/19 | 2021-09-18 13:45 | HLT | 1435413 | 1003 | 35 | 23 | 13 | 0 | 0 | 1718 | 1431.1196
21-0118761 | SHASTA | GIRVAN 1102 | UNK | 2021-09-17 08:26 | 9/13 to 9/19 | 2021-09-17 11:26 | HLT | 98280 | 546 | 31 | 25 | 8 | 0 | 0 | 180 | 180
21-0118754 | LAKE | MIDDLETOWN 1101 | UNK | 2021-09-17 08:25 | 9/13 to 9/19 | 2021-09-17 14:43 | HLT | 550957 | 2085 | 94 | 63 | 39 | 7 | 0 | 378 | 264.248
21-0118695 | SAN LUIS OBISPO | TEMPLETON 2113 | AN | 2021-09-17 06:35 | 9/13 to 9/19 | 2021-09-17 18:23 | HLT | 1413692 | 3113 | 161 | 113 | 50 | 2 | 1 | 708 | 454.1253
21-0118686 | SAN MATEO | BELMONT 1103 | UNK | 2021-09-17 06:08 | 9/13 to 9/19 | 2021-09-17 07:41 | HLT | 94860 | 5955 | 86 | 60 | 45 | 5 | 0 | 93 | 15.9295
21-0118608 | MONTEREY | OTTER 1101 | VEG | 2021-09-16 16:17 | 9/13 to 9/19 | 2021-09-16 18:25 | HLT | 48128 | 376 | 13 | 8 | 5 | 1 | 0 | 128 | 128
21-0118545 | NAPA | PUEBLO 2103 | UNK | 2021-09-16 14:38 | 9/13 to 9/19 | 2021-09-16 18:04 | HLT | 65096 | 316 | 6 | 4 | 3 | 2 | 0 | 206 | 206
21-0118278 | TUOLUMNE | CURTIS 1705 | 3RD | 2021-09-16 09:07 | 9/13 to 9/19 | 2021-09-16 12:19 | HLT | 77303 | 682 | 66 | 40 | 7 | 5 | 0 | 192 | 113.3475
21-0118200 | SANTA CRUZ | CAMP EVERS 2105 | AN | 2021-09-16 06:58 | 9/13 to 9/19 | 2021-09-16 14:51 | FTS | 203863 | 431 | 38 | 27 | 11 | 0 | 0 | 473 | 473
21-0118193 | SAN LUIS OBISPO | ATASCADERO 1103 | UNK | 2021-09-16 06:31 | 9/13 to 9/19 | 2021-09-16 12:16 | HLT | 70292 | 223 | 7 | 4 | 3 | 0 | 0 | 345 | 315.2108
21-0118150 | SANTA CRUZ | BEN LOMOND 0401 | UNK | 2021-09-15 20:57 | 9/13 to 9/19 | 2021-09-16 10:33 | FTS | 101184 | 124 | 14 | 10 | 2 | 0 | 0 | 816 | 816
21-0118131 | SANTA CRUZ | BIG BASIN 1102 | UNK | 2021-09-15 18:50 | 9/13 to 9/19 | 2021-09-16 13:49 | HLT | 1879611 | 1695 | 105 | 74 | 25 | 1 | 0 | 1139 | 1108.915
21-0118112 | SONOMA | FULTON 1107 | VEG | 2021-09-15 17:17 | 9/13 to 9/19 | 2021-09-16 02:45 | HLT | 47504 | 448 | 23 | 18 | 12 | 0 | 0 | 568 | 106.0357
21-0117771 | EL DORADO | APPLE HILL 2102 | UNK | 2021-09-15 10:14 | 9/13 to 9/19 | 2021-09-15 14:40 | HLT | 2154781 | 2675 | 202 | 143 | 39 | 8 | 0 | 266 | 805.5256
21-0117696 | MARIN | WOODACRE 1101 | UNK | 2021-09-15 08:31 | 9/13 to 9/19 | 2021-09-15 12:13 | FTS | 140638 | 740 | 41 | 25 | 19 | 1 | 0 | 222 | 190.0514
21-0117623 | SONOMA | MOLINO 1102 | EF | 2021-09-15 01:54 | 9/13 to 9/19 | 2021-09-15 19:12 | HLT | 1110165 | 2095 | 116 | 77 | 26 | 1 | 0 | 1038 | 529.9117
21-0117600 | SAN LUIS OBISPO | CAYUCOS 1102 | UNK | 2021-09-14 19:36 | 9/13 to 9/19 | 2021-09-15 18:50 | HLT | 20548 | 52 | 0 | 0 | 0 | 0 | 0 | 1394 | 395.1538
21-0117590 | AMADOR | ELECTRA 1101 | UNK | 2021-09-14 19:08 | 9/13 to 9/19 | 2021-09-15 08:34 | HLT | 502138 | 623 | 67 | 43 | 7 | 0 | 0 | 806 | 806
21-0117557 | PLACER | SHADY GLEN 1101 | AN | 2021-09-14 16:07 | 9/13 to 9/19 | 2021-09-14 21:35 | HLT | 114407 | 487 | 38 | 27 | 12 | 4 | 0 | 328 | 234.922
21-0117508 | MARIPOSA | INDIAN FLAT 1104 | EF | 2021-09-14 15:09 | 9/13 to 9/19 | 2021-09-16 16:08 | HLT | 152941 | 209 | 4 | 4 | 3 | 0 | 0 | 1401 | 731.7751
21-0117249 | PLUMAS | GANSNER 1101 | 3RD | 2021-09-14 09:07 | 9/13 to 9/19 | 2021-09-14 17:26 | HLT | 92327 | 205 | 11 | 8 | 4 | 0 | 0 | 499 | 450.3756
21-0117250 | BUTTE | BANGOR 1101 | EF | 2021-09-14 08:39 | 9/13 to 9/19 | 2021-09-14 12:20 | FTS | 93659 | 425 | 39 | 25 | 2 | 0 | 0 | 221 | 220.3741
21-0117167 | HUMBOLDT | WILLOW CREEK 1103 | UNK | 2021-09-14 07:43 | 9/13 to 9/19 | 2021-09-14 18:10 | HLT | 722671 | 1271 | 77 | 56 | 13 | 3 | 0 | 627 | 568.5846
21-0117157 | NAPA | PUEBLO 2103 | UNK | 2021-09-14 07:25 | 9/13 to 9/19 | 2021-09-14 15:52 | HLT | 87010 | 316 | 6 | 4 | 3 | 2 | 0 | 507 | 275.3481
21-0117135 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-09-14 06:46 | 9/13 to 9/19 | 2021-09-14 14:22 | FTS | 398599 | 1097 | 88 | 68 | 21 | 0 | 0 | 456 | 363.3537
21-0117097 | NEVADA | COLUMBIA HILL 1101 | UNK | 2021-09-14 00:17 | 9/13 to 9/19 | 2021-09-14 14:49 | HLT | 226720 | 260 | 40 | 35 | 3 | 2 | 0 | 872 | 872
21-0117060 | SANTA CRUZ | BIG BASIN 1102 | UNK | 2021-09-13 19:35 | 9/13 to 9/19 | 2021-09-14 11:24 | HLT | 165195 | 475 | 34 | 24 | 4 | 0 | 0 | 949 | 347.7789
21-0117038 | CONTRA COSTA | CLAYTON 2212 | CI | 2021-09-13 17:45 | 9/13 to 9/19 | 2021-09-14 10:22 | HLT | 1197282 | 3431 | 289 | 192 | 84 | 8 | 0 | 997 | 348.9601
21-0117031 | SAN LUIS OBISPO | ATASCADERO 1103 | AN | 2021-09-13 17:32 | 9/13 to 9/19 | 2021-09-14 17:40 | HLT | 1665582 | 2417 | 117 | 77 | 45 | 4 | 0 | 1448 | 689.1113
21-0117009 | TUOLUMNE | CURTIS 1705 | UNK | 2021-09-13 16:13 | 9/13 to 9/19 | 2021-09-13 19:37 | HLT | 139128 | 682 | 66 | 40 | 7 | 5 | 0 | 204 | 204
21-0116930 | SANTA BARBARA | SANTA YNEZ 1104 | CI | 2021-09-13 13:53 | 9/13 to 9/19 | 2021-09-13 21:40 | HLT | 65380 | 140 | 0 | 0 | 0 | 0 | 0 | 467 | 467
21-0116901 | SONOMA | FULTON 1107 | VEG | 2021-09-13 13:17 | 9/13 to 9/19 | 2021-09-13 18:53 | HLT | 59204 | 451 | 23 | 18 | 12 | 0 | 0 | 336 | 131.2727
21-0116932 | MONTEREY | OTTER 1101 | VEG | 2021-09-13 11:54 | 9/13 to 9/19 | 2021-09-13 22:43 | HLT | 90211 | 139 | 7 | 3 | 2 | 0 | 0 | 649 | 649
21-0116781 | BUTTE | ORO FINO 1102 | UNK | 2021-09-13 10:30 | 9/13 to 9/19 | 2021-09-13 15:14 | HLT | 98832 | 348 | 22 | 15 | 12 | 2 | 0 | 284 | 284
21-0116778 | BUTTE | ORO FINO 1101 | EF | 2021-09-13 10:28 | 9/13 to 9/19 | 2021-09-13 17:12 | HLT | 422180 | 1045 | 133 | 96 | 11 | 1 | 0 | 404 | 404
21-0116787 | SONOMA | GEYSERVILLE 1102 | UNK | 2021-09-13 09:23 | 9/13 to 9/19 | 2021-09-13 11:45 | HLT | 2982 | 21 | 2 | 2 | 0 | 0 | 0 | 142 | 142
21-0116643 | SANTA CRUZ | CAMP EVERS 2105 | AN | 2021-09-13 08:04 | 9/13 to 9/19 | 2021-09-13 13:44 | FTS | 585824 | 1974 | 0 | 0 | 0 | 0 | 0 |  | 296.77
21-0116603 | CALAVERAS | WEST POINT 1102 | VEG | 2021-09-13 06:21 | 9/13 to 9/19 | 2021-09-13 12:12 | HLT | 258336 | 736 | 48 | 34 | 7 | 0 | 0 | 351 | 351
21-0116600 | SONOMA | GEYSERVILLE 1102 | 3RD | 2021-09-13 05:53 | 9/13 to 9/19 | 2021-09-13 09:25 | HLT | 119709 | 567 | 14 | 6 | 13 | 2 | 0 | 212 | 211.127
21-0116590 | CALAVERAS | FROGTOWN 1702 | 3RD | 2021-09-13 03:15 | 9/13 to 9/19 | 2021-09-13 13:43 | HLT | 399562 | 876 | 38 | 24 | 30 | 2 | 0 | 628 | 456.121
21-0116577 | TEHAMA | COTTONWOOD 1103 | VEG | 2021-09-12 20:55 | 9/6 to 9/12 | 2021-09-14 01:19 | HLT | 565303 | 704 | 63 | 43 | 18 | 0 | 0 | 1704 | 802.9872
21-0116482 | PLACER | SHADY GLEN 1101 | UNK | 2021-09-12 07:19 | 9/6 to 9/12 | 2021-09-12 15:01 | HLT | 111804 | 242 | 23 | 17 | 0 | 0 | 0 | 462 | 462
21-0116478 | MADERA | OAKHURST 1103 | UNK | 2021-09-12 07:00 | 9/6 to 9/12 | 2021-09-12 14:19 | HLT | 146626 | 334 | 29 | 25 | 7 | 0 | 0 | 439 | 439
21-0116476 | SAN MATEO | HALF MOON BAY 1103 | UNK | 2021-09-12 06:41 | 9/6 to 9/12 | 2021-09-12 18:40 | HLT | 1245710 | 1902 | 55 | 45 | 54 | 10 | 0 | 719 | 654.9474
21-0116474 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-09-12 06:13 | 9/6 to 9/12 | 2021-09-12 16:26 | HLT | 1223544 | 3115 | 161 | 113 | 50 | 2 | 1 | 613 | 392.791
21-0116466 | PLACER | FORESTHILL 1101 | UNK | 2021-09-11 23:26 | 9/6 to 9/12 | 2021-09-12 00:04 | HLT | [9 empty] | Outage data under further review
21-0116419 | BUTTE | BANGOR 1101 | UNK | 2021-09-11 13:29 | 9/6 to 9/12 | 2021-09-11 17:09 | HLT | 92968 | 425 | 39 | 25 | 2 | 0 | 0 | 220 | 218.7482
21-0116391 | NEVADA | BRUNSWICK 1103 | AN | 2021-09-11 09:38 | 9/6 to 9/12 | 2021-09-11 12:36 | HLT | 23140 | 130 | 0 | 0 | 4 | 0 | 0 | 178 | 178
21-0116352 | EL DORADO | PLACERVILLE 2106 | CI | 2021-09-11 09:14 | 9/6 to 9/12 | 2021-09-11 10:36 | HLT | 220665 | 2970 | 229 | 169 | 65 | 16 | 0 | 82 | 74.298
21-0116260 | NAPA | SILVERADO 2104 | EF | 2021-09-10 18:14 | 9/6 to 9/12 | 2021-09-11 16:07 | HLT | 748790 | 738 | 29 | 17 | 17 | 3 | 0 | 1313 | 1014.6206
21-0116282 | SANTA CRUZ | CAMP EVERS 2105 | AN | 2021-09-10 17:56 | 9/6 to 9/12 | 2021-09-12 16:57 | HLT | 4358003 | 5198 | 404 | 317 | 84 | 8 | 0 | 1460 | 838.4
21-0116165 | CALAVERAS | WEST POINT 1102 | UNK | 2021-09-10 14:34 | 9/6 to 9/12 | 2021-09-10 18:46 | HLT | 169688 | 737 | 48 | 34 | 7 | 0 | 0 | 252 | 230.2415
21-0115903 | PLACER | SHADY GLEN 1101 | CI | 2021-09-10 10:05 | 9/6 to 9/12 | 2021-09-10 10:44 | HLT | 38454 | 986 | 63 | 41 | 13 | 1 | 0 | 39 | 39
21-0115857 | SHASTA | JESSUP 1101 | UNK | 2021-09-10 09:18 | 9/6 to 9/12 | 2021-09-10 17:06 | FTS | 668924 | 2040 | 192 | 131 | 22 | 5 | 0 | 468 | 327.9039
21-0115836 | SANTA BARBARA | SISQUOC 1102 | UNK | 2021-09-10 08:49 | 9/6 to 9/12 | 2021-09-10 14:53 | HLT | 25480 | 70 | 5 | 2 | 1 | 0 | 0 | 364 | 364
21-0115798 | EL DORADO | SHINGLE SPRINGS 2110 | 3RD | 2021-09-10 08:13 | 9/6 to 9/12 | 2021-09-10 18:46 | HLT | 313378 | 1005 | 78 | 50 | 15 | 7 | 0 | 633 | 311.8189
21-0115755 | PLUMAS | GANSNER 1101 | UNK | 2021-09-10 07:19 | 9/6 to 9/12 | 2021-09-10 15:41 | HLT | 102408 | 204 | 11 | 8 | 4 | 0 | 0 | 502 | 502
21-0115756 | TUOLUMNE | CURTIS 1704 | UNK | 2021-09-10 07:14 | 9/6 to 9/12 | 2021-09-10 13:20 | HLT | 471482 | 1557 | 168 | 122 | 16 | 0 | 0 | 366 | 302.8144
21-0115696 | CALAVERAS | FROGTOWN 1702 | ENV | 2021-09-10 03:24 | 9/6 to 9/12 | 2021-09-10 14:12 | HLT | 148683 | 377 | 17 | 13 | 17 | 0 | 1 | 648 | 394.3846
21-0115688 | LAKE | HIGHLANDS 1103 | ENV | 2021-09-10 02:48 | 9/6 to 9/12 | 2021-09-10 16:17 | HLT | 23867 | 56 | 3 | 2 | 7 | 3 | 0 | 809 | 426.1964
21-0115674 | SONOMA | GEYSERVILLE 1102 | UNK | 2021-09-10 01:19 | 9/6 to 9/12 | 2021-09-10 14:05 | HLT | 284725 | 381 | 4 | 2 | 15 | 1 | 0 | 766 | 747.3097
21-0115671 | SONOMA | GEYSERVILLE 1102 | ENV | 2021-09-10 01:17 | 9/6 to 9/12 | 2021-09-10 16:11 | HLT | 426617 | 567 | 14 | 6 | 13 | 2 | 0 | 893 | 752.4109
21-0115661 | CALAVERAS | WEST POINT 1102 | UNK | 2021-09-10 00:35 | 9/6 to 9/12 | 2021-09-10 14:13 | HLT | 603684 | 738 | 48 | 34 | 7 | 0 | 0 | 818 | 818
21-0115662 | CALAVERAS | WEST POINT 1102 | UNK | 2021-09-10 00:35 | 9/6 to 9/12 | 2021-09-10 15:05 | HLT | 953281 | 1228 | 83 | 59 | 20 | 0 | 0 | 870 | 776.2875
21-0115621 | SANTA CLARA | LOS GATOS 1106 | UNK | 2021-09-09 21:39 | 9/6 to 9/12 | 2021-09-10 17:11 | HLT | 1702333 | 1678 | 126 | 88 | 30 | 3 | 0 | 1172 | 1014.5012
21-0115615 | GLENN | ELK CREEK 1101 | UNK | 2021-09-09 21:25 | 9/6 to 9/12 | 2021-09-10 10:35 | HLT | 254380 | 322 | 23 | 19 | 11 | 5 | 0 | 790 | 790
21-0115614 | FRESNO | TIVY VALLEY 1107 | UNK | 2021-09-09 20:49 | 9/6 to 9/12 | 2021-09-10 09:51 | HLT | 400476 | 515 | 49 | 29 | 3 | 0 | 0 | 782 | 777.6233
21-0115611 | MADERA | COARSEGOLD 2104 | UNK | 2021-09-09 20:46 | 9/6 to 9/12 | 2021-09-10 13:45 | HLT | 3446878 | 3737 | 400 | 276 | 74 | 8 | 0 | 1019 | 922.365
21-0115606 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-09-09 20:29 | 9/6 to 9/12 | 2021-09-10 20:36 | HLT | 4003465 | 3005 | 231 | 171 | 67 | 16 | 0 | 1447 | 1332.2679
21-0115594 | SANTA CLARA | LLAGAS 2101 | 3RD | 2021-09-09 17:57 | 9/6 to 9/12 | 2021-09-10 15:46 | HLT | 362924 | 1002 | 49 | 33 | 16 | 2 | 0 | 1309 | 362.1996
21-0115426 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-09-09 13:23 | 9/6 to 9/12 | 2021-09-10 11:59 | HLT | 276570 | 410 | 18 | 12 | 8 | 0 | 0 | 1356 | 674.561
21-0115403 | TUOLUMNE | CURTIS 1703 | VEG | 2021-09-09 12:54 | 9/6 to 9/12 | 2021-09-10 10:26 | HLT | 247351 | 602 | 39 | 34 | 17 | 0 | 0 | 1292 | 410.8821
21-0115362 | BUTTE | BANGOR 1101 | UNK | 2021-09-09 12:22 | 9/6 to 9/12 | 2021-09-09 17:14 | HLT | 124100 | 425 | 39 | 25 | 2 | 0 | 0 | 292 | 292
21-0115295 | SAN LUIS OBISPO | ATASCADERO 1103 | 3RD | 2021-09-09 11:05 | 9/6 to 9/12 | 2021-09-10 10:41 | HLT | 962484 | 1664 | 73 | 48 | 24 | 2 | 0 | 1416 | 578.4159
21-0115171 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-09-09 09:49 | 9/6 to 9/12 | 2021-09-09 16:02 | HLT | 923471 | 2909 | 225 | 156 | 45 | 0 | 0 | 373 | 317.4531
21-0115039 | SANTA CRUZ | ROB ROY 2104 | VEG | 2021-09-09 04:25 | 9/6 to 9/12 | 2021-09-09 13:00 | HLT | 1045908 | 2392 | 154 | 128 | 34 | 6 | 0 | 515 | 437.2525
21-0114996 | SANTA CRUZ | PAUL SWEET 2106 | VEG | 2021-09-08 22:02 | 9/6 to 9/12 | 2021-09-09 13:20 | HLT | 210834 | 347 | 38 | 34 | 5 | 1 | 0 | 918 | 607.5908
21-0114970 | EL DORADO | EL DORADO PH 2101 | VEG | 2021-09-08 20:02 | 9/6 to 9/12 | 2021-09-09 15:29 | HLT | 2233281 | 2082 | 174 | 128 | 33 | 3 | 0 | 1167 | 1072.6614
21-0114968 | SOLANO | PUTAH CREEK 1102 | UNK | 2021-09-08 19:56 | 9/6 to 9/12 | 2021-09-09 11:10 | HLT | 246056 | 271 | 8 | 5 | 5 | 0 | 0 | 914 | 907.9557
21-0114942 | SAN MATEO | MENLO 1102 | CI | 2021-09-08 17:39 | 9/6 to 9/12 | 2021-09-09 12:58 | HLT | 87899 | 301 | 9 | 8 | 8 | 0 | 0 | 1159 | 292.0233
21-0114541 | BUTTE | BANGOR 1101 | UNK | 2021-09-08 08:36 | 9/6 to 9/12 | 2021-09-08 13:42 | HLT | 130050 | 425 | 39 | 25 | 2 | 0 | 0 | 306 | 306
21-0114402 | LAKE | KONOCTI 1102 | VEG | 2021-09-07 16:31 | 9/6 to 9/12 | 2021-09-08 13:25 | HLT | 2187044 | 2912 | 171 | 119 | 61 | 18 | 0 | 1254 | 751.0453
21-0114321 | MADERA | COARSEGOLD 2104 | VEG | 2021-09-07 14:36 | 9/6 to 9/12 | 2021-09-07 23:23 | HLT | 442448 | 1583 | 163 | 123 | 21 | 1 | 0 | 527 | 279.4997
21-0114222 | SANTA CRUZ | GREEN VALLEY 2101 | UNK | 2021-09-07 12:53 | 9/6 to 9/12 | 2021-09-07 14:46 | HLT | 42114 | 596 | 29 | 19 | 8 | 0 | 0 | 113 | 70.6611
21-0114035 | LAKE | CLEAR LAKE 1101 | AN | 2021-09-07 08:18 | 9/6 to 9/12 | 2021-09-07 12:19 | HLT | 117367 | 487 | 28 | 20 | 8 | 0 | 0 | 241 | 241
21-0113986 | SAN LUIS OBISPO | ATASCADERO 1103 | UNK | 2021-09-07 06:21 | 9/6 to 9/12 | 2021-09-07 13:44 | HLT | 591287 | 1664 | 73 | 48 | 24 | 2 | 0 | 443 | 355.3407
21-0113973 | MARIN | WOODACRE 1101 | UNK | 2021-09-07 00:36 | 9/6 to 9/12 | 2021-09-07 08:23 | HLT | 200219 | 740 | 41 | 25 | 19 | 1 | 0 | 467 | 270.5662
21-0113972 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-09-07 00:34 | 9/6 to 9/12 | 2021-09-07 13:56 | HLT | 1441060 | 2993 | 227 | 173 | 45 | 4 | 0 | 580 | 481.4768
21-0113888 | SAN LUIS OBISPO | CAYUCOS 1102 | UNK | 2021-09-06 14:47 | 9/6 to 9/12 | 2021-09-07 12:22 | HLT | 76328 | 104 | 1 | 1 | 0 | 0 | 0 | 1295 | 733.9231
21-0113865 | CALAVERAS | SALT SPRINGS 2102 | UNK | 2021-09-06 12:10 | 9/6 to 9/12 | 2021-09-06 15:07 | HLT | 189213 | 1069 | 27 | 18 | 12 | 0 | 0 | 177 | 177
21-0113847 | TEHAMA | COTTONWOOD 1103 | UNK | 2021-09-06 09:33 | 9/6 to 9/12 | 2021-09-06 13:21 | HLT | 159828 | 701 | 63 | 43 | 18 | 0 | 0 | 228 | 228
21-0113833 | MADERA | OAKHURST 1101 | EF | 2021-09-06 08:45 | 9/6 to 9/12 | 2021-09-06 14:50 | HLT | 496882 | 2070 | 210 | 154 | 42 | 3 | 0 | 365 | 240.0396
21-0113831 | SANTA CLARA | LOS GATOS 1106 | AN | 2021-09-06 08:36 | 9/6 to 9/12 | 2021-09-06 22:43 | HLT | 868005 | 2231 | 154 | 107 | 57 | 8 | 0 | 847 | 389.0654
21-0113813 | EL DORADO | APPLE HILL 2102 | UNK | 2021-09-06 00:12 | 9/6 to 9/12 | 2021-09-06 11:05 | HLT | 2186872 | 2675 | 202 | 143 | 39 | 8 | 0 | 653 | 817.5222
21-0113791 | SANTA CLARA | MORGAN HILL 2105 | EF | 2021-09-05 17:59 | 8/30 to 9/5 | 2021-09-06 14:10 | HLT | 1172012 | 1099 | 64 | 50 | 17 | 3 | 0 | 1211 | 1066.4349
21-0113767 | HUMBOLDT | WILLOW CREEK 1103 | UNK | 2021-09-05 13:50 | 8/30 to 9/5 | 2021-09-05 16:17 | HLT | 24402 | 166 | 11 | 7 | 1 | 0 | 0 | 147 | 147
21-0113759 | CALAVERAS | SALT SPRINGS 2102 | UNK | 2021-09-05 12:25 | 8/30 to 9/5 | 2021-09-05 15:26 | HLT | 193489 | 1069 | 27 | 18 | 12 | 0 | 0 | 181 | 181
21-0113714 | EL DORADO | SHINGLE SPRINGS 2110 | UNK | 2021-09-05 00:07 | 8/30 to 9/5 | 2021-09-05 13:00 | HLT | 660328 | 1220 | 90 | 59 | 23 | 8 | 0 | 773 | 541.2525
21-0113701 | SAN MATEO | MENLO 1103 | UNK | 2021-09-04 20:17 | 8/30 to 9/5 | 2021-09-05 13:53 | HLT | 58080 | 55 | 3 | 1 | 2 | 0 | 0 | 1056 | 1056
21-0113699 | LAKE | MIDDLETOWN 1101 | VEG | 2021-09-04 19:44 | 8/30 to 9/5 | 2021-09-05 14:23 | HLT | 1621085 | 2083 | 94 | 63 | 39 | 7 | 0 | 1119 | 778.2453
21-0113688 | LAKE | KONOCTI 1102 | VEG | 2021-09-04 17:41 | 8/30 to 9/5 | 2021-09-05 17:05 | HLT | 760715 | 774 | 42 | 30 | 13 | 0 | 0 | 1404 | 982.8359
21-0113671 | CALAVERAS | FROGTOWN 1702 | UNK | 2021-09-04 15:13 | 8/30 to 9/5 | 2021-09-04 18:03 | HLT | 26690 | 157 | 4 | 3 | 3 | 0 | 0 | 170 | 170
21-0113630 | CALAVERAS | SALT SPRINGS 2102 | UNK | 2021-09-04 11:12 | 8/30 to 9/5 | 2021-09-04 15:05 | HLT | 249077 | 1069 | 27 | 18 | 12 | 0 | 0 | 233 | 233
21-0113618 | SAN LUIS OBISPO | ATASCADERO 1103 | UNK | 2021-09-04 09:32 | 8/30 to 9/5 | 2021-09-04 15:06 | HLT | 155060 | 607 | 39 | 25 | 19 | 2 | 0 | 334 | 255.453
21-0113604 | SANTA CRUZ | ROB ROY 2104 | AN | 2021-09-04 08:10 | 8/30 to 9/5 | 2021-09-04 15:13 | HLT | 947134 | 2392 | 154 | 128 | 34 | 6 | 0 | 423 | 395.959
21-0113526 | SANTA CRUZ | GREEN VALLEY 2101 | 3RD | 2021-09-03 16:22 | 8/30 to 9/5 | 2021-09-04 08:56 | HLT | 148826 | 307 | 16 | 13 | 10 | 5 | 0 | 994 | 484.7752
21-0113229 | MARIN | WOODACRE 1101 | UNK | 2021-09-03 09:57 | 8/30 to 9/5 | 2021-09-03 14:59 | HLT | 223480 | 740 | 41 | 25 | 19 | 1 | 0 | 302 | 302
21-0110830 | TRINITY | WILLOW CREEK 1103 | EF | 2021-09-02 23:00 | 8/30 to 9/5 | 2021-09-03 13:55 | HLT | [9 empty] | Outage data under further review
21-0112690 | YUBA | CHALLENGE 1102 | UNK | 2021-09-02 11:43 | 8/30 to 9/5 | 2021-09-02 15:13 | HLT | 42000 | 200 | 18 | 13 | 0 | 0 | 0 | 210 | 210
21-0112617 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-09-02 09:49 | 8/30 to 9/5 | 2021-09-02 13:42 | HLT | 81056 | 410 | 18 | 12 | 8 | 0 | 0 | 233 | 197.6976
21-0112566 | NAPA | PUEBLO 2103 | UNK | 2021-09-02 09:11 | 8/30 to 9/5 | 2021-09-02 11:33 | HLT | 133152 | 1482 | 92 | 66 | 16 | 1 | 0 | 142 | 89.8462
21-0112519 | MARIPOSA | BEAR VALLEY 2105 | UNK | 2021-09-02 07:54 | 8/30 to 9/5 | 2021-09-02 13:43 | HLT | 187304 | 686 | 52 | 41 | 11 | 9 | 0 | 349 | 273.0379
21-0112484 | TUOLUMNE | CURTIS 1703 | AN | 2021-09-02 07:06 | 8/30 to 9/5 | 2021-09-02 13:40 | HLT | 450860 | 1873 | 118 | 87 | 23 | 1 | 0 | 394 | 240.7154
21-0112483 | SHASTA | DESCHUTES 1104 | 3RD | 2021-09-02 07:04 | 8/30 to 9/5 | 2021-09-02 09:16 | HLT | 59928 | 454 | 32 | 17 | 4 | 0 | 0 | 132 | 132
21-0112461 | SANTA CLARA | HICKS 2101 | EF | 2021-09-02 05:48 | 8/30 to 9/5 | 2021-09-02 18:05 | HLT | 372072 | 1877 | 107 | 76 | 25 | 3 | 0 | 508 | 198.227
21-0112458 | CALAVERAS | FROGTOWN 1702 | EF | 2021-09-02 04:44 | 8/30 to 9/5 | 2021-09-02 20:17 | HLT | 217044 | 698 | 49 | 37 | 11 | 2 | 0 | 677 | 310.9513
21-0112453 | AMADOR | WEST POINT 1101 | UNK | 2021-09-02 02:53 | 8/30 to 9/5 | 2021-09-02 15:36 | HLT | 968015 | 1779 | 141 | 104 | 17 | 0 | 0 | 763 | 544.1343
21-0112374 | FRESNO | AUBERRY 1101 | UNK | 2021-09-01 16:45 | 8/30 to 9/5 | 2021-09-02 10:20 | HLT | 1074149 | 1374 | 121 | 81 | 17 | 4 | 0 | 1055 | 781.7678
21-0112367 | NEVADA | NARROWS 2102 | VEG | 2021-09-01 16:12 | 8/30 to 9/5 | 2021-09-02 14:34 | HLT | 671147 | 887 | 48 | 29 | 20 | 7 | 0 | 1342 | 756.6483
21-0112065 | EL DORADO | APPLE HILL 2102 | UNK | 2021-09-01 10:13 | 8/30 to 9/5 | 2021-09-01 12:53 | HLT | 42195 | 270 | 26 | 18 | 3 | 0 | 0 | 160 | 156.2778
21-0111953 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-09-01 07:31 | 8/30 to 9/5 | 2021-09-01 10:31 | HLT | 80037 | 737 | 24 | 19 | 15 | 2 | 0 | 180 | 108.5984
21-0111945 | SHASTA | GIRVAN 1101 | UNK | 2021-09-01 07:22 | 8/30 to 9/5 | 2021-09-01 14:15 | HLT | 328296 | 1176 | 86 | 56 | 30 | 6 | 0 | 412 | 279.1633
21-0111922 | SONOMA | GEYSERVILLE 1101 | UNK | 2021-09-01 06:32 | 8/30 to 9/5 | 2021-09-01 15:32 | HLT | 116239 | 439 | 10 | 7 | 4 | 0 | 0 | 540 | 264.7813
21-0111921 | SONOMA | GEYSERVILLE 1102 | UNK | 2021-09-01 06:22 | 8/30 to 9/5 | 2021-09-01 15:43 | HLT | 131016 | 380 | 4 | 2 | 15 | 1 | 0 | 561 | 344.7789
21-0111930 | SANTA CLARA | HICKS 2101 | AN | 2021-09-01 06:11 | 8/30 to 9/5 | 2021-09-01 09:50 | HLT | 338725 | 1877 | 107 | 76 | 25 | 3 | 0 | 219 | 180.4608
21-0111554 | BUTTE | ORO FINO 1102 | AN | 2021-08-31 10:07 | 8/30 to 9/5 | 2021-08-31 18:01 | HLT | 371820 | 1087 | 78 | 49 | 13 | 1 | 0 | 474 | 342.0607
21-0111364 | SANTA CLARA | HICKS 2101 | CI | 2021-08-31 04:16 | 8/30 to 9/5 | 2021-08-31 10:02 | HLT | 381367 | 3152 | 142 | 96 | 31 | 4 | 0 | 346 | 120.9921
21-0111378 | SANTA CLARA | HICKS 2101 | CI | 2021-08-31 00:24 | 8/30 to 9/5 | 2021-08-31 13:46 | HLT | 628763 | 3150 | 159 | 105 | 51 | 6 | 0 | 802 | 199.6073
21-0111369 | SANTA CRUZ | CAMP EVERS 2106 | UNK | 2021-08-30 23:44 | 8/30 to 9/5 | 2021-09-01 11:47 | HLT | 1782950 | 2854 | 223 | 176 | 44 | 8 | 0 | 1064 | 624.7197
21-0111340 | NAPA | SILVERADO 2102 | AN | 2021-08-30 19:06 | 8/30 to 9/5 | 2021-08-31 11:15 | HLT | 325988 | 337 | 3 | 3 | 5 | 0 | 0 | 969 | 967.3234
21-0111272 | FRESNO | TIVY VALLEY 1107 | UNK | 2021-08-30 16:20 | 8/30 to 9/5 | 2021-08-31 09:04 | HLT | 407926 | 833 | 62 | 44 | 13 | 0 | 0 | 1004 | 489.7071
21-0111081 | SAN LUIS OBISPO | TEMPLETON 2113 | CI | 2021-08-30 12:51 | 8/30 to 9/5 | 2021-08-30 18:30 | HLT | 76614 | 226 | 14 | 9 | 2 | 0 | 0 | 339 | 339
21-0110868 | SONOMA | GEYSERVILLE 1102 | UNK | 2021-08-30 07:44 | 8/30 to 9/5 | 2021-08-30 11:39 | HLT | 114931 | 568 | 14 | 6 | 13 | 2 | 0 | 235 | 202.3433
21-0110822 | SANTA CRUZ | GREEN VALLEY 2101 | AN | 2021-08-29 21:56 | 8/23 to 8/29 | 2021-08-30 10:57 | HLT | 647568 | 1013 | 85 | 69 | 9 | 1 | 0 | 781 | 639.2577
21-0110783 | MONTEREY | DEL MONTE 2104 | AN | 2021-08-29 12:52 | 8/23 to 8/29 | 2021-08-29 19:52 | HLT | 1026887 | 4405 | 180 | 130 | 147 | 4 | 1 | 420 | 233.1185
21-0110772 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-08-29 10:27 | 8/23 to 8/29 | 2021-08-29 16:59 | HLT | 61016 | 348 | 37 | 32 | 6 | 1 | 0 | 392 | 175.3333
21-0110751 | SANTA CLARA | MORGAN HILL 2105 | AN | 2021-08-29 07:54 | 8/23 to 8/29 | 2021-08-29 13:43 | HLT | 187216 | 1099 | 64 | 50 | 17 | 3 | 0 | 349 | 170.3512
21-0110738 | CALAVERAS | WEST POINT 1102 | EF | 2021-08-29 03:09 | 8/23 to 8/29 | 2021-08-29 14:32 | HLT | 1329167 | 1965 | 131 | 93 | 27 | 0 | 0 | 683 | 676.4209
21-0110728 | SHASTA | JESSUP 1102 | UNK | 2021-08-29 00:03 | 8/23 to 8/29 | 2021-08-29 11:47 | HLT | 816367 | 1408 | 139 | 107 | 10 | 2 | 0 | 703 | 579.8061
21-0110730 | MADERA | OAKHURST 1101 | UNK | 2021-08-28 23:46 | 8/23 to 8/29 | 2021-08-29 11:09 | HLT | 1371290 | 2064 | 210 | 154 | 39 | 2 | 0 | 683 | 664.3847
21-0110716 | SANTA CLARA | LOS GATOS 1106 | VEG | 2021-08-28 22:02 | 8/23 to 8/29 | 2021-08-30 01:47 | HLT | 2416191 | 2229 | 154 | 107 | 57 | 8 | 0 | 1665 | 1083.9798
21-0110667 | SANTA CLARA | SARATOGA 1107 | VEG | 2021-08-28 18:52 | 8/23 to 8/29 | 2021-08-30 00:09 | HLT | 57930 | 166 | 6 | 2 | 2 | 2 | 0 | 1757 | 348.9759
21-0110642 | ALAMEDA | CASTRO VALLEY 1108 | UNK | 2021-08-28 16:19 | 8/23 to 8/29 | 2021-08-28 18:56 | HLT | 161897 | 1088 | 64 | 50 | 11 | 0 | 0 | 157 | 148.8024
21-0110588 | PLUMAS | GANSNER 1101 | UNK | 2021-08-28 12:01 | 8/23 to 8/29 | 2021-08-28 19:51 | HLT | 911600 | 2703 | 135 | 93 | 70 | 31 | 1 | 470 | 337.2549
21-0110578 | SAN BENITO | HOLLISTER 2105 | VEG | 2021-08-28 11:43 | 8/23 to 8/29 | 2021-08-28 23:19 | HLT | 32237 | 127 | 2 | 2 | 2 | 2 | 0 | 696 | 253.8346
21-0110564 | SANTA CRUZ | BIG BASIN 1102 | UNK | 2021-08-28 10:09 | 8/23 to 8/29 | 2021-08-28 17:13 | HLT | 292572 | 823 | 47 | 32 | 14 | 1 | 0 | 424 | 355.4945
21-0110542 | SAN MATEO | WOODSIDE 1104 | AN | 2021-08-28 09:37 | 8/23 to 8/29 | 2021-08-28 21:17 | HLT | 90110 | 414 | 14 | 8 | 14 | 1 | 0 | 700 | 217.657
21-0110525 | AMADOR | WEST POINT 1101 | UNK | 2021-08-28 08:03 | 8/23 to 8/29 | 2021-08-28 21:05 | HLT | 674671 | 1779 | 141 | 104 | 17 | 0 | 0 | 782 | 379.2417
21-0110517 | FRESNO | AUBERRY 1101 | UNK | 2021-08-28 07:38 | 8/23 to 8/29 | 2021-08-28 14:40 | HLT | 544094 | 1369 | 121 | 81 | 17 | 4 | 0 | 422 | 397.439
21-0110520 | FRESNO | DUNLAP 1102 | VEG | 2021-08-28 07:36 | 8/23 to 8/29 | 2021-08-28 16:28 | HLT | 109978 | 308 | 6 | 4 | 7 | 0 | 0 | 532 | 357.0714
21-0110507 | FRESNO | DUNLAP 1103 | UNK | 2021-08-28 07:06 | 8/23 to 8/29 | 2021-08-28 10:54 | HLT | 120300 | 556 | 42 | 26 | 5 | 3 | 0 | 228 | 216.3669
21-0110494 | SONOMA | GEYSERVILLE 1101 | 3RD | 2021-08-27 23:47 | 8/23 to 8/29 | 2021-08-28 09:13 | HLT | 118860 | 210 | 4 | 2 | 3 | 0 | 0 | 566 | 566
21-0110478 | SANTA CLARA | SARATOGA 1107 | CI | 2021-08-27 22:22 | 8/23 to 8/29 | 2021-08-28 00:08 | HLT | 24698 | 233 | 10 | 6 | 4 | 0 | 0 | 106 | 106
21-0110380 | SAN MATEO | HALF MOON BAY 1103 | EF | 2021-08-27 16:07 | 8/23 to 8/29 | 2021-08-28 14:59 | HLT | 2913913 | 2983 | 89 | 69 | 64 | 12 | 0 | 1372 | 976.8398
21-0110047 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-08-27 08:45 | 8/23 to 8/29 | 2021-08-27 12:16 | HLT | 153420 | 1240 | 54 | 36 | 15 | 5 | 0 | 211 | 123.7258
21-0110043 | FRESNO | DUNLAP 1103 | UNK | 2021-08-27 08:28 | 8/23 to 8/29 | 2021-08-27 12:19 | HLT | 122738 | 556 | 42 | 26 | 5 | 3 | 0 | 231 | 220.7518
21-0109982 | PLACER | WEIMAR 1101 | AN | 2021-08-27 07:33 | 8/23 to 8/29 | 2021-08-27 14:55 | HLT | 154700 | 350 | 19 | 14 | 1 | 0 | 0 | 442 | 442
21-0109962 | EL DORADO | PLACERVILLE 2106 | EF | 2021-08-27 06:43 | 8/23 to 8/29 | 2021-08-27 19:04 | HLT | 1757499 | 3005 | 231 | 171 | 67 | 16 | 0 | 741 | 584.8582
21-0109953 | SAN BENITO | SAN JUSTO 1101 | UNK | 2021-08-27 06:19 | 8/23 to 8/29 | 2021-08-27 08:46 | HLT | 24402 | 166 | 9 | 8 | 3 | 0 | 0 | 147 | 147
21-0109937 | MONTEREY | LOS OSITOS 2103 | 3RD | 2021-08-27 00:15 | 8/23 to 8/29 | 2021-08-27 10:23 | HLT | 211005 | 841 | 13 | 9 | 13 | 2 | 0 | 608 | 250.8977
21-0109911 | NAPA | SILVERADO 2104 | UNK | 2021-08-26 20:14 | 8/23 to 8/29 | 2021-08-27 14:08 | HLT | 2238136 | 2359 | 106 | 66 | 60 | 9 | 19 | 1074 | 948.7647
21-0109690 | BUTTE | ORO FINO 1102 | VEG | 2021-08-26 12:08 | 8/23 to 8/29 | 2021-08-27 10:17 | HLT | 424243 | 1087 | 78 | 49 | 13 | 1 | 0 | 777 | 390.2879
21-0109498 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-08-26 07:33 | 8/23 to 8/29 | 2021-08-26 16:09 | HLT | 1211979 | 3188 | 246 | 168 | 48 | 0 | 0 | 516 | 380.1691
21-0109462 | YUBA | BANGOR 1101 | UNK | 2021-08-26 06:14 | 8/23 to 8/29 | 2021-08-26 08:42 | HLT | 4588 | 31 | 1 | 1 | 0 | 0 | 0 | 148 | 148
21-0109454 | TUOLUMNE | CURTIS 1705 | UNK | 2021-08-26 05:56 | 8/23 to 8/29 | 2021-08-26 07:52 | HLT | 58232 | 502 | 54 | 43 | 4 | 0 | 0 | 116 | 116
21-0109408 | SAN LUIS OBISPO | ATASCADERO 1103 | UNK | 2021-08-25 19:17 | 8/23 to 8/29 | 2021-08-26 10:49 | HLT | 397296 | 603 | 39 | 25 | 19 | 2 | 0 | 932 | 658.8657
21-0109181 | SHASTA | JESSUP 1102 | UNK | 2021-08-25 11:44 | 8/23 to 8/29 | 2021-08-25 16:11 | HLT | 104931 | 393 | 46 | 36 | 1 | 0 | 0 | 267 | 267
21-0108925 | SANTA CRUZ | ROB ROY 2104 | VEG | 2021-08-25 03:07 | 8/23 to 8/29 | 2021-08-25 09:21 | HLT | 169422 | 453 | 26 | 25 | 10 | 0 | 0 | 374 | 374
21-0108844 | PLUMAS | GANSNER 1101 | UNK | 2021-08-24 17:24 | 8/23 to 8/29 | 2021-08-25 04:47 | HLT | 518037 | 2703 | 135 | 93 | 70 | 31 | 1 | 683 | 191.6526
21-0108577 | BUTTE | BANGOR 1101 | UNK | 2021-08-24 08:36 | 8/23 to 8/29 | 2021-08-24 12:42 | HLT | 104550 | 425 | 39 | 25 | 2 | 0 | 0 | 246 | 246
21-0108496 | NEVADA | BRUNSWICK 1103 | AN | 2021-08-24 07:51 | 8/23 to 8/29 | 2021-08-24 11:07 | HLT | 195524 | 1074 | 55 | 32 | 9 | 1 | 0 | 196 | 182.0521
21-0108429 | PLUMAS | GANSNER 1101 | UNK | 2021-08-23 21:02 | 8/23 to 8/29 | 2021-08-24 02:00 | HLT | 613886 | 2409 | 120 | 85 | 52 | 21 | 0 | 298 | 254.8302
21-0108411 | BUTTE | BANGOR 1101 | UNK | 2021-08-23 19:09 | 8/23 to 8/29 | 2021-08-23 21:37 | HLT | 373358 | 448 | 48 | 32 | 2 | 0 | 0 | 148 | 833.3884
21-0108416 | YUBA | BANGOR 1101 | UNK | 2021-08-23 19:08 | 8/23 to 8/29 | 2021-08-24 11:42 | HLT | 1136987 | 1217 | 111 | 82 | 9 | 4 | 0 | 994 | 934.2539
21-0108402 | SANTA CLARA | LOS GATOS 1106 | EF | 2021-08-23 18:02 | 8/23 to 8/29 | 2021-08-24 21:24 | HLT | 1694625 | 2229 | 154 | 107 | 57 | 8 | 0 | 1642 | 760.2624
21-0108234 | BUTTE | KANAKA 1101 | UNK | 2021-08-23 13:00 | 8/23 to 8/29 | 2021-08-23 17:28 | HLT | 92618 | 379 | 29 | 21 | 12 | 0 | 0 | 268 | 244.3747
21-0108226 | NAPA | SILVERADO 2102 | VEG | 2021-08-23 12:38 | 8/23 to 8/29 | 2021-08-23 17:43 | HLT | 94701 | 333 | 3 | 3 | 5 | 0 | 0 | 305 | 284.3874
21-0108180 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-08-23 11:14 | 8/23 to 8/29 | 2021-08-23 12:37 | HLT | 70316 | 1240 | 54 | 36 | 15 | 5 | 0 | 83 | 56.7065
21-0108169 | SONOMA | MOLINO 1102 | CI | 2021-08-23 10:46 | 8/23 to 8/29 | 2021-08-23 18:50 | HLT | 599194 | 2084 | 116 | 77 | 26 | 1 | 0 | 484 | 287.5211
21-0108050 | NEVADA | BRUNSWICK 1103 | VEG | 2021-08-23 07:01 | 8/23 to 8/29 | 2021-08-23 11:50 | HLT | 310386 | 1074 | 55 | 32 | 9 | 1 | 0 | 289 | 289
21-0108040 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-08-23 05:21 | 8/23 to 8/29 | 2021-08-23 15:04 | HLT | 1431616 | 2903 | 225 | 156 | 45 | 0 | 0 | 583 | 493.1505
21-0107983 | LAKE | KONOCTI 1102 | UNK | 2021-08-22 16:12 | 8/16 to 8/22 | 2021-08-22 18:12 | HLT | 13920 | 116 | 11 | 10 | 1 | 0 | 0 | 120 | 120
21-0107901 | ALAMEDA | SUNOL 1101 | 3RD | 2021-08-22 08:08 | 8/16 to 8/22 | 2021-08-22 14:39 | HLT | 3712 | 10 | 0 | 0 | 6 | 0 | 0 | 385 | 371.2
21-0107878 | AMADOR | OLETA 1102 | EF | 2021-08-22 07:34 | 8/16 to 8/22 | 2021-08-22 14:00 | HLT | 99202 | 257 | 9 | 7 | 4 | 0 | 0 | 386 | 386
21-0107877 | TUOLUMNE | PEORIA 1701 | UNK | 2021-08-22 07:10 | 8/16 to 8/22 | 2021-08-22 09:45 | HLT | 29915 | 193 | 8 | 7 | 7 | 2 | 0 | 155 | 155
21-0107817 | SAN LUIS OBISPO | TEMPLETON 2110 | AN | 2021-08-21 17:43 | 8/16 to 8/22 | 2021-08-22 14:20 | HLT | 1043056 | 1003 | 35 | 23 | 13 | 0 | 0 | 1237 | 1039.9362
21-0107799 | MADERA | COARSEGOLD 2104 | EF | 2021-08-21 13:58 | 8/16 to 8/22 | 2021-08-22 07:00 | HLT | 1557508 | 4367 | 467 | 331 | 84 | 9 | 0 | 1022 | 356.654
21-0107761 | SONOMA | GEYSERVILLE 1101 | EF | 2021-08-21 11:46 | 8/16 to 8/22 | 2021-08-21 18:48 | HLT | 27353 | 149 | 11 | 8 | 8 | 0 | 0 | 422 | 183.5772
21-0107711 | EL DORADO | SHINGLE SPRINGS 2110 | UNK | 2021-08-21 09:32 | 8/16 to 8/22 | 2021-08-21 14:47 | HLT | 227550 | 718 | 57 | 39 | 5 | 0 | 0 | 315 | 316.922
21-0107665 | SIERRA | ALLEGHANY 1101 | UNK | 2021-08-21 07:58 | 8/16 to 8/22 | 2021-08-21 16:14 | HLT | 220216 | 604 | 18 | 17 | 9 | 0 | 0 | 496 | 364.596
21-0107652 | EL DORADO | APPLE HILL 2102 | UNK | 2021-08-21 07:10 | 8/16 to 8/22 | 2021-08-22 13:02 | HLT | 2011481 | 2356 | 179 | 129 | 36 | 8 | 0 | 1792 | 853.7695
21-0107647 | YOLO | PUTAH CREEK 1102 | UNK | 2021-08-21 06:20 | 8/16 to 8/22 | 2021-08-21 12:19 | HLT | 99932 | 277 | 8 | 5 | 5 | 0 | 0 | 359 | 360.7653
21-0107642 | MADERA | COARSEGOLD 2104 | UNK | 2021-08-21 03:35 | 8/16 to 8/22 | 2021-08-21 12:13 | HLT | 1155354 | 2605 | 287 | 193 | 59 | 8 | 0 | 518 | 443.514
21-0107594 | TEHAMA | VOLTA 1101 | UNK | 2021-08-20 17:31 | 8/16 to 8/22 | 2021-08-21 11:21 | HLT | 153746 | 242 | 16 | 13 | 7 | 3 | 0 | 1070 | 635.314
21-0107555 | SOLANO | VACAVILLE 1108 | 3RD | 2021-08-20 16:08 | 8/16 to 8/22 | 2021-08-20 19:44 | HLT | 90524 | 420 | 20 | 14 | 14 | 1 | 0 | 216 | 215.5333
21-0107529 | HUMBOLDT | HOOPA 1101 | VEG | 2021-08-20 15:36 | 8/16 to 8/22 | 2021-08-21 17:03 | HLT | 1016853 | 668 | 17 | 15 | 24 | 5 | 0 | 1527 | 1522.235
21-0107210 | TUOLUMNE | MIWUK 1702 | EF | 2021-08-20 08:26 | 8/16 to 8/22 | 2021-08-20 11:06 | HLT | 69280 | 433 | 39 | 30 | 2 | 1 | 0 | 160 | 160
21-0107105 | SANTA CRUZ | GREEN VALLEY 2101 | UNK | 2021-08-20 05:46 | 8/16 to 8/22 | 2021-08-20 13:25 | HLT | 126234 | 307 | 16 | 13 | 10 | 5 | 0 | 459 | 411.1857
21-0107098 | SANTA CRUZ | ROB ROY 2104 | VEG | 2021-08-20 01:18 | 8/16 to 8/22 | 2021-08-20 15:58 | HLT | 1362901 | 2392 | 154 | 128 | 34 | 6 | 0 | 880 | 569.7747
21-0107090 | CALAVERAS | FROGTOWN 1702 | EF | 2021-08-19 22:44 | 8/16 to 8/22 | 2021-08-20 14:31 | HLT | 792968 | 928 | 38 | 24 | 40 | 2 | 0 | 947 | 854.4914
21-0107063 | PLACER | FORESTHILL 1101 | CI | 2021-08-19 17:57 | 8/16 to 8/22 | 2021-08-20 10:42 | HLT | 729688 | 2263 | 203 | 138 | 38 | 6 | 0 | 1005 | 322.4428
21-0106965 | SONOMA | CALISTOGA 1101 | UNK | 2021-08-19 14:36 | 8/16 to 8/22 | 2021-08-19 18:50 | HLT | 5442 | 26 | 0 | 0 | 0 | 0 | 0 | 254 | 209.3077
21-0106937 | YUBA | CHALLENGE 1101 | UNK | 2021-08-19 14:10 | 8/16 to 8/22 | 2021-08-19 17:41 | HLT | 75601 | 454 | 25 | 15 | 7 | 0 | 0 | 211 | 166.522
21-0106396 | SANTA BARBARA | SISQUOC 1102 | EF | 2021-08-18 13:34 | 8/16 to 8/22 | 2021-08-19 15:14 | HLT | 344942 | 346 | 6 | 4 | 6 | 0 | 0 | 1540 | 996.9422
21-0106331 | PLUMAS | HAMILTON BRANCH 1101 | UNK | 2021-08-18 11:50 | 8/16 to 8/22 | 2021-08-18 14:36 | HLT | 482535 | 3096 | 102 | 72 | 38 | 0 | 0 | 166 | 155.8576
21-0106293 | SAN LUIS OBISPO | TEMPLETON 2113 | EF | 2021-08-18 11:24 | 8/16 to 8/22 | 2021-08-18 20:08 | HLT | 1322873 | 3115 | 161 | 113 | 50 | 2 | 1 | 524 | 424.6783
21-0106212 | HUMBOLDT | WILLOW CREEK 1103 | EF | 2021-08-18 09:44 | 8/16 to 8/22 | 2021-08-19 14:12 | HLT | 963151 | 1244 | 75 | 56 | 13 | 3 | 0 | 1708 | 774.2371
21-0106180 | MARIPOSA | MARIPOSA 2101 | UNK | 2021-08-18 09:01 | 8/16 to 8/22 | 2021-08-18 13:21 | HLT | 164487 | 664 | 51 | 38 | 16 | 0 | 0 | 260 | 247.7214
21-0106088 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-08-18 06:20 | 8/16 to 8/22 | 2021-08-19 10:51 | HLT | 127437 | 147 | 4 | 4 | 2 | 0 | 0 | 1711 | 866.9184
21-0106079 | CALAVERAS | WEST POINT 1102 | VEG | 2021-08-18 03:51 | 8/16 to 8/22 | 2021-08-18 15:59 | HLT | 1264384 | 1965 | 131 | 93 | 27 | 0 | 0 | 728 | 643.4524
21-0106027 | NAPA | SILVERADO 2104 | CI | 2021-08-17 18:57 | 8/16 to 8/22 | 2021-08-18 10:17 | HLT | 454560 | 455 | 13 | 9 | 15 | 1 | 15 | 920 | 999.033
21-0106011 | EL DORADO | APPLE HILL 2102 | ENV | 2021-08-17 18:13 | 8/16 to 8/22 | 2021-08-29 14:48 | HLT | 12470 | 1722 | 112 | 69 | 19 | 0 | 0 | 17075 | 7.2416
21-0105921 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-08-17 15:50 | 8/16 to 8/22 | 2021-08-18 11:30 | HLT | 1272189 | 1115 | 91 | 70 | 22 | 0 | 0 | 1180 | 1140.9767
21-0105911 | SANTA CRUZ | PAUL SWEET 2106 | UNK | 2021-08-17 15:46 | 8/16 to 8/22 | 2021-08-17 20:35 | HLT | 66030 | 347 | 38 | 34 | 5 | 1 | 0 | 289 | 190.2882
21-0105629 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-08-17 11:10 | 8/16 to 8/22 | 2021-08-17 20:36 | HLT | 1377187 | 3004 | 231 | 171 | 70 | 16 | 0 | 566 | 458.4511
21-0105457 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-08-17 06:48 | 8/16 to 8/22 | 2021-08-17 13:03 | HLT | 464662 | 1994 | 151 | 94 | 26 | 4 | 1 | 375 | 233.0301
21-0105455 | TUOLUMNE | CURTIS 1704 | EF | 2021-08-17 06:39 | 8/16 to 8/22 | 2021-08-17 15:49 | HLT | 414625 | 1556 | 168 | 122 | 16 | 0 | 0 | 550 | 266.4685
21-0105453 | TUOLUMNE | PEORIA 1701 | UNK | 2021-08-17 06:38 | 8/16 to 8/22 | 2021-08-17 15:14 | HLT | 772410 | 1686 | 91 | 69 | 22 | 1 | 0 | 516 | 458.1317
21-0105423 | PLACER | FORESTHILL 1101 | EF | 2021-08-17 00:19 | 8/16 to 8/22 | 2021-08-17 13:34 | HLT | 1153902 | 1655 | 159 | 106 | 20 | 2 | 0 | 795 | 697.2218
21-0105289 | NAPA | SILVERADO 2104 | UNK | 2021-08-16 16:03 | 8/16 to 8/22 | 2021-08-16 19:16 | HLT | 100167 | 519 | 32 | 22 | 15 | 1 | 3 | 193 | 193
21-0105271 | ALAMEDA | CASTRO VALLEY 1108 | 3RD | 2021-08-16 15:34 | 8/16 to 8/22 | 2021-08-16 18:23 | HLT | 176456 | 1088 | 64 | 50 | 11 | 0 | 0 | 169 | 162.1838
21-0105053 | MADERA | COARSEGOLD 2104 | UNK | 2021-08-16 11:43 | 8/16 to 8/22 | 2021-08-16 18:32 | HLT | 815454 | 2598 | 285 | 192 | 59 | 8 | 0 | 409 | 313.8776
21-0104886 | SANTA BARBARA | SISQUOC 1102 | UNK | 2021-08-16 08:21 | 8/16 to 8/22 | 2021-08-16 13:01 | HLT | 19600 | 70 | 5 | 2 | 1 | 0 | 0 | 280 | 280
21-0104880 | PLACER | SHADY GLEN 1101 | AN | 2021-08-16 08:12 | 8/16 to 8/22 | 2021-08-16 12:29 | HLT | 253402 | 986 | 63 | 41 | 13 | 1 | 0 | 257 | 257
21-0104798 | SANTA CLARA | LOS GATOS 1106 | VEG | 2021-08-15 18:01 | 8/9 to 8/15 | 2021-08-17 10:56 | HLT | 1633668 | 2224 | 154 | 107 | 55 | 8 | 0 | 2455 | 734.5629
21-0104753 | SHASTA | STILLWATER 1102 | UNK | 2021-08-15 09:34 | 8/9 to 8/15 | 2021-08-15 14:52 | HLT | 290070 | 755 | 67 | 47 | 13 | 0 | 0 | 318 | 384.1987
21-0104752 | MARIN | SAN RAFAEL 1108 | VEG | 2021-08-15 09:18 | 8/9 to 8/15 | 2021-08-15 21:13 | HLT | 1148978 | 3095 | 94 | 52 | 25 | 1 | 0 | 715 | 371.2368
21-0104742 | CALAVERAS | FROGTOWN 1702 | EF | 2021-08-15 07:27 | 8/9 to 8/15 | 2021-08-16 03:36 | HLT | 176872 | 698 | 49 | 37 | 11 | 2 | 0 | 1209 | 253.3983
21-0104738 | MONTEREY | DEL MONTE 2104 | UNK | 2021-08-15 06:17 | 8/9 to 8/15 | 2021-08-16 17:16 | HLT | 3941945 | 5706 | 160 | 98 | 19 | 3 | 0 | 1150 | 690.8421
21-0104721 | CONTRA COSTA | EL CERRITO G 1105 | EF | 2021-08-14 22:09 | 8/9 to 8/15 | 2021-08-16 12:52 | HLT | 213653 | 713 | 32 | 22 | 14 | 2 | 0 | 2323 | 299.6536
21-0104679 | NAPA | PUEBLO 2103 | EF | 2021-08-14 18:08 | 8/9 to 8/15 | 2021-08-15 11:50 | HLT | 335592 | 316 | 6 | 4 | 3 | 2 | 0 | 1062 | 1062
21-0104548 | SANTA CRUZ | GREEN VALLEY 2101 | UNK | 2021-08-14 09:11 | 8/9 to 8/15 | 2021-08-14 17:35 | HLT | 107077 | 307 | 16 | 13 | 10 | 5 | 0 | 504 | 348.785
21-0104530 | TUOLUMNE | CURTIS 1705 | AN | 2021-08-14 08:16 | 8/9 to 8/15 | 2021-08-14 11:36 | HLT | 111443 | 682 | 66 | 40 | 7 | 5 | 0 | 200 | 163.4062
21-0104502 | MONTEREY | HATTON 1101 | UNK | 2021-08-14 07:21 | 8/9 to 8/15 | 2021-08-14 09:55 | HLT | 325482 | 3027 | 78 | 51 | 81 | 8 | 0 | 154 | 107.5263
21-0104487 | SANTA CLARA | HICKS 2101 | EF | 2021-08-14 04:59 | 8/9 to 8/15 | 2021-08-14 19:11 | HLT | 453384 | 3150 | 159 | 105 | 51 | 6 | 0 | 581 | 143.9314
21-0104485 | SANTA CRUZ | ROB ROY 2104 | VEG | 2021-08-14 04:13 | 8/9 to 8/15 | 2021-08-14 09:10 | HLT | 136323 | 459 | 26 | 25 | 10 | 0 | 0 | 297 | 297
21-0104483 | SONOMA | MONTE RIO 1111 | VEG | 2021-08-14 01:56 | 8/9 to 8/15 | 2021-08-14 13:31 | HLT | 436815 | 1259 | 68 | 40 | 29 | 3 | 0 | 695 | 346.9539
21-0104481 | SAN MATEO | WOODSIDE 1104 | AN | 2021-08-14 00:27 | 8/9 to 8/15 | 2021-08-14 11:00 | HLT | 1250291 | 1981 | 81 | 56 | 34 | 7 | 0 | 633 | 631.1413
21-0104393 | SONOMA | MOLINO 1102 | VEG | 2021-08-13 17:40 | 8/9 to 8/15 | 2021-08-14 16:11 | HLT | 1784761 | 2093 | 116 | 77 | 26 | 1 | 0 | 1351 | 852.7286
21-0104046 | EL DORADO | PLACERVILLE 2106 | VEG | 2021-08-13 09:06 | 8/9 to 8/15 | 2021-08-13 13:12 | HLT | 59778 | 243 | 7 | 5 | 3 | 0 | 0 | 246 | 246
21-0103836 |  | LOW GAP 1101 | UNK | 2021-08-12 15:53 | 8/9 to 8/15 | 2021-08-12 20:45 | HLT | 213580 | 733 | 27 | 19 | 12 | 3 | 0 | 292 | 291.3779
21-0103608 | YOLO | PUTAH CREEK 1102 | UNK | 2021-08-12 11:35 | 8/9 to 8/15 | 2021-08-12 15:43 | HLT | 16391 | 93 | 5 | 3 | 0 | 0 | 0 | 248 | 176.2473
21-0103505 | SANTA CLARA | LOS GATOS 1106 | VEG | 2021-08-12 09:24 | 8/9 to 8/15 | 2021-08-13 02:30 | HLT | 800032 | 2224 | 154 | 107 | 55 | 8 | 0 | 1026 | 359.7266
21-0103407 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-08-12 06:25 | 8/9 to 8/15 | 2021-08-12 14:38 | HLT | 326640 | 1115 | 91 | 70 | 22 | 0 | 0 | 493 | 292.9507
21-0103396 | EL DORADO | SHINGLE SPRINGS 2110 | VEG | 2021-08-12 05:20 | 8/9 to 8/15 | 2021-08-12 12:36 | HLT | 319580 | 1004 | 78 | 50 | 15 | 7 | 0 | 436 | 318.3068
21-0103395 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-08-12 04:50 | 8/9 to 8/15 | 2021-08-12 18:34 | HLT | 1970273 | 2997 | 231 | 171 | 67 | 16 | 0 | 824 | 657.4151
21-0103394 | TUOLUMNE | CURTIS 1703 | VEG | 2021-08-12 03:06 | 8/9 to 8/15 | 2021-08-12 06:42 | HLT | 742288 | 3861 | 276 | 208 | 54 | 6 | 0 | 216 | 192.2528
21-0103374 | KERN | TEJON 1102 | CI | 2021-08-11 22:25 | 8/9 to 8/15 | 2021-08-12 09:57 | HLT | 246845 | 499 | 24 | 19 | 27 | 3 | 0 | 692 | 494.6794
21-0103298 | FRESNO | DUNLAP 1103 | VEG | 2021-08-11 16:45 | 8/9 to 8/15 | 2021-08-12 10:40 | HLT | 466769 | 556 | 42 | 26 | 5 | 3 | 0 | 1075 | 839.5126
21-0103224 | HUMBOLDT | WILLOW CREEK 1103 | 3RD | 2021-08-11 15:07 | 8/9 to 8/15 | 2021-08-12 13:19 | HLT | 774823 | 1157 | 75 | 56 | 13 | 3 | 0 | 1332 | 669.6828
21-0103124 | LAKE | KONOCTI 1102 | UNK | 2021-08-11 12:54 | 8/9 to 8/15 | 2021-08-11 18:35 | HLT | 278957 | 826 | 48 | 34 | 24 | 0 | 0 | 341 | 337.7203
21-0102882 | SAN MATEO | WOODSIDE 1101 | AN | 2021-08-11 08:11 | 8/9 to 8/15 | 2021-08-11 17:06 | HLT | 320019 | 869 | 33 | 16 | 37 | 17 | 0 | 535 | 368.2612
21-0102881 | MARIN | SAN RAFAEL 1108 | UNK | 2021-08-11 08:07 | 8/9 to 8/15 | 2021-08-11 12:43 | HLT | 328140 | 1196 | 28 | 16 | 45 | 25 | 0 | 276 | 274.3645
21-0102778 | SANTA CRUZ | CAMP EVERS 2105 | 3RD | 2021-08-10 20:56 | 8/9 to 8/15 | 2021-08-11 15:18 | HLT | 961207 | 1013 | 85 | 64 | 21 | 0 | 0 | 1102 | 948.8717
21-0102562 | BUTTE | BANGOR 1101 | AN | 2021-08-10 13:39 | 8/9 to 8/15 | 2021-08-10 20:33 | HLT | 504023 | 1648 | 153 | 110 | 11 | 4 | 0 | 414 | 305.8392
21-0102392 | MARIPOSA | MARIPOSA 2102 | UNK | 2021-08-10 09:51 | 8/9 to 8/15 | 2021-08-10 14:11 | HLT | 110500 | 425 | 46 | 32 | 4 | 0 | 0 | 260 | 260
21-0102306 | SANTA CRUZ | ROB ROY 2104 | VEG | 2021-08-10 07:53 | 8/9 to 8/15 | 2021-08-10 20:46 | HLT | 828504 | 2392 | 154 | 128 | 34 | 6 | 0 | 773 | 346.3645
21-0102211 | MARIN | SAN RAFAEL 1108 | VEG | 2021-08-09 21:27 | 8/9 to 8/15 | 2021-08-10 07:14 | HLT | 452577 | 771 | 26 | 12 | 6 | 3 | 0 | 587 | 587
21-0102193 | LAKE | KONOCTI 1108 | AN | 2021-08-09 19:24 | 8/9 to 8/15 | 2021-08-09 21:51 | HLT | 65562 | 446 | 33 | 24 | 7 | 0 | 0 | 147 | 147
21-0102049 | NAPA | PUEBLO 1105 | EF | 2021-08-09 14:04 | 8/9 to 8/15 | 2021-08-10 09:13 | HLT | 108855 | 242 | 5 | 4 | 1 | 0 | 0 | 1149 | 449.814
21-0101227 | MADERA | COARSEGOLD 2104 | UNK | 2021-08-09 11:01 | 8/9 to 8/15 | 2021-08-09 17:28 | HLT | 395847 | 1131 | 120 | 73 | 20 | 6 | 0 | 387 | 349.9973
21-0100306 | MADERA | COARSEGOLD 2104 | EF | 2021-08-09 10:57 | 8/9 to 8/15 | 2021-08-09 17:15 | HLT | 554904 | 1468 | 166 | 119 | 39 | 2 | 0 | 378 | 378
21-0101925 | SHASTA | GIRVAN 1101 | UNK | 2021-08-09 10:40 | 8/9 to 8/15 | 2021-08-09 15:06 | HLT | 40964 | 154 | 6 | 5 | 5 | 0 | 0 | 266 | 266
21-0101902 | NEVADA | NARROWS 2102 | UNK | 2021-08-09 10:29 | 8/9 to 8/15 | 2021-08-09 17:12 | HLT | 653164 | 1786 | 124 | 77 | 33 | 7 | 0 | 403 | 365.7133
21-0101786 | MADERA | COARSEGOLD 2102 | 3RD | 2021-08-09 07:40 | 8/9 to 8/15 | 2021-08-09 16:45 | HLT | 500214 | 1274 | 100 | 77 | 30 | 0 | 0 | 545 | 392.6327
21-0101777 | EL DORADO | APPLE HILL 2102 | UNK | 2021-08-09 06:22 | 8/9 to 8/15 | 2021-08-09 11:55 | HLT | 341402 | 1224 | 98 | 74 | 17 | 3 | 0 | 333 | 278.9232
21-0101776 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-08-09 06:13 | 8/9 to 8/15 | 2021-08-09 16:46 | HLT | 1555612 | 3003 | 231 | 171 | 70 | 16 | 0 | 633 | 518.0193
21-0101657 | CALAVERAS | STANISLAUS 1702 | EF | 2021-08-08 08:07 | 8/2 to 8/8 | 2021-08-08 15:10 | HLT | 939739 | 2458 | 88 | 66 | 28 | 3 | 2 | 423 | 382.3186
21-0101651 | TUOLUMNE | PEORIA 1701 | AN | 2021-08-08 07:08 | 8/2 to 8/8 | 2021-08-08 09:58 | HLT | 325040 | 1912 | 99 | 76 | 30 | 3 | 0 | 170 | 170
21-0101639 | SANTA CLARA | LLAGAS 2101 | EF | 2021-08-08 04:50 | 8/2 to 8/8 | 2021-08-09 11:48 | HLT | 526196 | 1002 | 49 | 33 | 16 | 2 | 0 | 1858 | 525.1457
21-0101636 | YUBA | BANGOR 1101 | UNK | 2021-08-08 03:37 | 8/2 to 8/8 | 2021-08-09 09:33 | HLT | 1544167 | 1672 | 159 | 114 | 11 | 4 | 0 | 1794 | 923.5449
21-0101600 | SAN MATEO | HALF MOON BAY 1101 | AN | 2021-08-07 20:11 | 8/2 to 8/8 | 2021-08-08 15:44 | HLT | 316714 | 306 | 9 | 5 | 23 | 0 | 0 | 1173 | 1035.0131
21-0101575 | NAPA | SILVERADO 2104 | VEG | 2021-08-07 16:42 | 8/2 to 8/8 | 2021-08-08 12:39 | HLT | 2527680 | 2212 | 98 | 60 | 59 | 9 | 19 | 1197 | 1142.7125
21-0101566 | MARIPOSA | MARIPOSA 2102 | 3RD | 2021-08-07 16:19 | 8/2 to 8/8 | 2021-08-08 13:33 | HLT | 2754707 | 2643 | 203 | 143 | 42 | 6 | 0 | 1274 | 1042.2652
21-0101516 | SANTA CRUZ | GREEN VALLEY 2101 | 3RD | 2021-08-07 13:32 | 8/2 to 8/8 | 2021-08-07 17:33 | HLT | 201161 | 1013 | 85 | 69 | 9 | 1 | 0 | 241 | 198.5795
21-0101504 | EL DORADO | SHINGLE SPRINGS 2110 | UNK | 2021-08-07 12:45 | 8/2 to 8/8 | 2021-08-07 17:10 | HLT | 228105 | 933 | 75 | 48 | 15 | 7 | 0 | 265 | 244.4855
21-0101385 | CALAVERAS | WEST POINT 1102 | EF | 2021-08-07 06:57 | 8/2 to 8/8 | 2021-08-07 18:02 | HLT | 1194033 | 1965 | 131 | 93 | 27 | 0 | 0 | 665 | 607.6504
21-0101099 | NEVADA | NARROWS 2105 | VEG | 2021-08-06 12:54 | 8/2 to 8/8 | 2021-08-06 21:38 | HLT | 859576 | 2099 | 173 | 100 | 28 | 5 | 0 | 524 | 409.5169
21-0101023 | LAKE | CLEAR LAKE 1101 | 3RD | 2021-08-06 11:20 | 8/2 to 8/8 | 2021-08-06 18:07 | HLT | 213268 | 524 | 35 | 21 | 8 | 0 | 1 | 407 | 407
21-0100932 | MADERA | OAKHURST 1101 | UNK | 2021-08-06 09:19 | 8/2 to 8/8 | 2021-08-06 15:47 | HLT | 475700 | 1474 | 166 | 122 | 30 | 2 | 0 | 388 | 322.7273
21-0100834 | FRESNO | AUBERRY 1101 | UNK | 2021-08-06 08:04 | 8/2 to 8/8 | 2021-08-06 14:46 | HLT | 289045 | 812 | 37 | 24 | 23 | 3 | 0 | 402 | 355.9667
21-0100780 | NEVADA | BRUNSWICK 1105 | UNK | 2021-08-06 07:05 | 8/2 to 8/8 | 2021-08-06 18:04 | HLT | 98058 | 205 | 12 | 9 | 6 | 0 | 0 | 659 | 478.3317
21-0100772 | SAN BENITO | LOS OSITOS 2103 | EF | 2021-08-06 06:43 | 8/2 to 8/8 | 2021-08-06 14:32 | HLT | 2250103 | 5259 | 126 | 83 | 66 | 19 | 0 | 469 | 427.8576
21-0100761 | SAN LUIS OBISPO | SAN LUIS OBISPO 1104 | EF | 2021-08-06 06:05 | 8/2 to 8/8 | 2021-08-06 12:16 | HLT | 189045 | 539 | 20 | 16 | 14 | 0 | 0 | 371 | 350.7328
21-0100756 | FRESNO | TIVY VALLEY 1107 | UNK | 2021-08-06 00:32 | 8/2 to 8/8 | 2021-08-06 10:40 | HLT | 434621 | 744 | 53 | 32 | 16 | 0 | 0 | 608 | 584.168
21-0100752 | SANTA BARBARA | SANTA YNEZ 1104 | UNK | 2021-08-05 23:55 | 8/2 to 8/8 | 2021-08-06 13:45 | HLT | 195500 | 436 | 8 | 4 | 7 | 2 | 0 | 830 | 448.3945
21-0089190 | TUOLUMNE | SPRING GAP 1702 | CI | 2021-08-05 19:58 | 8/2 to 8/8 | 2021-08-05 20:51 | HLT | 45713 | 1538 | 34 | 24 | 22 | 2 | 0 | 53 | 29.7224
21-0100687 | SAN BENITO | LOS OSITOS 2103 | EF | 2021-08-05 18:04 | 8/2 to 8/8 | 2021-08-06 05:25 | HLT | 555496 | 2724 | 69 | 45 | 27 | 6 | 0 | 681 | 203.9266
21-0100729 | SAN BENITO | PANOCHE 1103 | 3RD | 2021-08-05 16:23 | 8/2 to 8/8 | 2021-08-06 08:52 | HLT | 163021 | 203 | 2 | 2 | 8 | 1 | 0 | 989 | 803.0591
21-0100137 | YOLO | PUTAH CREEK 1102 | UNK | 2021-08-05 06:39 | 8/2 to 8/8 | 2021-08-05 14:11 | HLT | 109476 | 276 | 8 | 5 | 5 | 0 | 0 | 452 | 396.6522
21-0100128 | SANTA CLARA | MORGAN HILL 2105 | AN | 2021-08-05 06:34 | 8/2 to 8/8 | 2021-08-05 10:11 | HLT | 72044 | 332 | 21 | 16 | 1 | 0 | 1 | 217 | 217
21-0100126 | SANTA CRUZ | CAMP EVERS 2106 | UNK | 2021-08-05 06:30 | 8/2 to 8/8 | 2021-08-05 15:56 | HLT | 1030540 | 2853 | 223 | 176 | 44 | 8 | 0 | 566 | 361.2128
21-0100124 | SANTA CRUZ | CAMP EVERS 2106 | UNK | 2021-08-05 06:28 | 8/2 to 8/8 | 2021-08-05 12:33 | HLT | 187817 | 721 | 53 | 33 | 11 | 0 | 0 | 365 | 260.4951
21-0100065 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-08-04 20:31 | 8/2 to 8/8 | 2021-08-05 13:52 | HLT | 2678863 | 3001 | 227 | 173 | 45 | 4 | 0 | 1041 | 892.6568
21-0099932 | PLACER | SHADY GLEN 1101 | ENV | 2021-08-04 15:10 | 8/2 to 8/8 | 2021-08-06 17:47 | HLT | 34225 | 3172 | 306 | 207 | 62 | 12 | 0 | 2983 | 10.7897
21-0099572 | HUMBOLDT | HOOPA 1101 | UNK | 2021-08-04 09:21 | 8/2 to 8/8 | 2021-08-04 22:32 | HLT | 162946 | 206 | 4 | 4 | 8 | 1 | 0 | 791 | 791
21-0099476 | SANTA CRUZ | CAMP EVERS 2105 | VEG | 2021-08-04 07:55 | 8/2 to 8/8 | 2021-08-04 18:05 | HLT | 513025 | 1971 | 139 | 106 | 33 | 3 | 0 | 610 | 260.2867
21-0099454 | EL DORADO | PLACERVILLE 2106 | UNK | 2021-08-04 07:01 | 8/2 to 8/8 | 2021-08-04 14:58 | HLT | 662614 | 1744 | 130 | 79 | 25 | 4 | 1 | 477 | 379.9392
21-0099442 | HUMBOLDT | WILLOW CREEK 1103 | EF | 2021-08-04 06:15 | 8/2 to 8/8 | 2021-08-27 17:27 | HLT | 3297651 | 1309 | 82 | 60 | 14 | 3 | 0 | 33792 | 2519.2139
21-0099425 | PLUMAS | HAMILTON BRANCH 1101 | UNK | 2021-08-04 00:58 | 8/2 to 8/8 | 2021-08-04 04:47 | HLT | [9 empty] | Outage data under further review
21-0099402 | FRESNO | SAND CREEK 1103 | EF | 2021-08-03 20:45 | 8/2 to 8/8 | 2021-08-04 12:08 | HLT | 479960 | 520 | 53 | 34 | 5 | 0 | 0 | 923 | 923
21-0099376 | EL DORADO | EL DORADO PH 2101 | UNK | 2021-08-03 18:33 | 8/2 to 8/8 | 2021-08-04 12:35 | HLT | 890656 | 1087 | 25 | 15 | 51 | 1 | 0 | 1082 | 819.3707
21-0089426 | SAN MATEO | WOODSIDE 1101 | CI | 2021-08-02 20:25 | 8/2 to 8/8 | 2021-08-02 21:30 | HLT | 4485 | 69 | 6 | 6 | 1 | 1 | 0 | 65 | 65
21-0098752 | SANTA BARBARA | SANTA YNEZ 1104 | UNK | 2021-08-02 16:38 | 8/2 to 8/8 | 2021-08-03 10:21 | HLT | 225365 | 436 | 8 | 4 | 7 | 2 | 0 | 1063 | 516.8922
21-0098310 | PLACER | WEIMAR 1101 | AN | 2021-08-02 07:28 | 8/2 to 8/8 | 2021-08-02 10:34 | HLT | 92256 | 496 | 31 | 21 | 4 | 3 | 0 | 186 | 186
21-0098316 | SANTA CLARA | LOS GATOS 1106 | EF | 2021-08-02 07:28 | 8/2 to 8/8 | 2021-08-03 20:12 | HLT | 2217110 | 2065 | 143 | 101 | 54 | 8 | 0 | 2204 | 1073.661
21-0098296 | CALAVERAS | STANISLAUS 1702 | UNK | 2021-08-02 04:57 | 8/2 to 8/8 | 2021-08-02 10:51 | HLT | 398263 | 1467 | 58 | 48 | 16 | 0 | 0 | 354 | 271.4813
21-0098285 | MONTEREY | HATTON 1101 | AN | 2021-08-01 23:45 | 7/28 to 8/1 | 2021-08-02 11:10 | HLT | 1197179 | 2103 | 41 | 23 | 55 | 8 | 0 | 685 | 569.272
21-0098263 | SANTA CRUZ | CAMP EVERS 2106 | VEG | 2021-08-01 20:47 | 7/28 to 8/1 | 2021-08-03 13:30 | HLT | 1914387 | 2837 | 220 | 174 | 44 | 8 | 0 | 2443 | 674.7927
21-0098272 | SANTA CRUZ | CAMP EVERS 2106 | UNK | 2021-08-01 20:47 | 7/28 to 8/1 | 2021-08-03 21:05 | HLT | 642395 | 716 | 53 | 33 | 11 | 0 | 0 | 2898 | 897.1997
21-0098229 | SANTA CLARA | MORGAN HILL 2105 | UNK | 2021-08-01 15:11 | 7/28 to 8/1 | 2021-08-02 10:54 | HLT | 95529 | 165 | 6 | 4 | 2 | 0 | 0 | 1183 | 578.9636
21-0098197 | FRESNO | DUNLAP 1102 | VEG | 2021-08-01 10:14 | 7/28 to 8/1 | 2021-08-01 16:05 | HLT | 28748 | 82 | 4 | 4 | 2 | 0 | 0 | 351 | 350.5854
21-0098186 | NAPA | SILVERADO 2104 | AN | 2021-08-01 09:34 | 7/28 to 8/1 | 2021-08-01 23:59 | HLT | 1301176 | 2359 | 106 | 66 | 62 | 9 | 20 | 865 | 551.5795
21-0098180 | MARIN | SAN RAFAEL 1108 | AN | 2021-08-01 08:01 | 7/28 to 8/1 | 2021-08-01 15:19 | HLT | 1176593 | 3095 | 94 | 52 | 25 | 1 | 0 | 438 | 380.1593
21-0098178 | TUOLUMNE | MIWUK 1702 | EF | 2021-08-01 07:34 | 7/28 to 8/1 | 2021-08-02 02:08 | HLT | 131481 | 526 | 49 | 32 | 5 | 0 | 0 | 1114 | 249.9639
21-0098174 | SHASTA | JESSUP 1101 | UNK | 2021-08-01 07:04 | 7/28 to 8/1 | 2021-08-01 17:53 | HLT | 704838 | 1794 | 175 | 123 | 19 | 4 | 0 | 649 | 392.8863
21-0098167 | SAN LUIS OBISPO | CAMBRIA 1102 | AN | 2021-08-01 04:53 | 7/28 to 8/1 | 2021-08-01 07:48 | HLT | 107625 | 615 | 25 | 22 | 6 | 0 | 0 | 175 | 175
21-0098158 | SONOMA | GEYSERVILLE 1101 | VEG | 2021-08-01 01:38 | 7/28 to 8/1 | 2021-08-01 21:36 | HLT | 282112 | 441 | 10 | 7 | 4 | 0 | 0 | 1198 | 639.7098
21-0098116 | NAPA | PUEBLO 2103 | UNK | 2021-07-31 20:21 | 7/28 to 8/1 | 2021-08-01 12:08 | HLT | 293132 | 316 | 6 | 4 | 3 | 2 | 0 | 947 | 927.6329
21-0097837 | SANTA BARBARA | SANTA YNEZ 1101 | UNK | 2021-07-31 00:44 | 7/28 to 8/1 | 2021-07-31 15:35 | HLT | 254862 | 363 | 4 | 4 | 28 | 0 | 0 | 891 | 702.0992
21-0097727 | NAPA | SILVERADO 2104 | UNK | 2021-07-30 17:08 | 7/28 to 8/1 | 2021-07-31 12:52 | HLT | 1823659 | 2359 | 106 | 66 | 62 | 9 | 20 | 1184 | 773.0644
21-0097351 | SOLANO | VACA DIXON 1105 | 3RD | 2021-07-30 09:52 | 7/28 to 8/1 | 2021-07-30 11:20 | HLT | 141680 | 1610 | 169 | 108 | 16 | 0 | 0 | 88 | 88
21-0097300 | NEVADA | BRUNSWICK 1105 | AN | 2021-07-30 08:59 | 7/28 to 8/1 | 2021-07-30 15:00 | HLT | 328847 | 1226 | 97 | 56 | 27 | 0 | 0 | 361 | 268.2276
21-0097203 | SAN BENITO | SAN JUSTO 1101 | UNK | 2021-07-30 05:58 | 7/28 to 8/1 | 2021-07-30 10:49 | HLT | 31882 | 170 | 8 | 4 | 13 | 0 | 0 | 291 | 187.5412
21-0097201 | EL DORADO | APPLE HILL 2102 | UNK | 2021-07-30 05:32 | 7/28 to 8/1 | 2021-07-30 11:41 | HLT | 252620 | 748 | 58 | 36 | 9 | 0 | 0 | 369 | 337.7273
21-0097184 | FRESNO | TIVY VALLEY 1107 | EF | 2021-07-30 01:13 | 7/28 to 8/1 | 2021-07-30 13:19 | HLT | 450912 | 744 | 53 | 32 | 16 | 0 | 0 | 726 | 606.0645
21-0097099 | HUMBOLDT | HOOPA 1101 | AN | 2021-07-29 21:53 | 7/28 to 8/1 | 2021-07-30 14:30 | HLT | 112884 | 245 | 10 | 7 | 8 | 0 | 0 | 997 | 460.751
21-0096774 | SANTA CRUZ | ROB ROY 2104 | UNK | 2021-07-29 11:18 | 7/28 to 8/1 | 2021-07-29 21:33 | HLT | 758463 | 2329 | 148 | 122 | 34 | 6 | 0 | 615 | 325.6604
21-0096645 | NEVADA | NARROWS 2105 | UNK | 2021-07-29 09:26 | 7/28 to 8/1 | 2021-07-29 15:47 | HLT | 789060 | 2088 | 175 | 101 | 28 | 5 | 0 | 381 | 377.9023
21-0096456 | CALAVERAS | STANISLAUS 1702 | VEG | 2021-07-28 22:00 | 7/28 to 8/1 | 2021-07-29 15:04 | HLT | 968306 | 1439 | 58 | 48 | 15 | 0 | 0 | 1024 | 672.902
21-0095921 | SANTA CRUZ | CAMP EVERS 2105 | UNK | 2021-07-28 07:05 | 7/28 to 8/1 | 2021-07-28 08:42 | HLT | 12125 | 125 | 9 | 6 | 3 | 0 | 0 | 97 | 97

## Outages 110121_113021
Outage ID | County | Circuit | Cause | FNL | Week | End_Date_Time | EPSS Outage Type | Customer Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Duration | CAIDI | Comments
21-0143043 | MONTEREY | LOS OSITOS 2103 | UNK | 2021-11-06 12:55 | 11/1 to 11/7 | 2021-11-06 14:36 | FTS | 808 | 8 | 0 | 0 | 1 | 0 | 0 | 101 | 101
21-0142951 | SAN LUIS OBISPO | TEMPLETON 2113 | UNK | 2021-11-05 16:00 | 11/1 to 11/7 | 2021-11-05 17:59 | FTS | 524037 | 5510 | 274 | 189 | 84 | 9 | 1 | 119 | 95.1065
21-0142562 | SAN LUIS OBISPO | CAYUCOS 1102 | UNK | 2021-11-04 20:15 | 11/1 to 11/7 | 2021-11-04 20:40 | FTS | 2600 | 104 | 1 | 1 | 0 | 0 | 0 | 25 | 25
21-0142460 | SANTA BARBARA | SISQUOC 1103 | UNK | 2021-11-04 15:42 | 11/1 to 11/7 | 2021-11-04 16:30 | FTS | 1824 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 48
21-0141991 | SAN LUIS OBISPO | PERRY 1101 | UNK | 2021-11-03 19:41 | 11/1 to 11/7 | 2021-11-03 20:07 | FTS | 40950 | 1575 | 66 | 43 | 10 | 0 | 0 | 26 | 26
21-0141902 | SANTA BARBARA | SISQUOC 1103 | UNK | 2021-11-03 15:29 | 11/1 to 11/7 | 2021-11-03 15:36 | FTS | 266 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 7
21-0141398 | SAN LUIS OBISPO | TEMPLETON 2110 | VEG | 2021-11-02 17:04 | 11/1 to 11/7 | 2021-11-03 04:40 | FTS | 152645 | 1604 | 47 | 33 | 23 | 0 | 0 | 696 | 95.1652
21-0141204 | FRESNO | DUNLAP 1102 | EF | 2021-11-02 12:13 | 11/1 to 11/7 | 2021-11-03 12:34 | FTS | 77976 | 308 | 6 | 4 | 7 | 0 | 0 | 1408 | 253.1688
21-0140718 | SAN LUIS OBISPO | TEMPLETON 2113 | 3RD | 2021-11-01 14:13 | 11/1 to 11/7 | 2021-11-01 14:19 | FTS | 984 | 164 | 10 | 4 | 4 | 0 | 1 | 6 | 6

## EPSS Outages_Circuit
Row Labels | Count of Outage ID
CAMP EVERS 2105 | 19
TEMPLETON 2113 | 15
PLACERVILLE 2106 | 14
ORO FINO 1102 | 12
SILVERADO 2104 | 11
BANGOR 1101 | 11
WEST POINT 1102 | 11
CAMP EVERS 2106 | 10
ROB ROY 2104 | 10
APPLE HILL 2102 | 10
PANOCHE 1103 | 9
FROGTOWN 1702 | 9
GREEN VALLEY 2101 | 9
LOS GATOS 1106 | 9
HALF MOON BAY 1103 | 8
GEYSERVILLE 1101 | 8
PUEBLO 2103 | 8
GEYSERVILLE 1102 | 8
SHINGLE SPRINGS 2110 | 8
BIG BASIN 1102 | 8
COARSEGOLD 2104 | 8
MARIPOSA 2101 | 8
PERRY 1101 | 7
WILLOW CREEK 1103 | 7
ATASCADERO 1103 | 7
PAUL SWEET 2106 | 7
SHADY GLEN 1101 | 7
HICKS 2101 | 7
HOOPA 1101 | 7
LOS OSITOS 2103 | 7
EL DORADO PH 2101 | 6
TIVY VALLEY 1107 | 6
CURTIS 1703 | 6
GANSNER 1101 | 6
MORGAN HILL 2105 | 6
NARROWS 2105 | 6
SILVERADO 2102 | 5
MIWUK 1702 | 5
SISQUOC 1102 | 5
AUBERRY 1101 | 5
SAN RAFAEL 1108 | 5
BRUNSWICK 1105 | 5
DESCHUTES 1104 | 5
PEORIA 1701 | 5
LLAGAS 2101 | 5
KONOCTI 1102 | 5
SALT SPRINGS 2102 | 5
PUTAH CREEK 1102 | 5
SAN JUSTO 1101 | 4
DUNLAP 1102 | 4
STANISLAUS 1702 | 4
GIRVAN 1102 | 4
MOLINO 1102 | 4
SAND CREEK 1103 | 4
JESSUP 1102 | 4
SANTA YNEZ 1104 | 4
TEMPLETON 2110 | 4
CURTIS 1705 | 4
WOODSIDE 1104 | 4
DEL MONTE 2104 | 4
WOODACRE 1101 | 4
BEAR VALLEY 2105 | 4
MENDOCINO 1101 | 4
OLETA 1102 | 4
CAYUCOS 1102 | 3
GIRVAN 1101 | 3
WEST POINT 1101 | 3
NARROWS 2102 | 3
SISQUOC 1103 | 3
OAKHURST 1101 | 3
VACA DIXON 1105 | 3
CHALLENGE 1102 | 3
MENLO 1102 | 3
CLEAR LAKE 1101 | 3
LOS GATOS 1107 | 3
HATTON 1101 | 3
LOW GAP 1101 | 3
FORT ROSS 1121 | 3
MARIPOSA 2102 | 3
SAN RAMON 2108 | 3
VOLTA 1101 | 3
BRUNSWICK 1103 | 3
DUNLAP 1103 | 3
SARATOGA 1107 | 3
MENLO 1103 | 3
FORESTHILL 1101 | 3
JESSUP 1101 | 3
TEJON 1102 | 2
CURTIS 1704 | 2
HIGHLANDS 1103 | 2
HALF MOON BAY 1101 | 2
WOODSIDE 1101 | 2
MIDDLETOWN 1101 | 2
COTTONWOOD 1103 | 2
SANTA YNEZ 1101 | 2
RED BLUFF 1103 | 2
ELK CREEK 1101 | 2
FULTON 1107 | 2
MONTE RIO 1111 | 2
INDIAN FLAT 1104 | 2
KANAKA 1101 | 2
BEN LOMOND 0401 | 2
OTTER 1101 | 2
BEAR VALLEY 2101 | 2
CLAYTON 2212 | 2
VACAVILLE 1108 | 2
CASTRO VALLEY 1108 | 2
WEIMAR 1101 | 2
CAMBRIA 1102 | 2
HOLLISTER 2105 | 2
CALISTOGA 1101 | 2
HAMILTON BRANCH 1101 | 2
SPRING GAP 1702 | 2
SAN LUIS OBISPO 1104 | 2
ALLEGHANY 1101 | 2
SWIFT 2110 | 2
Grand Total | 566

## EPSS Outage Trends - CESO
Comments | (blank)
Row Labels | Count of Outage ID | Average of CESO | Average CESO % Increase / (Decrease)
ALLEGHANY 1101 | 2 | 756
Aug | 1 | 604 | 100%
Sep | 1 | 908 | 150.3%
APPLE HILL 2102 | 10 | 1347.2
Jul | 1 | 748 | 100%
Aug | 3 | 1767.3333 | 236.3%
Sep | 4 | 1573.5 | 89.03%
Oct | 2 | 564 | 35.84%
ATASCADERO 1103 | 7 | 1140.2857
Aug | 1 | 603 | 100%
Sep | 5 | 1315 | 218.1%
Oct | 1 | 804 | 61.14%
AUBERRY 1101 | 5 | 1150.8
Aug | 2 | 1090.5 | 100%
Sep | 1 | 1374 | 126%
Oct | 2 | 1099.5 | 80.02%
BANGOR 1101 | 11 | 687.8182
Aug | 6 | 906.8333 | 100%
Sep | 5 | 425 | 46.87%
BEAR VALLEY 2101 | 2 | 673
Oct | 2 | 673 | 100%
BEAR VALLEY 2105 | 4 | 517.25
Sep | 2 | 444 | 100%
Oct | 2 | 590.5 | 133%
BEN LOMOND 0401 | 2 | 124
Sep | 2 | 124 | 100%
BIG BASIN 1102 | 8 | 704.875
Aug | 1 | 823 | 100%
Sep | 2 | 1085 | 131.8%
Oct | 5 | 529.2 | 48.77%
BRUNSWICK 1103 | 3 | 759.3333
Aug | 2 | 1074 | 100%
Sep | 1 | 130 | 12.1%
BRUNSWICK 1105 | 4 | 863.25
Jul | 1 | 1226 | 100%
Aug | 1 | 205 | 16.72%
Sep | 1 | 1083 | 528.3%
Oct | 1 | 939 | 86.7%
CALISTOGA 1101 | 2 | 42
Aug | 1 | 26 | 100%
Oct | 1 | 58 | 223.1%
CAMBRIA 1102 | 2 | 919
Aug | 1 | 615 | 100%
Oct | 1 | 1223 | 198.9%
CAMP EVERS 2105 | 19 | 1812.1579
Jul | 1 | 125 | 100%
Aug | 6 | 1427.1667 | 1142%
Sep | 7 | 2636.4286 | 184.7%
Oct | 5 | 1457.6 | 55.29%
CAMP EVERS 2106 | 10 | 2130.1
Aug | 5 | 1996.2 | 100%
Sep | 1 | 451 | 22.59%
Oct | 4 | 2717.25 | 602.5%
CASTRO VALLEY 1108 | 2 | 1088
Aug | 2 | 1088 | 100%
CAYUCOS 1102 | 3 | 86.6667
Sep | 2 | 78 | 100%
Nov | 1 | 104 | 133.3%
CHALLENGE 1102 | 3 | 432.6667
Sep | 1 | 200 | 100%
Oct | 2 | 549 | 274.5%
CLAYTON 2212 | 2 | 3429
Sep | 1 | 3431 | 100%
Oct | 1 | 3427 | 99.88%
CLEAR LAKE 1101 | 3 | 511.3333
Aug | 1 | 524 | 100%
Sep | 1 | 487 | 92.94%
Oct | 1 | 523 | 107.4%
COARSEGOLD 2104 | 8 | 2384.125
Aug | 5 | 2433.8 | 100%
Sep | 2 | 2660 | 109.3%
Oct | 1 | 1584 | 59.55%
COTTONWOOD 1103 | 2 | 702.5
Sep | 2 | 702.5 | 100%
CURTIS 1703 | 6 | 1646.3333
Aug | 1 | 3861 | 100%
Sep | 2 | 1237.5 | 32.05%
Oct | 3 | 1180.6667 | 95.41%
CURTIS 1704 | 2 | 1556.5
Aug | 1 | 1556 | 100%
Sep | 1 | 1557 | 100.1%
CURTIS 1705 | 4 | 637
Aug | 2 | 592 | 100%
Sep | 2 | 682 | 115.2%
DEL MONTE 2104 | 4 | 4376
Aug | 2 | 5055.5 | 100%
Oct | 2 | 3696.5 | 73.12%
DESCHUTES 1104 | 5 | 557.8
Sep | 2 | 453.5 | 100%
Oct | 3 | 627.3333 | 138.3%
DUNLAP 1102 | 4 | 251.5
Aug | 2 | 195 | 100%
Sep | 1 | 308 | 157.9%
Nov | 1 | 308 | 100%
DUNLAP 1103 | 3 | 556
Aug | 3 | 556 | 100%
EL DORADO PH 2101 | 6 | 1398.5
Aug | 1 | 1087 | 100%
Sep | 4 | 1305 | 120.1%
Oct | 1 | 2084 | 159.7%
ELK CREEK 1101 | 2 | 445.5
Sep | 1 | 322 | 100%
Oct | 1 | 569 | 176.7%
FORESTHILL 1101 | 2 | 1959
Aug | 2 | 1959 | 100%
FORT ROSS 1121 | 3 | 224.6667
Oct | 3 | 224.6667 | 100%
FROGTOWN 1702 | 9 | 612.7778
Aug | 2 | 813 | 100%
Sep | 5 | 452.8 | 55.69%
Oct | 2 | 812.5 | 179.4%
FULTON 1107 | 2 | 449.5
Sep | 2 | 449.5 | 100%
GANSNER 1101 | 6 | 1404.6667
Aug | 3 | 2605 | 100%
Sep | 2 | 204.5 | 7.85%
Oct | 1 | 204 | 99.76%
GEYSERVILLE 1101 | 8 | 302.75
Aug | 3 | 266.6667 | 100%
Sep | 4 | 352.5 | 132.2%
Oct | 1 | 212 | 60.14%
GEYSERVILLE 1102 | 8 | 436.125
Aug | 1 | 568 | 100%
Sep | 5 | 383.2 | 67.46%
Oct | 2 | 502.5 | 131.1%
GIRVAN 1101 | 3 | 835.3333
Aug | 1 | 154 | 100%
Sep | 2 | 1176 | 763.6%
GIRVAN 1102 | 4 | 735.75
Sep | 3 | 416 | 100%
Oct | 1 | 1695 | 407.5%
GREEN VALLEY 2101 | 9 | 635.2222
Aug | 4 | 660 | 100%
Sep | 3 | 638.6667 | 96.77%
Oct | 2 | 580.5 | 90.89%
HALF MOON BAY 1101 | 2 | 173.5
Aug | 1 | 306 | 100%
Sep | 1 | 41 | 13.4%
HALF MOON BAY 1103 | 8 | 1835.625
Aug | 1 | 2983 | 100%
Sep | 6 | 1783.3333 | 59.78%
Oct | 1 | 1002 | 56.19%
HATTON 1101 | 3 | 2411
Aug | 2 | 2565 | 100%
Oct | 1 | 2103 | 81.99%
HICKS 2101 | 7 | 2066.1429
Aug | 3 | 3150.6667 | 100%
Sep | 2 | 1877 | 59.57%
Oct | 2 | 628.5 | 33.48%
HIGHLANDS 1103 | 2 | 685
Sep | 1 | 56 | 100%
Oct | 1 | 1314 | 2346%
HOLLISTER 2105 | 2 | 361.5
Aug | 1 | 127 | 100%
Oct | 1 | 596 | 469.3%
HOOPA 1101 | 7 | 415.4286
Jul | 1 | 245 | 100%
Aug | 2 | 437 | 178.4%
Oct | 4 | 447.25 | 102.3%
INDIAN FLAT 1104 | 2 | 208.5
Sep | 2 | 208.5 | 100%
JESSUP 1101 | 3 | 1876
Aug | 1 | 1794 | 100%
Sep | 2 | 1917 | 106.9%
JESSUP 1102 | 4 | 624.25
Aug | 2 | 900.5 | 100%
Oct | 2 | 348 | 38.65%
KANAKA 1101 | 2 | 379
Aug | 1 | 379 | 100%
Oct | 1 | 379 | 100%
KONOCTI 1102 | 5 | 1080.4
Aug | 2 | 471 | 100%
Sep | 3 | 1486.6667 | 315.6%
LOS GATOS 1106 | 9 | 1773.2222
Aug | 5 | 2194.2 | 100%
Sep | 2 | 1954.5 | 89.08%
Oct | 2 | 539.5 | 27.6%
LOS GATOS 1107 | 3 | 922
Sep | 1 | 934 | 100%
Oct | 2 | 916 | 98.07%
LOS OSITOS 2103 | 7 | 1390.7143
Aug | 3 | 2941.3333 | 100%
Oct | 3 | 301 | 10.23%
Nov | 1 | 8 | 2.658%
LOW GAP 1101 | 3 | 734.3333
Aug | 1 | 733 | 100%
Sep | 2 | 735 | 100.3%
MARIPOSA 2101 | 8 | 2053
Aug | 3 | 2251.6667 | 100%
Sep | 1 | 2909 | 129.2%
Oct | 4 | 1690 | 58.1%
MARIPOSA 2102 | 3 | 1888.6667
Aug | 2 | 1534 | 100%
Sep | 1 | 2598 | 169.4%
MENDOCINO 1101 | 4 | 706.5
Sep | 2 | 744 | 100%
Oct | 2 | 669 | 89.92%
MENLO 1102 | 3 | 583.6667
Sep | 1 | 301 | 100%
Oct | 2 | 725 | 240.9%
MENLO 1103 | 3 | 218.3333
Sep | 2 | 177.5 | 100%
Oct | 1 | 300 | 169%
MIDDLETOWN 1101 | 2 | 2084
Sep | 2 | 2084 | 100%
MIWUK 1702 | 5 | 945
Aug | 2 | 479.5 | 100%
Sep | 1 | 438 | 91.35%
Oct | 2 | 1664 | 379.9%
MOLINO 1102 | 4 | 2091.75
Aug | 2 | 2088.5 | 100%
Sep | 2 | 2095 | 100.3%
MONTE RIO 1111 | 2 | 1371
Aug | 1 | 1259 | 100%
Sep | 1 | 1483 | 117.8%
MORGAN HILL 2105 | 6 | 1347.8333
Aug | 3 | 532 | 100%
Sep | 1 | 1099 | 206.6%
Oct | 2 | 2696 | 245.3%
NARROWS 2102 | 3 | 1186.6667
Aug | 1 | 1786 | 100%
Sep | 1 | 887 | 49.66%
Oct | 1 | 887 | 100%
NARROWS 2105 | 6 | 1593.8333
Jul | 1 | 2088 | 100%
Aug | 1 | 2099 | 100.5%
Oct | 4 | 1344 | 64.03%
OAKHURST 1101 | 3 | 1869.3333
Aug | 2 | 1769 | 100%
Sep | 1 | 2070 | 117%
OLETA 1102 | 4 | 542.75
Aug | 1 | 257 | 100%
Oct | 3 | 638 | 248.2%
ORO FINO 1102 | 12 | 651.8333
Aug | 2 | 1087 | 100%
Sep | 7 | 563.2857 | 51.82%
Oct | 3 | 568.3333 | 100.9%
OTTER 1101 | 2 | 257.5
Sep | 2 | 257.5 | 100%
PANOCHE 1103 | 9 | 160
Aug | 1 | 203 | 100%
Sep | 2 | 105.5 | 51.97%
Oct | 6 | 171 | 162.1%
PAUL SWEET 2106 | 7 | 313.1429
Aug | 1 | 347 | 100%
Sep | 1 | 347 | 100%
Oct | 5 | 299.6 | 86.34%
PEORIA 1701 | 5 | 1392.6
Aug | 3 | 1263.6667 | 100%
Oct | 2 | 1586 | 125.5%
PERRY 1101 | 7 | 1303.5714
Aug | 1 | 147 | 100%
Sep | 2 | 1150.5 | 782.7%
Oct | 3 | 1700.6667 | 147.8%
Nov | 1 | 1575 | 92.61%
PLACERVILLE 2106 | 14 | 1946.1429
Aug | 7 | 2284.2857 | 100%
Sep | 4 | 2248.5 | 98.43%
Oct | 3 | 754 | 33.53%
PUEBLO 2103 | 8 | 621
Jul | 1 | 316 | 100%
Aug | 1 | 316 | 100%
Sep | 4 | 547.5 | 173.3%
Oct | 2 | 1073 | 196%
PUTAH CREEK 1102 | 5 | 237.6
Aug | 3 | 215.3333 | 100%
Sep | 2 | 271 | 125.9%
RED BLUFF 1103 | 2 | 2723
Sep | 2 | 2723 | 100%
ROB ROY 2104 | 10 | 1809.2
Jul | 1 | 2329 | 100%
Aug | 4 | 1424 | 61.14%
Sep | 3 | 2391 | 167.9%
Oct | 2 | 1447 | 60.52%
SALT SPRINGS 2102 | 5 | 1631
Sep | 3 | 1069 | 100%
Oct | 2 | 2474 | 231.4%
SAN JUSTO 1101 | 4 | 168
Jul | 1 | 170 | 100%
Aug | 1 | 166 | 97.65%
Sep | 1 | 170 | 102.4%
Oct | 1 | 166 | 97.65%
SAN LUIS OBISPO 1104 | 2 | 537
Aug | 1 | 539 | 100%
Oct | 1 | 535 | 99.26%
SAN RAFAEL 1108 | 5 | 2881.2
Aug | 4 | 2039.25 | 100%
Oct | 1 | 6249 | 306.4%
SAN RAMON 2108 | 3 | 2567.6667
Sep | 2 | 1948.5 | 100%
Oct | 1 | 3806 | 195.3%
SAND CREEK 1103 | 4 | 492.25
Aug | 1 | 520 | 100%
Sep | 1 | 296 | 56.92%
Oct | 2 | 576.5 | 194.8%
SANTA YNEZ 1101 | 2 | 277.5
Jul | 1 | 363 | 100%
Sep | 1 | 192 | 52.89%
SANTA YNEZ 1104 | 4 | 288.25
Aug | 2 | 436 | 100%
Sep | 1 | 140 | 32.11%
Oct | 1 | 141 | 100.7%
SARATOGA 1107 | 3 | 952.3333
Aug | 2 | 199.5 | 100%
Oct | 1 | 2458 | 1232%
SHADY GLEN 1101 | 7 | 1120.7143
Aug | 2 | 2079 | 100%
Sep | 3 | 571.6667 | 27.5%
Oct | 2 | 986 | 172.5%
SHINGLE SPRINGS 2110 | 8 | 1022.875
Aug | 3 | 885 | 100%
Sep | 4 | 1130.75 | 127.8%
Oct | 1 | 1005 | 88.88%
SILVERADO 2102 | 5 | 347.6
Aug | 2 | 335 | 100%
Sep | 1 | 275 | 82.09%
Oct | 2 | 396.5 | 144.2%
SILVERADO 2104 | 11 | 1248
Jul | 1 | 2359 | 100%
Aug | 5 | 1580.8 | 67.01%
Sep | 3 | 666 | 42.13%
Oct | 2 | 733.5 | 110.1%
SISQUOC 1102 | 5 | 148.8
Aug | 2 | 208 | 100%
Sep | 2 | 99.5 | 47.84%
Oct | 1 | 129 | 129.6%
SISQUOC 1103 | 3 | 37.6667
Oct | 1 | 37 | 100%
Nov | 2 | 38 | 102.7%
SPRING GAP 1702 | 2 | 1538
Aug | 1 | 1538 | 100%
Sep | 1 | 1538 | 100%
STANISLAUS 1702 | 4 | 2090.5
Jul | 1 | 1439 | 100%
Aug | 2 | 1962.5 | 136.4%
Oct | 1 | 2998 | 152.8%
SWIFT 2110 | 2 | 95
Oct | 2 | 95 | 100%
TEJON 1102 | 2 | 260.5
Aug | 1 | 499 | 100%
Sep | 1 | 22 | 4.409%
TEMPLETON 2110 | 4 | 1233.25
Aug | 1 | 1003 | 100%
Sep | 1 | 1003 | 100%
Oct | 1 | 1323 | 131.9%
Nov | 1 | 1604 | 121.2%
TEMPLETON 2113 | 15 | 1758.2667
Aug | 4 | 1455.25 | 100%
Sep | 7 | 1627.2857 | 111.8%
Oct | 2 | 1744 | 107.2%
Nov | 2 | 2837 | 162.7%
TIVY VALLEY 1107 | 6 | 683.1667
Jul | 1 | 744 | 100%
Aug | 2 | 788.5 | 106%
Sep | 1 | 515 | 65.31%
Oct | 2 | 631.5 | 122.6%
VACA DIXON 1105 | 3 | 916.3333
Jul | 1 | 1610 | 100%
Oct | 2 | 569.5 | 35.37%
VACAVILLE 1108 | 2 | 419
Aug | 1 | 420 | 100%
Sep | 1 | 418 | 99.52%
VOLTA 1101 | 3 | 371.3333
Aug | 1 | 242 | 100%
Oct | 2 | 436 | 180.2%
WEIMAR 1101 | 2 | 423
Aug | 2 | 423 | 100%
WEST POINT 1101 | 3 | 1773
Aug | 1 | 1779 | 100%
Sep | 1 | 1779 | 100%
Oct | 1 | 1761 | 98.99%
WEST POINT 1102 | 11 | 1149.6364
Aug | 3 | 1965 | 100%
Sep | 4 | 859.75 | 43.75%
Oct | 4 | 828 | 96.31%
WILLOW CREEK 1103 | 6 | 1069.6667
Aug | 3 | 1236.6667 | 100%
Sep | 3 | 902.6667 | 72.99%
WOODACRE 1101 | 4 | 622.5
Sep | 3 | 740 | 100%
Oct | 1 | 270 | 36.49%
WOODSIDE 1101 | 2 | 469
Aug | 2 | 469 | 100%
WOODSIDE 1104 | 4 | 702.75
Aug | 2 | 1197.5 | 100%
Sep | 2 | 208 | 17.37%
LLAGAS 2101 | 5 | 1001.6
Aug | 1 | 1002 | 100%
Sep | 2 | 1002 | 100%
Oct | 2 | 1001 | 99.9%
Grand Total | 561 | 1129.959

## EPSS Outage Trends - Duration
Comments | (blank)
Row Labels | Count of Outage ID | Average of Duration | Average Duration % Increase / (Decrease)
ALLEGHANY 1101 | 2 | 893
Aug | 1 | 496
Sep | 1 | 1290 | 160.1%
APPLE HILL 2102 | 10 | 2229.3
Jul | 1 | 369
Aug | 3 | 6400 | 1634%
Sep | 4 | 561.75 | -91.22%
Oct | 2 | 238.5 | -57.54%
ATASCADERO 1103 | 7 | 767.4286
Aug | 1 | 932
Sep | 5 | 797.2 | -14.46%
Oct | 1 | 454 | -43.05%
AUBERRY 1101 | 5 | 693.2
Aug | 2 | 412
Sep | 1 | 1055 | 156.1%
Oct | 2 | 793.5 | -24.79%
BANGOR 1101 | 11 | 470.6364
Aug | 6 | 624
Sep | 5 | 286.6 | -54.07%
BEAR VALLEY 2101 | 2 | 453.5
Oct | 2 | 453.5
BEAR VALLEY 2105 | 4 | 511.25
Sep | 2 | 400.5
Oct | 2 | 622 | 55.31%
BEN LOMOND 0401 | 2 | 668
Sep | 2 | 668
BIG BASIN 1102 | 8 | 441.125
Aug | 1 | 424
Sep | 2 | 1044 | 146.2%
Oct | 5 | 203.4 | -80.52%
BRUNSWICK 1103 | 3 | 221
Aug | 2 | 242.5
Sep | 1 | 178 | -26.6%
BRUNSWICK 1105 | 4 | 448.5
Jul | 1 | 361
Aug | 1 | 659 | 82.55%
Sep | 1 | 525 | -20.33%
Oct | 1 | 249 | -52.57%
CALISTOGA 1101 | 2 | 367
Aug | 1 | 254
Oct | 1 | 480 | 88.98%
CAMBRIA 1102 | 2 | 822
Aug | 1 | 175
Oct | 1 | 1469 | 739.4%
CAMP EVERS 2105 | 19 | 621.7222
Jul | 1 | 97
Aug | 6 | 803 | 727.8%
Sep | 7 | 632.3333 | -21.25%
Oct | 5 | 496.4 | -21.5%
CAMP EVERS 2106 | 10 | 976.5
Aug | 5 | 1467.2
Sep | 1 | 227 | -84.53%
Oct | 4 | 550.5 | 142.5%
CASTRO VALLEY 1108 | 2 | 163
Aug | 2 | 163
CAYUCOS 1102 | 3 | 904.6667
Sep | 2 | 1344.5
Nov | 1 | 25 | -98.14%
CHALLENGE 1102 | 3 | 330.6667
Sep | 1 | 210
Oct | 2 | 391 | 86.19%
CLAYTON 2212 | 2 | 1087
Sep | 1 | 997
Oct | 1 | 1177 | 18.05%
CLEAR LAKE 1101 | 3 | 531.3333
Aug | 1 | 407
Sep | 1 | 241 | -40.79%
Oct | 1 | 946 | 292.5%
COARSEGOLD 2104 | 8 | 646.25
Aug | 5 | 542.8
Sep | 2 | 773 | 42.41%
Oct | 1 | 910 | 17.72%
COTTONWOOD 1103 | 2 | 966
Sep | 2 | 966
CURTIS 1703 | 6 | 646.8333
Aug | 1 | 216
Sep | 2 | 843 | 290.3%
Oct | 3 | 659.6667 | -21.75%
CURTIS 1704 | 2 | 458
Aug | 1 | 550
Sep | 1 | 366 | -33.45%
CURTIS 1705 | 4 | 178
Aug | 2 | 158
Sep | 2 | 198 | 25.32%
DEL MONTE 2104 | 4 | 459
Aug | 2 | 785
Oct | 2 | 133 | -83.06%
DESCHUTES 1104 | 5 | 399.4
Sep | 2 | 385
Oct | 3 | 409 | 6.234%
DUNLAP 1102 | 4 | 931.75
Aug | 2 | 441.5
Sep | 1 | 1436 | 225.3%
Nov | 1 | 1408 | -1.95%
DUNLAP 1103 | 3 | 511.3333
Aug | 3 | 511.3333
EL DORADO PH 2101 | 6 | 590.5
Aug | 1 | 1082
Sep | 4 | 549.25 | -49.24%
Oct | 1 | 264 | -51.93%
ELK CREEK 1101 | 2 | 1295.5
Sep | 1 | 790
Oct | 1 | 1801 | 128%
FORESTHILL 1101 | 2 | 900
Aug | 2 | 900
FORT ROSS 1121 | 3 | 821.3333
Oct | 3 | 821.3333
FROGTOWN 1702 | 9 | 558.3333
Aug | 2 | 1078
Sep | 5 | 458 | -57.51%
Oct | 2 | 289.5 | -36.79%
FULTON 1107 | 2 | 452
Sep | 2 | 452
GANSNER 1101 | 6 | 564.6667
Aug | 3 | 483.6667
Sep | 2 | 500.5 | 3.48%
Oct | 1 | 936 | 87.01%
GEYSERVILLE 1101 | 8 | 443.5
Aug | 3 | 728.6667
Sep | 4 | 302 | -58.55%
Oct | 1 | 154 | -49.01%
GEYSERVILLE 1102 | 8 | 388.375
Aug | 1 | 235
Sep | 5 | 514.8 | 119.1%
Oct | 2 | 149 | -71.06%
GIRVAN 1101 | 3 | 364
Aug | 1 | 266
Sep | 2 | 413 | 55.26%
GIRVAN 1102 | 4 | 291.5
Sep | 3 | 199
Oct | 1 | 569 | 185.9%
GREEN VALLEY 2101 | 9 | 394.1111
Aug | 4 | 496.25
Sep | 3 | 426.3333 | -14.09%
Oct | 2 | 141.5 | -66.81%
HALF MOON BAY 1101 | 2 | 1217.5
Aug | 1 | 1173
Sep | 1 | 1262 | 7.587%
HALF MOON BAY 1103 | 8 | 921.5
Aug | 1 | 1372
Sep | 6 | 914.5 | -33.35%
Oct | 1 | 513 | -43.9%
HATTON 1101 | 3 | 315
Aug | 2 | 419.5
Oct | 1 | 106 | -74.73%
HICKS 2101 | 7 | 382.5714
Aug | 3 | 576.3333
Sep | 2 | 363.5 | -36.93%
Oct | 2 | 111 | -69.46%
HIGHLANDS 1103 | 2 | 527.5
Sep | 1 | 809
Oct | 1 | 246 | -69.59%
HOLLISTER 2105 | 2 | 498.5
Aug | 1 | 696
Oct | 1 | 301 | -56.75%
HOOPA 1101 | 7 | 1149
Jul | 1 | 997
Aug | 2 | 1159 | 16.25%
Oct | 4 | 1182 | 1.984%
INDIAN FLAT 1104 | 2 | 770.5
Sep | 2 | 770.5
JESSUP 1101 | 3 | 594.6667
Aug | 1 | 649
Sep | 2 | 567.5 | -12.56%
JESSUP 1102 | 4 | 516.75
Aug | 2 | 485
Oct | 2 | 548.5 | 13.09%
KANAKA 1101 | 2 | 223
Aug | 1 | 268
Oct | 1 | 178 | -33.58%
KONOCTI 1102 | 5 | 747.2
Aug | 2 | 230.5
Sep | 3 | 1091.6667 | 373.6%
LOS GATOS 1106 | 9 | 1428.8889
Aug | 5 | 1798.4
Sep | 2 | 1009.5 | -43.87%
Oct | 2 | 924.5 | -8.42%
LOS GATOS 1107 | 3 | 376
Sep | 1 | 235
Oct | 2 | 446.5 | 90%
LOS OSITOS 2103 | 7 | 478.4286
Aug | 3 | 586
Oct | 3 | 496.6667 | -15.24%
Nov | 1 | 101 | -79.66%
LOW GAP 1101 | 3 | 247.3333
Aug | 1 | 292
Sep | 2 | 225 | -22.95%
MARIPOSA 2101 | 8 | 387.625
Aug | 3 | 453
Sep | 1 | 373 | -17.66%
Oct | 4 | 342.25 | -8.244%
MARIPOSA 2102 | 3 | 617
Aug | 2 | 767
Sep | 1 | 317 | -58.67%
MENDOCINO 1101 | 4 | 342
Sep | 2 | 320
Oct | 2 | 364 | 13.75%
MENLO 1102 | 3 | 977.6667
Sep | 1 | 1159
Oct | 2 | 887 | -23.47%
MENLO 1103 | 3 | 596.3333
Sep | 2 | 802
Oct | 1 | 185 | -76.93%
MIDDLETOWN 1101 | 2 | 748.5
Sep | 2 | 748.5
MIWUK 1702 | 5 | 367.4
Aug | 2 | 637
Sep | 1 | 135 | -78.81%
Oct | 2 | 214 | 58.52%
MOLINO 1102 | 4 | 916.25
Aug | 2 | 917.5
Sep | 2 | 915 | -0.2725%
MONTE RIO 1111 | 2 | 381.5
Aug | 1 | 695
Sep | 1 | 68 | -90.22%
MORGAN HILL 2105 | 6 | 863.5
Aug | 3 | 583
Sep | 1 | 1211 | 107.7%
Oct | 2 | 1110.5 | -8.299%
NARROWS 2102 | 3 | 1317.6667
Aug | 1 | 403
Sep | 1 | 1342 | 233%
Oct | 1 | 2208 | 64.53%
NARROWS 2105 | 6 | 580
Jul | 1 | 381
Aug | 1 | 524 | 37.53%
Oct | 4 | 643.75 | 22.85%
OAKHURST 1101 | 3 | 478.6667
Aug | 2 | 535.5
Sep | 1 | 365 | -31.84%
OLETA 1102 | 4 | 283
Aug | 1 | 386
Oct | 3 | 248.6667 | -35.58%
ORO FINO 1102 | 12 | 688
Aug | 2 | 625.5
Sep | 7 | 635.7143 | 1.633%
Oct | 3 | 851.6667 | 33.97%
OTTER 1101 | 2 | 388.5
Sep | 2 | 388.5
PANOCHE 1103 | 9 | 425.3333
Aug | 1 | 989
Sep | 2 | 684 | -30.84%
Oct | 6 | 245.1667 | -64.16%
PAUL SWEET 2106 | 7 | 551.8571
Aug | 1 | 289
Sep | 1 | 918 | 217.6%
Oct | 5 | 531.2 | -42.14%
PEORIA 1701 | 5 | 224.4
Aug | 3 | 280.3333
Oct | 2 | 140.5 | -49.88%
PERRY 1101 | 7 | 387.2857
Aug | 1 | 1711
Sep | 2 | 194.5 | -88.63%
Oct | 3 | 195 | 0.2571%
Nov | 1 | 26 | -86.67%
PLACERVILLE 2106 | 14 | 558.4286
Aug | 7 | 551.7143
Sep | 4 | 539.25 | -2.259%
Oct | 3 | 599.6667 | 11.2%
PUEBLO 2103 | 8 | 854.875
Jul | 1 | 947
Aug | 1 | 1062 | 12.14%
Sep | 4 | 402.5 | -62.1%
Oct | 2 | 1610 | 300%
PUTAH CREEK 1102 | 5 | 458.6
Aug | 3 | 353
Sep | 2 | 617 | 74.79%
RED BLUFF 1103 | 2 | 470.5
Sep | 2 | 470.5
ROB ROY 2104 | 10 | 585.3
Jul | 1 | 615
Aug | 4 | 581 | -5.528%
Sep | 3 | 428 | -26.33%
Oct | 2 | 815 | 90.42%
SALT SPRINGS 2102 | 5 | 332.8
Sep | 3 | 197
Oct | 2 | 536.5 | 172.3%
SAN JUSTO 1101 | 4 | 441.75
Jul | 1 | 291
Aug | 1 | 147 | -49.48%
Sep | 1 | 284 | 93.2%
Oct | 1 | 1045 | 268%
SAN LUIS OBISPO 1104 | 2 | 297.5
Aug | 1 | 371
Oct | 1 | 224 | -39.62%
SAN RAFAEL 1108 | 5 | 440.8
Aug | 4 | 504
Oct | 1 | 188 | -62.7%
SAN RAMON 2108 | 3 | 675.3333
Sep | 2 | 836.5
Oct | 1 | 353 | -57.8%
SAND CREEK 1103 | 4 | 744.25
Aug | 1 | 923
Sep | 1 | 540 | -41.5%
Oct | 2 | 757 | 40.19%
SANTA YNEZ 1101 | 2 | 1024.5
Jul | 1 | 891
Sep | 1 | 1158 | 29.97%
SANTA YNEZ 1104 | 4 | 872.75
Aug | 2 | 946.5
Sep | 1 | 467 | -50.66%
Oct | 1 | 1131 | 142.2%
SARATOGA 1107 | 3 | 674
Aug | 2 | 931.5
Oct | 1 | 159 | -82.93%
SHADY GLEN 1101 | 7 | 655.8571
Aug | 2 | 1620
Sep | 3 | 276.3333 | -82.94%
Oct | 2 | 261 | -5.549%
SHINGLE SPRINGS 2110 | 8 | 413.5
Aug | 3 | 338.6667
Sep | 4 | 460.75 | 36.05%
Oct | 1 | 449 | -2.55%
SILVERADO 2102 | 5 | 623
Aug | 2 | 637
Sep | 1 | 147 | -76.92%
Oct | 2 | 847 | 476.2%
SILVERADO 2104 | 11 | 706
Jul | 1 | 1184
Aug | 5 | 849.8 | -28.23%
Sep | 3 | 618 | -27.28%
Oct | 2 | 239.5 | -61.25%
SISQUOC 1102 | 5 | 861.2
Aug | 2 | 910
Sep | 2 | 824.5 | -9.396%
Oct | 1 | 837 | 1.516%
SISQUOC 1103 | 3 | 76.3333
Oct | 1 | 174
Nov | 2 | 27.5 | -84.2%
SPRING GAP 1702 | 2 | 204.5
Aug | 1 | 53
Sep | 1 | 356 | 571.7%
STANISLAUS 1702 | 4 | 658.5
Jul | 1 | 1024
Aug | 2 | 388.5 | -62.06%
Oct | 1 | 833 | 114.4%
SWIFT 2110 | 2 | 494
Oct | 2 | 494
TEJON 1102 | 2 | 437
Aug | 1 | 692
Sep | 1 | 182 | -73.7%
TEMPLETON 2110 | 4 | 924.25
Aug | 1 | 1237
Sep | 1 | 1718 | 38.88%
Oct | 1 | 46 | -97.32%
Nov | 1 | 696 | 1413%
TEMPLETON 2113 | 15 | 470.7333
Aug | 4 | 289.25
Sep | 7 | 677.2857 | 134.2%
Oct | 2 | 519 | -23.37%
Nov | 2 | 62.5 | -87.96%
TIVY VALLEY 1107 | 6 | 690.6667
Jul | 1 | 726
Aug | 2 | 806 | 11.02%
Sep | 1 | 782 | -2.978%
Oct | 2 | 512 | -34.53%
VACA DIXON 1105 | 3 | 247.3333
Jul | 1 | 88
Oct | 2 | 327 | 271.6%
VACAVILLE 1108 | 2 | 295
Aug | 1 | 216
Sep | 1 | 374 | 73.15%
VOLTA 1101 | 3 | 625.3333
Aug | 1 | 1070
Oct | 2 | 403 | -62.34%
WEIMAR 1101 | 2 | 314
Aug | 2 | 314
WEST POINT 1101 | 3 | 550.6667
Aug | 1 | 782
Sep | 1 | 763 | -2.43%
Oct | 1 | 107 | -85.98%
WEST POINT 1102 | 11 | 483.0909
Aug | 3 | 692
Sep | 4 | 572.75 | -17.23%
Oct | 4 | 236.75 | -58.66%
WILLOW CREEK 1103 | 6 | 6501.5
Aug | 3 | 12277.3333
Sep | 3 | 725.6667 | -94.09%
WOODACRE 1101 | 4 | 509.5
Sep | 3 | 330.3333
Oct | 1 | 1047 | 217%
WOODSIDE 1101 | 2 | 300
Aug | 2 | 300
WOODSIDE 1104 | 4 | 484.25
Aug | 2 | 666.5
Sep | 2 | 302 | -54.69%
LLAGAS 2101 | 5 | 1280.6
Aug | 1 | 1858
Sep | 2 | 1144 | -38.43%
Oct | 2 | 1128.5 | -1.355%
Grand Total | 561 | 688.4875