## Dictionary
Column | Description
Outages | Unique event identification number
County | County
Circuit | Overhead Distribution Circuit Name
CPZ | Circuit Protection Zone
Cause | Outage Suspected Initiating Cause
3rd | Third Party
AN | Animal
CI | Company Initiated
EF | Equipment Failure
ENV | Environmental
UNK | Unknown
VEG | Vegetation
FNL | "First No Light"; Outage Start Day & Time
Week | Reporting Week by FNL
End_Date | Outage End Day & Time
CAIDI | Customer Average Interruption Duration Index, in minutes
EPSS_Outage_Type | FTS, HLT or T-EPSS
FTS | "Fast Trip Setting"; Post-Optimized Circuit Settings
HLT | "Hot Line Tag"; Pre-Optimized Circuit Settings
T-EPSS | "Transmission"-EPSS; EPSS outages on transmission lines
C/OUT | “Reclosing Cut Out (Reclose Blocking Enabled)”; device will not reclose when fault occurs
CESO | Count of Customers Experiencing Sustained Outages
Medical_Baseline | Count of Medical Baseline customer service points
Life_Support | Count of Life Support customer service points
Critical_Customer | Count of Critical Customer service points
Schools | Count of School customer service points
Hospitals | Count of Hospital customer service points
Well_Water_Dependent | Count of Well Water Depended customer service points
Customer_Minutes | Sum of total outage customer minutes
Restoration_Time_Minutes | Amount of time between the FNL and End Date, in minutes

## Summary
2023 YTD Summary
Category | Count
Medical Baseline | 129825
Life Support | 92674
Critical Customers | 33456
Hospitals | 260
Schools | 4301
Overall CAIDI | 193.4772
Restored <60 Mins | 348
Total Outages | 2263
Total Customers Experiencing Outages | 1972285
Unique Customers Experiencing Outages | 726708
December 2023 Summary
Category | Count
Medical Baseline | 1591
Life Support | 1155
Critical Customers | 497
Hospitals | 2
Schools | 37
Overall CAIDI | 130.9932
Restored <60 Mins | 9
Total Outages | 46
Total Customers Experiencing Outages | 28993
Unique Customers Experiencing Outages | 24155

## YTD Outages 010123_123123
Outages | County | Circuit | CPZ | Cause | FNL | Week | End_Date | CAIDI | EPSS_Outage_Type | Customer_Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Well_Water_Dependent | Restoration_Time_Minutes
23-0004384 | Placer | HORSESHOE 1101 | HORSESHOE 11012714 | Vegetation | 2022-12-31 20:00 | 12/27 - 1/2 | 2023-01-01 13:40 | 1060 | FTS | 80560 | 76 | 5 | 3 | 2 | 0 | 0 | 0 | 1060
23-0017227 | Amador | TIGER CREEK 0201 | TIGER CREEK 0201CB | Equipment Failure/Involved | 2023-01-16 13:32 | 1/17 - 1/23 | 2023-01-18 11:41 | 2728.9286 | FTS | 38205 | 14 | 0 | 0 | 3 | 0 | 0 | 0 | 2769
23-0022726 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 11011664 | Unknown Cause | 2023-01-29 11:56 | 1/24 - 1/30 | 2023-01-29 18:05 | 367.4161 | FTS | 177462 | 483 | 27 | 20 | 11 | 1 | 0 | 1 | 369
23-0022739 | Shasta | PIT NO 5 1101 | PIT NO 5 110190846 | 3rd Party | 2023-01-29 15:09 | 1/24 - 1/30 | 2023-01-30 02:59 | 220.6889 | FTS | 29793 | 135 | 5 | 3 | 9 | 2 | 0 | 0 | 710
23-0022907 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101548 | Vegetation | 2023-01-30 10:29 | 1/24 - 1/30 | 2023-01-30 11:52 | 83 | FTS | 91798 | 1106 | 55 | 38 | 17 | 1 | 0 | 0 | 83
23-0027784 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | Unknown Cause | 2023-02-11 06:28 | 2/7 - 2/13 | 2023-02-11 07:25 | 57 | FTS | 5814 | 102 | 1 | 1 | 1 | 0 | 0 | 0 | 57
23-0027947 | Napa | CALISTOGA 1101 | CALISTOGA 11015934 | Unknown Cause | 2023-02-12 16:08 | 2/14 - 2/20 | 2023-02-13 12:03 | 1040.1715 | FTS | 394225 | 379 | 14 | 12 | 1 | 0 | 0 | 1 | 1195
23-0030310 | Kern | SAN BERNARD 1101 | SAN BERNARD 1101641042 | Equipment Failure/Involved | 2023-02-17 16:18 | 2/14 - 2/20 | 2023-02-17 17:43 | 85 | FTS | 1445 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 85
23-0033514 | Shasta | PIT NO 5 1101 | PIT NO 5 11011660 | Unknown Cause | 2023-02-24 00:08 | 2/21 - 2/27 | 2023-02-24 03:50 | 28.513 | FTS | 6558 | 230 | 4 | 3 | 9 | 2 | 0 | 0 | 222
23-0048455 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-03-19 08:46 | 3/14 - 3/20 | 2023-03-19 11:54 | 188 | FTS | 6204 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 188
23-0065531 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | 3rd Party | 2023-04-27 12:21 | 4/25 - 5/1 | 2023-04-27 15:20 | 160.3483 | FTS | 57084 | 356 | 30 | 22 | 15 | 0 | 0 | 1 | 179
23-0065880 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | Company Initiated | 2023-04-28 07:50 | 4/25 - 5/1 | 2023-04-28 11:40 | 225.6186 | FTS | 663093 | 2939 | 272 | 196 | 51 | 5 | 0 | 4 | 230
23-0066135 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Unknown Cause | 2023-04-28 15:17 | 4/25 - 5/1 | 2023-04-28 17:42 | 50.2073 | FTS | 65621 | 1307 | 127 | 90 | 20 | 2 | 0 | 2 | 145
23-0066227 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21069712 | Unknown Cause | 2023-04-29 05:46 | 4/25 - 5/1 | 2023-04-29 12:58 | 430.0479 | FTS | 1312076 | 3051 | 233 | 178 | 66 | 15 | 0 | 4 | 432
23-0066363 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | Company Initiated | 2023-04-29 23:47 | 4/25 - 5/1 | 2023-04-30 09:53 | 605.8333 | FTS | 1780544 | 2939 | 272 | 196 | 51 | 5 | 0 | 4 | 606
23-0066339 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | Unknown Cause | 2023-04-29 20:09 | 4/25 - 5/1 | 2023-04-30 10:42 | 185.6597 | FTS | 284245 | 1531 | 116 | 93 | 44 | 10 | 0 | 1 | 873
23-0069178 | Tehama | RAWSON SUB | N/A | Environmental/External | 2023-05-06 12:49 | 5/2 - 5/8 | 2023-05-06 13:03 | 14 | T-EPSS | 35336 | 2524 | 201 | 147 | 34 | 13 | 0 | 0 | 14
23-0069167 | Tehama | TYLER SUB | N/A | Environmental/External | 2023-05-06 12:49 | 5/2 - 5/8 | 2023-05-06 13:26 | 37 | T-EPSS | 136530 | 3690 | 329 | 232 | 66 | 7 | 4 | 1 | 37
23-0069532 | Tehama | TYLER SUB | N/A | Unknown Cause | 2023-05-08 11:56 | 5/2 - 5/8 | 2023-05-08 12:30 | 31.4839 | T-EPSS | 110414 | 3507 | 329 | 232 | 66 | 7 | 4 | 1 | 34
23-0070454 | Lake | MIDDLETOWN SUB | N/A | 3rd Party | 2023-05-10 12:13 | 5/9 - 5/15 | 2023-05-10 13:20 | 66.5471 | T-EPSS | 312239 | 4692 | 300 | 212 | 76 | 11 | 1 | 5 | 67
23-0071176 | Monterey | BORONDA SUB | N/A | Unknown Cause | 2023-05-12 03:09 | 5/9 - 5/15 | 2023-05-12 05:02 | 113 | T-EPSS | 101022 | 894 | 45 | 35 | 18 | 5 | 0 | 0 | 113
23-0071542 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | Vegetation | 2023-05-13 08:49 | 5/9 - 5/15 | 2023-05-13 12:02 | 96.2433 | FTS | 64483 | 670 | 51 | 34 | 3 | 0 | 0 | 5 | 193
23-0072098 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 11077380 | Company Initiated | 2023-05-15 21:07 | 5/16 - 5/22 | 2023-05-15 22:07 | 47.5632 | FTS | 57171 | 1202 | 103 | 63 | 18 | 0 | 0 | 1 | 60
23-0072164 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 110737522 | Unknown Cause | 2023-05-16 07:39 | 5/16 - 5/22 | 2023-05-16 12:10 | 261.4567 | FTS | 99615 | 381 | 26 | 15 | 5 | 0 | 0 | 0 | 271
23-0072232 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | Equipment Failure/Involved | 2023-05-16 09:48 | 5/16 - 5/22 | 2023-05-16 19:00 | 136.3099 | FTS | 48390 | 355 | 30 | 22 | 15 | 0 | 0 | 1 | 552
23-0072444 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Company Initiated | 2023-05-16 17:06 | 5/16 - 5/22 | 2023-05-17 08:18 | 269.3389 | FTS | 240789 | 894 | 62 | 42 | 16 | 0 | 0 | 0 | 912
23-0072482 | Fresno | KERCKHOFF 1101 | KERCKHOFF 1101R308 | Unknown Cause | 2023-05-16 20:11 | 5/16 - 5/22 | 2023-05-17 15:02 | 1129 | FTS | 33870 | 30 | 2 | 1 | 1 | 0 | 0 | 0 | 1131
23-0073057 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Company Initiated | 2023-05-18 09:59 | 5/16 - 5/22 | 2023-05-18 19:58 | 491.0827 | FTS | 2388135 | 4863 | 425 | 302 | 63 | 12 | 0 | 26 | 599
23-0073268 | Fresno | AUBERRY 1101 | AUBERRY 1101R314 | Unknown Cause | 2023-05-18 18:47 | 5/16 - 5/22 | 2023-05-19 09:43 | 350.6417 | FTS | 468808 | 1337 | 121 | 84 | 17 | 4 | 0 | 6 | 896
23-0073390 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Company Initiated | 2023-05-19 07:57 | 5/16 - 5/22 | 2023-05-19 13:41 | 112.3401 | FTS | 450259 | 4008 | 122 | 80 | 32 | 0 | 0 | 13 | 344
23-0073670 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210623190 | Equipment Failure/Involved | 2023-05-19 14:37 | 5/16 - 5/22 | 2023-05-19 17:52 | 117.7852 | FTS | 237455 | 2016 | 157 | 99 | 22 | 3 | 1 | 4 | 195
23-0073584 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | Unknown Cause | 2023-05-19 12:31 | 5/16 - 5/22 | 2023-05-19 18:05 | 334 | FTS | 17034 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 334
23-0073766 | Placer | WEIMAR 1101 | WEIMAR 11012058 | Unknown Cause | 2023-05-19 23:32 | 5/16 - 5/22 | 2023-05-20 09:20 | 251.299 | FTS | 148769 | 592 | 39 | 28 | 9 | 0 | 0 | 3 | 588
23-0073788 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown Cause | 2023-05-20 06:34 | 5/16 - 5/22 | 2023-05-20 10:59 | 265 | FTS | 14575 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 265
23-0073932 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Equipment Failure/Involved | 2023-05-20 23:24 | 5/16 - 5/22 | 2023-05-21 10:01 | 637 | FTS | 188552 | 296 | 22 | 17 | 2 | 0 | 0 | 0 | 637
23-0073958 | Tuolumne | MIWUK 1702 | MIWUK 17029270 | Equipment Failure/Involved | 2023-05-21 08:50 | 5/16 - 5/22 | 2023-05-21 14:02 | 170.541 | FTS | 89534 | 525 | 51 | 34 | 5 | 0 | 0 | 0 | 312
23-0073959 | Placer | WEIMAR 1101 | WEIMAR 11012058 | Equipment Failure/Involved | 2023-05-21 09:41 | 5/16 - 5/22 | 2023-05-21 15:12 | 162.1351 | FTS | 95984 | 592 | 39 | 28 | 9 | 0 | 0 | 3 | 331
23-0073989 | Madera | COARSEGOLD 2103 | COARSEGOLD 21036110 | Unknown Cause | 2023-05-21 13:41 | 5/16 - 5/22 | 2023-05-21 17:21 | 188.9515 | FTS | 38924 | 206 | 11 | 7 | 33 | 4 | 0 | 0 | 220
23-0074002 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Company Initiated | 2023-05-21 17:52 | 5/16 - 5/22 | 2023-05-21 19:51 | 109.2908 | FTS | 513011 | 4694 | 293 | 219 | 72 | 8 | 0 | 2 | 119
23-0074493 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Company Initiated | 2023-05-23 07:23 | 5/23 - 5/29 | 2023-05-23 11:19 | 224.337 | FTS | 80537 | 359 | 16 | 15 | 5 | 0 | 0 | 0 | 236
23-0074745 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | Company Initiated | 2023-05-23 13:09 | 5/23 - 5/29 | 2023-05-23 20:42 | 453 | FTS | 126840 | 280 | 15 | 14 | 2 | 0 | 0 | 0 | 453
23-0074901 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | Company Initiated | 2023-05-23 21:58 | 5/23 - 5/29 | 2023-05-24 08:58 | 660 | FTS | 184800 | 280 | 15 | 14 | 2 | 0 | 0 | 0 | 660
23-0075399 | Fresno | KETTLEMAN HILLS 2104 | KETTLEMAN HILLS 2104358094 | Animal | 2023-05-25 07:57 | 5/23 - 5/29 | 2023-05-25 10:41 | 164 | FTS | 164 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 164
23-0075751 | Tehama | TYLER SUB | N/A | Environmental/External | 2023-05-25 20:50 | 5/23 - 5/29 | 2023-05-25 23:06 | 134.3986 | T-EPSS | 495931 | 3690 | 349 | 249 | 72 | 7 | 4 | 1 | 136
23-0075759 | Shasta | KESWICK 1101 | KESWICK 1101417066 | Unknown Cause | 2023-05-25 20:35 | 5/23 - 5/29 | 2023-05-26 09:39 | 784 | FTS | 13328 | 17 | 0 | 0 | 10 | 0 | 0 | 0 | 784
23-0076378 | Lassen | MC ARTHUR SUB | N/A | Environmental/External | 2023-05-27 22:29 | 5/23 - 5/29 | 2023-05-28 06:58 | 350.5484 | T-EPSS | 608552 | 1736 | 85 | 64 | 38 | 6 | 0 | 0 | 509
23-0076420 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 110541954 | Animal | 2023-05-28 08:43 | 5/23 - 5/29 | 2023-05-28 11:11 | 148 | FTS | 23828 | 161 | 7 | 6 | 6 | 4 | 0 | 0 | 148
23-0076259 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 1104CB | Equipment Failure/Involved | 2023-05-27 04:06 | 5/23 - 5/29 | 2023-05-28 18:58 | 339.4635 | FTS | 213862 | 630 | 11 | 9 | 10 | 2 | 0 | 4 | 2332
23-0076603 | Plumas | GRAYS FLAT SUB | N/A | Environmental/External | 2023-05-29 17:13 | 5/30 - 6/5 | 2023-05-29 21:55 | 125.6348 | T-EPSS | 229786 | 1829 | 77 | 60 | 57 | 97 | 2 | 3 | 282
23-0078471 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2023-06-02 20:05 | 5/30 - 6/5 | 2023-06-03 07:08 | 348.6176 | FTS | 23706 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 663
23-0078696 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210521160 | Equipment Failure/Involved | 2023-06-04 10:31 | 5/30 - 6/5 | 2023-06-04 14:03 | 212 | FTS | 48548 | 229 | 14 | 9 | 1 | 0 | 0 | 0 | 212
23-0078714 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | 3rd Party | 2023-06-04 13:04 | 5/30 - 6/5 | 2023-06-04 14:43 | 99 | FTS | 27720 | 280 | 15 | 14 | 2 | 0 | 0 | 0 | 99
23-0078676 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104828842 | Animal | 2023-06-04 06:50 | 5/30 - 6/5 | 2023-06-04 17:20 | 137.7945 | FTS | 219231 | 1591 | 166 | 127 | 20 | 1 | 0 | 0 | 630
23-0023481 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101502 | Unknown Cause | 2023-06-04 18:35 | 5/30 - 6/5 | 2023-06-04 22:24 | 165.198 | FTS | 145209 | 879 | 126 | 90 | 53 | 1 | 5 | 0 | 229
23-0078778 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | Unknown Cause | 2023-06-05 02:46 | 5/30 - 6/5 | 2023-06-05 03:38 | 52 | FTS | 18460 | 355 | 31 | 23 | 15 | 0 | 0 | 1 | 52
23-0078739 | Yolo | MADISON 2101 | MADISON 210189332 | Unknown Cause | 2023-06-04 17:50 | 5/30 - 6/5 | 2023-06-05 10:24 | 909.7726 | FTS | 644119 | 708 | 20 | 11 | 15 | 13 | 0 | 1 | 994
23-0078800 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Unknown Cause | 2023-06-05 07:27 | 5/30 - 6/5 | 2023-06-05 10:40 | 181.337 | FTS | 65100 | 359 | 16 | 15 | 5 | 0 | 0 | 0 | 193
23-0079045 | Tuolumne | TAR FLAT 0402 | TAR FLAT 04023144 | Unknown Cause | 2023-06-05 15:59 | 6/6 - 6/12 | 2023-06-05 17:19 | 80 | FTS | 20240 | 253 | 17 | 10 | 1 | 0 | 0 | 0 | 80
23-0079023 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | Environmental/External | 2023-06-05 14:53 | 6/6 - 6/12 | 2023-06-05 17:54 | 125.8623 | FTS | 129764 | 1031 | 71 | 57 | 42 | 10 | 0 | 1 | 181
23-0079101 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Unknown Cause | 2023-06-05 18:45 | 6/6 - 6/12 | 2023-06-05 22:08 | 203 | FTS | 302267 | 1489 | 176 | 133 | 39 | 2 | 0 | 0 | 203
23-0079127 | Shasta | OREGON TRAIL 1103 | OREGON TRAIL 110346860 | Environmental/External | 2023-06-05 19:44 | 6/6 - 6/12 | 2023-06-05 23:48 | 243.9844 | FTS | 155906 | 639 | 61 | 42 | 4 | 0 | 0 | 0 | 244
23-0079131 | Shasta | ANTLER 1101 | ANTLER 11011378 | Environmental/External | 2023-06-05 20:27 | 6/6 - 6/12 | 2023-06-06 00:57 | 270 | FTS | 20250 | 75 | 7 | 6 | 1 | 0 | 0 | 0 | 270
23-0079098 | Tuolumne | TAR FLAT 0402 | TAR FLAT 04023144 | Unknown Cause | 2023-06-05 18:22 | 6/6 - 6/12 | 2023-06-06 03:20 | 191.3755 | FTS | 48418 | 253 | 17 | 10 | 1 | 0 | 0 | 0 | 538
23-0079105 | Butte | PARADISE 1105 | PARADISE 1105878870 | Vegetation | 2023-06-05 19:26 | 6/6 - 6/12 | 2023-06-06 03:30 | 38.0877 | FTS | 47762 | 1254 | 128 | 98 | 19 | 1 | 0 | 0 | 484
23-0079149 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2023-06-05 22:07 | 6/6 - 6/12 | 2023-06-06 11:34 | 807 | FTS | 41157 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 807
23-0079129 | Kings | DEVILS DEN 1101 | DEVILS DEN 1101CB | Animal | 2023-06-05 20:35 | 6/6 - 6/12 | 2023-06-06 15:06 | 284.1194 | FTS | 19036 | 67 | 0 | 0 | 8 | 0 | 0 | 0 | 1111
23-0079424 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Animal | 2023-06-06 13:41 | 6/6 - 6/12 | 2023-06-06 16:58 | 179.42 | FTS | 80739 | 450 | 44 | 29 | 8 | 0 | 0 | 0 | 197
23-0079185 | Madera | SAN JOAQUIN #3 1103 | SAN JOAQUIN #3 1103CB | Environmental/External | 2023-06-06 05:10 | 6/6 - 6/12 | 2023-06-06 18:59 | 247.5127 | FTS | 340825 | 1377 | 108 | 82 | 30 | 7 | 0 | 1 | 829
23-0079104 | Shasta | VOLTA 1102 | VOLTA 11021646 | Equipment Failure/Involved | 2023-06-05 19:16 | 6/6 - 6/12 | 2023-06-07 09:47 | 927.2865 | FTS | 666719 | 719 | 70 | 51 | 7 | 3 | 0 | 0 | 2311
23-0079644 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103388671 | Unknown Cause | 2023-06-07 02:50 | 6/6 - 6/12 | 2023-06-07 11:12 | 502 | FTS | 502 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 502
23-0079939 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103388671 | 3rd Party | 2023-06-07 13:28 | 6/6 - 6/12 | 2023-06-07 16:34 | 186 | FTS | 186 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 186
23-0079609 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | Animal | 2023-06-06 22:10 | 6/6 - 6/12 | 2023-06-08 01:48 | 1658 | FTS | 82900 | 50 | 0 | 0 | 2 | 0 | 0 | 0 | 1658
23-0079588 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21013990 | Animal | 2023-06-06 21:22 | 6/6 - 6/12 | 2023-06-08 08:08 | 2086 | FTS | 31290 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 2086
23-0080448 | Yuba | SMARTVILLE SUB | N/A | Equipment Failure/Involved | 2023-06-08 14:19 | 6/6 - 6/12 | 2023-06-08 15:34 | 75 | T-EPSS | 42150 | 562 | 44 | 32 | 13 | 0 | 0 | 5 | 75
23-0081098 | Madera | COARSEGOLD 2103 | COARSEGOLD 21036110 | Unknown Cause | 2023-06-10 07:19 | 6/6 - 6/12 | 2023-06-10 08:03 | 43.6019 | FTS | 8982 | 206 | 11 | 7 | 33 | 4 | 0 | 0 | 44
23-0081325 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Unknown Cause | 2023-06-11 18:01 | 6/6 - 6/12 | 2023-06-11 19:41 | 99.5923 | FTS | 12947 | 130 | 4 | 4 | 4 | 0 | 0 | 0 | 100
23-0081348 | Tehama | TYLER / RAWSON SUB | N/A | Environmental/External | 2023-06-11 20:27 | 6/6 - 6/12 | 2023-06-11 22:27 | 85.6612 | T-EPSS | 532984 | 6222 | 543 | 387 | 106 | 20 | 4 | 1 | 120
23-0081702 | Butte | NOTRE DAME 1104 | NOTRE DAME 11042028 | Environmental/External | 2023-06-12 21:51 | 6/13 - 6/19 | 2023-06-13 14:43 | 736.8623 | FTS | 101687 | 138 | 9 | 5 | 2 | 1 | 0 | 2 | 1012
23-0082047 | Madera | AVENAL 2101 | AVENAL 21019070 | Animal | 2023-06-13 17:11 | 6/13 - 6/19 | 2023-06-13 21:03 | 232 | FTS | 15776 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 232
23-0082475 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 11077380 | Animal | 2023-06-14 18:15 | 6/13 - 6/19 | 2023-06-14 18:41 | 26 | FTS | 19474 | 749 | 50 | 32 | 15 | 0 | 0 | 1 | 26
23-0082486 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2023-06-14 18:17 | 6/13 - 6/19 | 2023-06-14 20:30 | 133 | FTS | 9044 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 133
23-0082556 | Tuolumne | TAR FLAT 0401 | TAR FLAT 0401922858 | 3rd Party | 2023-06-15 06:21 | 6/13 - 6/19 | 2023-06-15 12:08 | 85.0548 | FTS | 29514 | 347 | 28 | 23 | 2 | 0 | 0 | 0 | 347
23-0082792 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102556 | Unknown Cause | 2023-06-15 14:07 | 6/13 - 6/19 | 2023-06-15 15:58 | 63.3214 | FTS | 31914 | 504 | 53 | 32 | 5 | 0 | 0 | 1 | 111
23-0082829 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | 3rd Party | 2023-06-15 14:54 | 6/13 - 6/19 | 2023-06-15 16:48 | 114 | FTS | 106704 | 936 | 68 | 44 | 11 | 0 | 0 | 1 | 114
23-0082853 | Tehama | RED BLUFF 1104 | RED BLUFF 110451238 | Animal | 2023-06-15 15:32 | 6/13 - 6/19 | 2023-06-15 18:15 | 163 | FTS | 59006 | 362 | 35 | 20 | 10 | 0 | 0 | 1 | 163
23-0082936 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | 3rd Party | 2023-06-15 20:53 | 6/13 - 6/19 | 2023-06-16 01:49 | 213.3824 | FTS | 429112 | 2011 | 220 | 159 | 23 | 2 | 0 | 3 | 296
23-0083070 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Animal | 2023-06-16 08:57 | 6/13 - 6/19 | 2023-06-16 11:22 | 144.4978 | FTS | 65024 | 450 | 44 | 29 | 8 | 0 | 0 | 0 | 145
23-0083115 | Tehama | LOS MOLINOS 1101 | LOS MOLINOS 11011308 | Animal | 2023-06-16 10:18 | 6/13 - 6/19 | 2023-06-16 11:39 | 68.3419 | FTS | 15992 | 234 | 16 | 9 | 4 | 3 | 0 | 0 | 81
23-0083147 | Nevada | HIGGINS 1103 | HIGGINS 1103995672 | Unknown Cause | 2023-06-16 11:09 | 6/13 - 6/19 | 2023-06-16 12:34 | 85 | FTS | 18530 | 218 | 17 | 12 | 2 | 0 | 0 | 0 | 85
23-0083168 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Unknown Cause | 2023-06-16 11:37 | 6/13 - 6/19 | 2023-06-16 16:17 | 280 | FTS | 232680 | 831 | 81 | 60 | 14 | 1 | 0 | 24 | 280
23-0083196 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 1101CB | Equipment Failure/Involved | 2023-06-16 12:33 | 6/13 - 6/19 | 2023-06-16 20:03 | 441.5127 | FTS | 364248 | 825 | 33 | 25 | 17 | 3 | 0 | 0 | 450
23-0083294 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 21099372 | Company Initiated | 2023-06-16 18:34 | 6/13 - 6/19 | 2023-06-17 01:19 | 396.6719 | FTS | 841341 | 2121 | 178 | 125 | 23 | 2 | 0 | 33 | 405
23-0083300 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Unknown Cause | 2023-06-16 20:58 | 6/13 - 6/19 | 2023-06-17 01:22 | 242.8689 | FTS | 109291 | 450 | 44 | 29 | 8 | 0 | 0 | 0 | 264
23-0083322 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Animal | 2023-06-17 03:39 | 6/13 - 6/19 | 2023-06-17 05:52 | 133 | FTS | 246582 | 1854 | 125 | 94 | 26 | 6 | 0 | 2 | 133
23-0083337 | Humboldt | EEL RIVER 1102 | EEL RIVER 11021902 | Unknown Cause | 2023-06-17 08:10 | 6/13 - 6/19 | 2023-06-17 10:37 | 146.1792 | FTS | 15495 | 106 | 3 | 2 | 12 | 0 | 0 | 0 | 147
23-0083325 | Napa | MONTICELLO 1101 | MONTICELLO 1101630 | Unknown Cause | 2023-06-17 05:29 | 6/13 - 6/19 | 2023-06-17 11:21 | 246.2463 | FTS | 32997 | 134 | 11 | 7 | 7 | 0 | 0 | 0 | 352
23-0083392 | Humboldt | GARBERVILLE SUB | GARBERVILLE 11021510 | Vegetation | 2023-06-17 14:24 | 6/13 - 6/19 | 2023-06-17 16:29 | 67.7484 | FTS | 123302 | 1820 | 18 | 14 | 29 | 6 | 0 | 0 | 125
23-0083415 | Lake | HIGHLANDS 1102 | HIGHLANDS 110275140 | Animal | 2023-06-17 17:16 | 6/13 - 6/19 | 2023-06-17 18:17 | 61 | FTS | 158051 | 2591 | 296 | 205 | 29 | 9 | 0 | 0 | 61
23-0083411 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111919856 | Vegetation | 2023-06-17 16:57 | 6/13 - 6/19 | 2023-06-17 19:35 | 158 | FTS | 19592 | 124 | 6 | 4 | 1 | 0 | 0 | 0 | 158
23-0083396 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Unknown Cause | 2023-06-17 14:51 | 6/13 - 6/19 | 2023-06-17 20:28 | 245.5242 | FTS | 203294 | 828 | 80 | 59 | 14 | 1 | 0 | 24 | 337
23-0083380 | Napa | SILVERADO 2102 | SILVERADO 210258626 | Vegetation | 2023-06-17 13:08 | 6/13 - 6/19 | 2023-06-17 23:45 | 264.4 | FTS | 91218 | 345 | 4 | 3 | 5 | 0 | 0 | 2 | 637
23-0083365 | Placer | WEIMAR 1102 | WEIMAR 11022038 | Vegetation | 2023-06-17 10:42 | 6/13 - 6/19 | 2023-06-18 | 99.3862 | FTS | 282555 | 2843 | 230 | 169 | 37 | 12 | 0 | 8 | 798
23-0083468 | Contra Costa | CLAYTON 2212 | CLAYTON 221296224 | Vegetation | 2023-06-17 23:33 | 6/13 - 6/19 | 2023-06-18 00:33 | 60 | FTS | 15360 | 256 | 20 | 12 | 3 | 0 | 0 | 1 | 60
23-0083424 | Kern | CARNERAS 1103 | CARNERAS 1103430670 | Unknown Cause | 2023-06-17 18:33 | 6/13 - 6/19 | 2023-06-18 02:47 | 494 | FTS | 6916 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 494
23-0083480 | Yolo | PUTAH CREEK 1102 | PUTAH CREEK 1102202158 | Unknown Cause | 2023-06-18 06:15 | 6/13 - 6/19 | 2023-06-18 08:16 | 121 | FTS | 7623 | 63 | 4 | 3 | 0 | 0 | 0 | 2 | 121
23-0083481 | Calaveras | Valley Springs 1101 | Valley Springs 1101207256 | Animal | 2023-06-18 07:31 | 6/13 - 6/19 | 2023-06-18 10:22 | 99.5529 | FTS | 147637 | 1483 | 114 | 80 | 37 | 5 | 0 | 0 | 171
23-0083464 | Stanislaus | WESTLEY 1103 | WESTLEY 1103237522 | Unknown Cause | 2023-06-17 22:38 | 6/13 - 6/19 | 2023-06-18 10:42 | 724 | FTS | 28960 | 40 | 0 | 0 | 12 | 0 | 0 | 0 | 724
23-0083400 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 11032936 | Unknown Cause | 2023-06-17 15:13 | 6/13 - 6/19 | 2023-06-18 11:29 | 424.2734 | FTS | 412818 | 973 | 64 | 48 | 10 | 1 | 0 | 0 | 1216
23-0083485 | Yolo | MADISON 2101 | MADISON 210189332 | Animal | 2023-06-18 08:33 | 6/13 - 6/19 | 2023-06-18 13:03 | 129.1992 | FTS | 91473 | 708 | 20 | 11 | 15 | 13 | 0 | 1 | 270
23-0083419 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Unknown Cause | 2023-06-17 17:55 | 6/13 - 6/19 | 2023-06-18 14:09 | 1000.7474 | FTS | 2273698 | 2272 | 99 | 66 | 47 | 2 | 0 | 4 | 1214
23-0083522 | Napa | PUEBLO 2104 | PUEBLO 2102698 | 3rd Party | 2023-06-18 15:36 | 6/13 - 6/19 | 2023-06-18 18:43 | 187 | FTS | 347820 | 1860 | 45 | 29 | 20 | 2 | 0 | 3 | 187
23-0083518 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Vegetation | 2023-06-18 15:08 | 6/13 - 6/19 | 2023-06-18 18:51 | 221.8354 | FTS | 420600 | 1896 | 87 | 52 | 28 | 6 | 0 | 0 | 223
23-0083530 | Kern | MARICOPA 1102 | MARICOPA 11023558 | 3rd Party | 2023-06-18 17:26 | 6/13 - 6/19 | 2023-06-18 19:02 | 96 | FTS | 18432 | 192 | 20 | 15 | 3 | 0 | 0 | 0 | 96
23-0083523 | Solano | PEABODY 2113 | PEABODY 2113CB | 3rd Party | 2023-06-18 15:24 | 6/13 - 6/19 | 2023-06-18 19:15 | 201.809 | FTS | 1062726 | 5266 | 418 | 299 | 52 | 3 | 0 | 0 | 231
23-0083528 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105B534R | Equipment Failure/Involved | 2023-06-18 15:59 | 6/13 - 6/19 | 2023-06-18 21:34 | 75.4485 | FTS | 35159 | 466 | 28 | 18 | 14 | 0 | 0 | 0 | 335
23-0083585 | Monterey | KING CITY 1103 | KING CITY 11037038 | Animal | 2023-06-19 05:43 | 6/13 - 6/19 | 2023-06-19 07:22 | 57.6348 | FTS | 45762 | 794 | 53 | 40 | 15 | 0 | 0 | 0 | 99
23-0083539 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 110137454 | Unknown Cause | 2023-06-18 18:51 | 6/13 - 6/19 | 2023-06-19 09:24 | 429 | FTS | 102102 | 238 | 4 | 3 | 1 | 0 | 0 | 1 | 873
23-0083584 | Shasta | GIRVAN 1102 | GIRVAN 110280726 | Animal | 2023-06-19 04:58 | 6/13 - 6/19 | 2023-06-19 13:55 | 118 | FTS | 64664 | 548 | 30 | 24 | 8 | 0 | 0 | 1 | 537
23-0083545 | Sonoma | COTATI 1105 | COTATI 1105328 | Equipment Failure/Involved | 2023-06-18 19:06 | 6/13 - 6/19 | 2023-06-19 13:57 | 165.2387 | FTS | 164743 | 997 | 57 | 40 | 11 | 1 | 0 | 1 | 1131
23-0083588 | Tehama | RED BLUFF 1105 | RED BLUFF 110585632 | Animal | 2023-06-19 06:31 | 6/13 - 6/19 | 2023-06-19 14:10 | 139.3313 | FTS | 139192 | 999 | 109 | 76 | 20 | 1 | 0 | 7 | 459
23-0083653 | Amador | OLETA 1101 | OLETA 1101296804 | Animal | 2023-06-19 12:28 | 6/13 - 6/19 | 2023-06-19 14:57 | 111.1723 | FTS | 118732 | 1068 | 58 | 40 | 22 | 4 | 0 | 1 | 149
23-0083595 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651484 | Vegetation | 2023-06-19 05:59 | 6/13 - 6/19 | 2023-06-19 15:13 | 554 | FTS | 21606 | 39 | 3 | 3 | 0 | 0 | 0 | 0 | 554
23-0083686 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Unknown Cause | 2023-06-19 15:26 | 6/13 - 6/19 | 2023-06-19 16:13 | 47 | FTS | 106784 | 2272 | 99 | 66 | 47 | 2 | 0 | 4 | 47
23-0083690 | Fresno | REEDLEY 1112 | REEDLEY 11127240 | 3rd Party | 2023-06-19 15:59 | 6/13 - 6/19 | 2023-06-19 16:58 | 52.1148 | FTS | 15895 | 305 | 2 | 2 | 1 | 0 | 0 | 0 | 59
23-0083639 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Unknown Cause | 2023-06-19 10:57 | 6/20 - 6/26 | 2023-06-19 19:25 | 463.54 | FTS | 208593 | 450 | 44 | 29 | 8 | 0 | 0 | 0 | 508
23-0083651 | Nevada | BRUNSWICK 1104 | BRUNSWICK 11042112 | Unknown Cause | 2023-06-19 11:49 | 6/20 - 6/26 | 2023-06-19 19:55 | 358.4482 | FTS | 190336 | 531 | 30 | 15 | 4 | 1 | 0 | 15 | 486
23-0083647 | Sonoma | MIRABEL 1101 | MIRABEL 1101116 | Equipment Failure/Involved | 2023-06-19 11:27 | 6/20 - 6/26 | 2023-06-20 01:45 | 107.9164 | FTS | 41332 | 383 | 17 | 14 | 2 | 0 | 0 | 0 | 858
23-0083657 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | 3rd Party | 2023-06-19 12:52 | 6/20 - 6/26 | 2023-06-20 02:05 | 166.1482 | FTS | 127768 | 769 | 58 | 46 | 17 | 0 | 0 | 3 | 793
23-0083772 | Madera | OAKHURST 1103 | OAKHURST 110311900 | Animal | 2023-06-20 07:53 | 6/20 - 6/26 | 2023-06-20 09:21 | 88 | FTS | 19448 | 221 | 9 | 4 | 4 | 1 | 0 | 0 | 88
23-0083789 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102Y18 | 3rd Party | 2023-06-20 08:10 | 6/20 - 6/26 | 2023-06-20 10:05 | 112.1229 | FTS | 60210 | 537 | 17 | 8 | 15 | 0 | 0 | 0 | 115
23-0083839 | Sonoma | DUNBAR 1102 | DUNBAR 1102694641 | Company Initiated | 2023-06-20 10:04 | 6/20 - 6/26 | 2023-06-20 11:10 | 28.0132 | FTS | 17004 | 607 | 38 | 28 | 12 | 0 | 0 | 6 | 66
23-0083717 | Yolo | MADISON 2101 | MADISON 210189332 | Animal | 2023-06-19 18:55 | 6/20 - 6/26 | 2023-06-20 11:41 | 942.4336 | FTS | 667243 | 708 | 20 | 11 | 15 | 13 | 0 | 1 | 1006
23-0083842 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Animal | 2023-06-20 09:59 | 6/20 - 6/26 | 2023-06-20 12:52 | 119.9474 | FTS | 2279 | 19 | 2 | 1 | 0 | 0 | 0 | 0 | 173
23-0083931 | Nevada | NARROWS 2105 | NARROWS 21052228 | Company Initiated | 2023-06-20 13:45 | 6/20 - 6/26 | 2023-06-20 14:14 | 29 | FTS | 6612 | 228 | 11 | 7 | 5 | 0 | 0 | 2 | 29
23-0084034 | Fresno | GATES 1106 | GATES 110699914 | 3rd Party | 2023-06-20 19:32 | 6/20 - 6/26 | 2023-06-21 00:10 | 278 | FTS | 31136 | 112 | 0 | 0 | 5 | 0 | 0 | 0 | 278
23-0084045 | El Dorado | DIAMOND SPRINGS 1104 | DIAMOND SPRINGS 1104CB | Animal | 2023-06-20 21:47 | 6/20 - 6/26 | 2023-06-21 04:40 | 276.5138 | FTS | 280938 | 1016 | 93 | 59 | 20 | 7 | 0 | 0 | 413
23-0084077 | Butte | BANGOR 1101 | BANGOR 110131502 | Unknown Cause | 2023-06-21 01:40 | 6/20 - 6/26 | 2023-06-21 06:20 | 101.9138 | FTS | 133609 | 1311 | 135 | 90 | 6 | 0 | 0 | 9 | 280
23-0084103 | Placer | PENRYN 1103 | PENRYN 1103660 | Animal | 2023-06-21 06:33 | 6/20 - 6/26 | 2023-06-21 07:48 | 75 | FTS | 33975 | 453 | 32 | 18 | 2 | 0 | 0 | 4 | 75
23-0084093 | Kern | MARICOPA 1102 | MARICOPA 1102CB | 3rd Party | 2023-06-21 06:21 | 6/20 - 6/26 | 2023-06-21 09:18 | 165.0628 | FTS | 94581 | 573 | 39 | 27 | 18 | 2 | 0 | 0 | 177
23-0084170 | Placer | SHADY GLEN 1101 | SHADY GLEN 11012768 | Animal | 2023-06-21 08:28 | 6/20 - 6/26 | 2023-06-21 09:32 | 64 | FTS | 11392 | 178 | 12 | 11 | 6 | 4 | 0 | 1 | 64
23-0084128 | Nevada | BRUNSWICK 1103 | BRUNSWICK 11032784 | Animal | 2023-06-21 07:21 | 6/20 - 6/26 | 2023-06-21 12:50 | 81.5812 | FTS | 104424 | 1280 | 80 | 48 | 12 | 1 | 0 | 5 | 329
23-0084105 | Calaveras | CORRAL 1101 | CORRAL 110112606 | Animal | 2023-06-21 06:38 | 6/20 - 6/26 | 2023-06-21 14:45 | 198.8679 | FTS | 66223 | 333 | 25 | 17 | 7 | 0 | 0 | 0 | 487
23-0084439 | El Dorado | CLARKSVILLE 2106 | CLARKSVILLE 210619642 | Animal | 2023-06-21 18:20 | 6/20 - 6/26 | 2023-06-21 20:06 | 106 | FTS | 89782 | 847 | 65 | 41 | 20 | 1 | 0 | 0 | 106
23-0084423 | Kings | AVENAL 2101 | AVENAL 21019070 | Unknown Cause | 2023-06-21 16:49 | 6/20 - 6/26 | 2023-06-21 20:46 | 237 | FTS | 16116 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 237
23-0084419 | Fresno | REEDLEY 1112 | REEDLEY 11127240 | 3rd Party | 2023-06-21 16:32 | 6/20 - 6/26 | 2023-06-22 01:24 | 223.6033 | FTS | 68199 | 305 | 2 | 2 | 1 | 0 | 0 | 0 | 532
23-0084500 | Sonoma | MONTE RIO 1113 | MONTE RIO 11133970 | Unknown Cause | 2023-06-22 00:23 | 6/20 - 6/26 | 2023-06-22 07:24 | 331.1641 | FTS | 851754 | 2572 | 153 | 98 | 45 | 6 | 0 | 0 | 421
23-0084553 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 110541954 | 3rd Party | 2023-06-22 07:48 | 6/20 - 6/26 | 2023-06-22 09:30 | 102 | FTS | 16422 | 161 | 7 | 6 | 6 | 4 | 0 | 0 | 102
23-0084507 | Tuolumne | CURTIS 1703 | CURTIS 17039330 | Unknown Cause | 2023-06-22 01:52 | 6/20 - 6/26 | 2023-06-22 09:42 | 470 | FTS | 286230 | 609 | 39 | 32 | 17 | 0 | 0 | 0 | 470
23-0084593 | Amador | ELECTRA 1102 | CALAVERAS CEMENT 11012646 | Animal | 2023-06-22 09:23 | 6/20 - 6/26 | 2023-06-22 10:58 | 90.072 | FTS | 72598 | 806 | 57 | 40 | 18 | 1 | 0 | 0 | 95
23-0084511 | Tehama | CORNING 1102 | CORNING 11021900 | Animal | 2023-06-22 04:23 | 6/20 - 6/26 | 2023-06-22 11:54 | 220.2539 | FTS | 84137 | 382 | 26 | 21 | 11 | 3 | 0 | 1 | 451
23-0084794 | Santa Barbara | ZACA 1102 | ZACA 1102Y48 | Equipment Failure/Involved | 2023-06-22 15:02 | 6/20 - 6/26 | 2023-06-22 15:11 | 9 | FTS | 7434 | 826 | 25 | 11 | 16 | 15 | 0 | 2 | 9
23-0084930 | Placer | LINCOLN 1104 | LINCOLN 11042070 | Animal | 2023-06-23 07:32 | 6/20 - 6/26 | 2023-06-23 08:57 | 85 | FTS | 29325 | 345 | 27 | 20 | 2 | 0 | 0 | 5 | 85
23-0084929 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21033010 | Unknown Cause | 2023-06-23 07:27 | 6/20 - 6/26 | 2023-06-23 12:20 | 293 | FTS | 125404 | 428 | 9 | 5 | 4 | 0 | 0 | 0 | 293
23-0085040 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210912392 | Animal | 2023-06-23 10:56 | 6/20 - 6/26 | 2023-06-23 12:51 | 115 | HLT | 100050 | 870 | 85 | 58 | 21 | 3 | 0 | 6 | 115
23-0085131 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101644756 | Company Initiated | 2023-06-23 13:37 | 6/20 - 6/26 | 2023-06-23 14:14 | 37 | FTS | 1369 | 37 | 0 | 0 | 1 | 0 | 0 | 0 | 37
23-0085051 | Butte | WYANDOTTE 1107 | WYANDOTTE 11071026 | Unknown Cause | 2023-06-23 11:15 | 6/20 - 6/26 | 2023-06-23 15:47 | 272 | FTS | 78880 | 290 | 27 | 23 | 3 | 0 | 0 | 2 | 272
23-0085064 | Nevada | ALLEGHANY 1102 | ALLEGHANY 1102CB | Unknown Cause | 2023-06-23 11:05 | 6/20 - 6/26 | 2023-06-23 16:04 | 299 | HLT | 49036 | 164 | 4 | 4 | 4 | 1 | 0 | 0 | 299
23-0085208 | Madera | COARSEGOLD 2103 | COARSEGOLD 21035020 | Unknown Cause | 2023-06-23 16:12 | 6/20 - 6/26 | 2023-06-24 09:19 | 217.6368 | FTS | 260076 | 1195 | 138 | 96 | 56 | 6 | 0 | 0 | 1027
23-0085277 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 11011302 | 3rd Party | 2023-06-24 02:30 | 6/20 - 6/26 | 2023-06-24 10:26 | 150.8406 | FTS | 79493 | 527 | 39 | 25 | 8 | 0 | 1 | 0 | 476
23-0085315 | Mendocino | PHILO SUB | N/A | Equipment Failure/Involved | 2023-06-24 10:23 | 6/20 - 6/26 | 2023-06-24 11:18 | 51.3425 | T-EPSS | 114083 | 2222 | 58 | 40 | 50 | 13 | 0 | 2 | 55
23-0085316 | Mendocino | GUALALA SUB | N/A | Equipment Failure/Involved | 2023-06-24 10:23 | 6/20 - 6/26 | 2023-06-24 11:59 | 96 | T-EPSS | 364224 | 3794 | 139 | 107 | 55 | 0 | 0 | 0 | 96
23-0085314 | Sonoma | ANNAPOLIS SUB | N/A | Equipment Failure/Involved | 2023-06-24 10:23 | 6/20 - 6/26 | 2023-06-24 11:59 | 96 | T-EPSS | 21984 | 229 | 8 | 6 | 14 | 6 | 0 | 2 | 96
23-0085313 | Mendocino | POINT ARENA SUB | N/A | Equipment Failure/Involved | 2023-06-24 10:23 | 6/20 - 6/26 | 2023-06-24 11:59 | 96 | T-EPSS | 87552 | 912 | 42 | 28 | 32 | 9 | 0 | 1 | 96
23-0085317 | Mendocino | GARCIA SUB | N/A | Equipment Failure/Involved | 2023-06-24 10:23 | 6/20 - 6/26 | 2023-06-24 11:59 | 96 | T-EPSS | 864 | 9 | 0 | 0 | 2 | 0 | 0 | 0 | 96
23-0085299 | Santa Cruz | LOS GATOS 1107 | LOS GATOS 110760114 | Unknown Cause | 2023-06-24 08:09 | 6/20 - 6/26 | 2023-06-24 15:11 | 320.7089 | FTS | 93647 | 292 | 19 | 13 | 16 | 0 | 0 | 4 | 422
23-0085330 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Animal | 2023-06-24 12:00 | 6/20 - 6/26 | 2023-06-24 15:15 | 195 | FTS | 25545 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 195
23-0085351 | Contra Costa | TIDEWATER 2106 | TIDEWATER 210695842 | 3rd Party | 2023-06-24 15:22 | 6/20 - 6/26 | 2023-06-24 16:18 | 56 | FTS | 32144 | 574 | 40 | 33 | 14 | 1 | 0 | 0 | 56
23-0085302 | San Joaquin | CORRAL 1101 | CORRAL 110175204 | Equipment Failure/Involved | 2023-06-24 08:28 | 6/20 - 6/26 | 2023-06-24 16:25 | 139.9945 | FTS | 25479 | 182 | 3 | 2 | 4 | 0 | 0 | 0 | 477
23-0073777 | Tuolumne | STANISLAUS 1701 | STANISLAUS 1701CB | Equipment Failure/Involved | 2023-06-24 00:27 | 6/20 - 6/26 | 2023-06-24 21:22 | 391.5447 | FTS | 700865 | 1790 | 62 | 41 | 16 | 0 | 0 | 0 | 1255
23-0085377 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021888 | Unknown Cause | 2023-06-24 18:58 | 6/20 - 6/26 | 2023-06-25 09:13 | 588.909 | FTS | 867463 | 1473 | 68 | 54 | 16 | 0 | 0 | 0 | 855
23-0085356 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | Unknown Cause | 2023-06-24 15:54 | 6/20 - 6/26 | 2023-06-25 10:42 | 639.5207 | FTS | 324237 | 507 | 34 | 21 | 14 | 4 | 0 | 7 | 1128
23-0085331 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | Unknown Cause | 2023-06-24 12:12 | 6/20 - 6/26 | 2023-06-25 20:20 | 1439.4403 | FTS | 1830968 | 1272 | 78 | 58 | 12 | 1 | 0 | 0 | 1928
23-0085442 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237288 | Equipment Failure/Involved | 2023-06-25 17:42 | 6/20 - 6/26 | 2023-06-25 20:30 | 168 | FTS | 117768 | 701 | 55 | 43 | 15 | 5 | 0 | 1 | 168
23-0085447 | Placer | LINCOLN 1101 | LINCOLN 110195756 | Unknown Cause | 2023-06-25 20:04 | 6/20 - 6/26 | 2023-06-25 22:29 | 107.4222 | FTS | 29004 | 270 | 28 | 22 | 0 | 0 | 0 | 6 | 145
23-0085483 | Butte | WYANDOTTE 1103 | WYANDOTTE 11031504 | Animal | 2023-06-26 06:47 | 6/20 - 6/26 | 2023-06-26 12:52 | 198.2215 | FTS | 295350 | 1490 | 131 | 104 | 22 | 0 | 0 | 2 | 365
23-0085703 | Santa Barbara | ZACA 1102 | ZACA 1102Y48 | Equipment Failure/Involved | 2023-06-26 13:48 | 6/20 - 6/26 | 2023-06-26 14:04 | 16 | FTS | 13216 | 826 | 25 | 11 | 16 | 15 | 0 | 2 | 16
23-0085681 | Shasta | GIRVAN 1101 | GIRVAN 1101409530 | Company Initiated | 2023-06-26 13:09 | 6/20 - 6/26 | 2023-06-26 14:33 | 84 | FTS | 53172 | 633 | 41 | 27 | 17 | 2 | 0 | 0 | 84
23-0085692 | Napa | SILVERADO 2105 | SILVERADO 2105658898 | 3rd Party | 2023-06-26 13:19 | 6/20 - 6/26 | 2023-06-26 16:14 | 175 | FTS | 22750 | 130 | 2 | 1 | 2 | 0 | 0 | 0 | 175
23-0085791 | Santa Barbara | ZACA 1102 | ZACA 1102Y48 | Equipment Failure/Involved | 2023-06-26 16:31 | 6/20 - 6/26 | 2023-06-26 16:42 | 11 | FTS | 9086 | 826 | 25 | 11 | 16 | 15 | 0 | 2 | 11
23-0085678 | Shasta | GIRVAN 1101 | GIRVAN 11019732 | Unknown Cause | 2023-06-26 13:08 | 6/27 - 7/3 | 2023-06-26 17:07 | 239 | FTS | 117827 | 493 | 52 | 39 | 12 | 4 | 0 | 0 | 239
23-0085581 | Merced | SANTA NELLA 1101 | SANTA NELLA 11037200 | Animal | 2023-06-26 10:58 | 6/27 - 7/3 | 2023-06-26 17:43 | 305.7207 | FTS | 33935 | 111 | 1 | 1 | 9 | 0 | 0 | 0 | 405
23-0085522 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015144 | Vegetation | 2023-06-26 08:53 | 6/27 - 7/3 | 2023-06-27 02:30 | 182.0947 | FTS | 48073 | 264 | 19 | 16 | 8 | 1 | 0 | 0 | 1057
23-0085869 | Mendocino | COVELO 1101 | COVELO 1101562360 | Unknown Cause | 2023-06-27 01:35 | 6/27 - 7/3 | 2023-06-27 04:16 | 161 | FTS | 83237 | 517 | 23 | 18 | 2 | 3 | 0 | 0 | 161
23-0085943 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | Company Initiated | 2023-06-27 08:22 | 6/27 - 7/3 | 2023-06-27 08:55 | 33 | FTS | 61578 | 1866 | 206 | 150 | 19 | 2 | 0 | 3 | 33
23-0085844 | Shasta | ANTLER 1101 | ANTLER 11011378 | Environmental/External | 2023-06-26 20:57 | 6/27 - 7/3 | 2023-06-27 12:14 | 342.212 | FTS | 130725 | 382 | 30 | 20 | 8 | 1 | 0 | 0 | 917
23-0085861 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 1101451856 | Equipment Failure/Involved | 2023-06-26 22:20 | 6/27 - 7/3 | 2023-06-27 12:50 | 663.3333 | FTS | 1990 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 870
23-0086034 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Company Initiated | 2023-06-27 10:33 | 6/27 - 7/3 | 2023-06-27 13:25 | 164.7252 | FTS | 21579 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 172
23-0085860 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 1101CB | Equipment Failure/Involved | 2023-06-26 22:07 | 6/27 - 7/3 | 2023-06-27 13:43 | 226.3116 | FTS | 45036 | 199 | 21 | 15 | 2 | 0 | 0 | 0 | 936
23-0002206 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106CB | Equipment Failure/Involved | 2023-06-27 07:36 | 6/27 - 7/3 | 2023-06-27 16:54 | 121.9808 | FTS | 719565 | 5899 | 439 | 299 | 66 | 11 | 1 | 14 | 558
23-0086267 | Alameda | CAYETANO 2109 | CAYETANO 2109MR186 | Unknown Cause | 2023-06-27 16:18 | 6/27 - 7/3 | 2023-06-27 18:07 | 109 | FTS | 1308 | 12 | 1 | 0 | 0 | 0 | 0 | 0 | 109
23-0086121 | Santa Clara | SWIFT 2110 | SWIFT 2110XR332 | 3rd Party | 2023-06-27 12:44 | 6/27 - 7/3 | 2023-06-27 19:04 | 379.4783 | FTS | 34912 | 92 | 5 | 3 | 6 | 0 | 0 | 0 | 380
23-0085873 | Shasta | WHITMORE 1101 | WHITMORE 1101589578 | Environmental/External | 2023-06-26 22:24 | 6/27 - 7/3 | 2023-06-27 22:38 | 1109.5847 | FTS | 130931 | 118 | 9 | 9 | 2 | 0 | 0 | 0 | 1454
23-0086353 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Unknown Cause | 2023-06-28 00:22 | 6/27 - 7/3 | 2023-06-28 08:51 | 192.9616 | FTS | 140669 | 729 | 19 | 12 | 14 | 1 | 0 | 0 | 509
23-0086413 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 1104Y04 | Company Initiated | 2023-06-28 08:04 | 6/27 - 7/3 | 2023-06-28 09:35 | 91 | FTS | 40677 | 447 | 8 | 3 | 7 | 2 | 0 | 0 | 91
23-0086358 | Amador | CLAY 1103 | CLAY 11037142 | Unknown Cause | 2023-06-28 03:32 | 6/27 - 7/3 | 2023-06-28 10:29 | 417 | FTS | 33777 | 81 | 0 | 0 | 5 | 0 | 0 | 0 | 417
23-0086532 | Mendocino | UKIAH 1114 | UKIAH 1114822 | Company Initiated | 2023-06-28 10:46 | 6/27 - 7/3 | 2023-06-28 10:56 | 10 | FTS | 6800 | 680 | 39 | 23 | 10 | 1 | 0 | 0 | 10
23-0086486 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Unknown Cause | 2023-06-28 09:41 | 6/27 - 7/3 | 2023-06-28 11:49 | 127.5878 | FTS | 16714 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 128
23-0086429 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101406798 | Equipment Failure/Involved | 2023-06-28 08:32 | 6/27 - 7/3 | 2023-06-28 12:03 | 126.2537 | HLT | 8459 | 67 | 4 | 4 | 3 | 0 | 0 | 0 | 211
23-0086407 | Napa | SILVERADO 2102 | SILVERADO 210234959 | Unknown Cause | 2023-06-28 07:49 | 6/27 - 7/3 | 2023-06-28 12:09 | 260 | FTS | 55900 | 215 | 2 | 2 | 4 | 0 | 0 | 1 | 260
23-0086545 | Calaveras | FROGTOWN 1702 | FROGTOWN 17027134 | 3rd Party | 2023-06-28 10:36 | 6/27 - 7/3 | 2023-06-28 12:16 | 100 | FTS | 15900 | 159 | 4 | 3 | 1 | 0 | 0 | 0 | 100
23-0086458 | Shasta | GIRVAN 1101 | GIRVAN 11011636 | Company Initiated | 2023-06-28 09:02 | 6/27 - 7/3 | 2023-06-28 14:21 | 277.1542 | FTS | 300158 | 1083 | 88 | 61 | 29 | 6 | 0 | 0 | 319
23-0086489 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113CB | Equipment Failure/Involved | 2023-06-28 09:40 | 6/27 - 7/3 | 2023-06-28 15:21 | 174.4522 | FTS | 1267570 | 7266 | 360 | 252 | 104 | 20 | 2 | 20 | 341
23-0086801 | Mendocino | WILLITS 1103 | WILLITS 1103409216 | Unknown Cause | 2023-06-28 15:07 | 6/27 - 7/3 | 2023-06-28 19:17 | 250 | FTS | 63250 | 253 | 17 | 9 | 8 | 0 | 0 | 0 | 250
23-0086893 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110560528 | Unknown Cause | 2023-06-28 22:04 | 6/27 - 7/3 | 2023-06-28 22:52 | 44.5003 | FTS | 84239 | 1893 | 106 | 72 | 28 | 2 | 0 | 2 | 48
23-0086900 | Lake | KONOCTI 1108 | KONOCTI 11081278 | Unknown Cause | 2023-06-28 23:51 | 6/27 - 7/3 | 2023-06-29 03:30 | 217.0045 | FTS | 97001 | 447 | 42 | 32 | 7 | 0 | 0 | 2 | 219
23-0086908 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 211051790 | Unknown Cause | 2023-06-29 04:51 | 6/27 - 7/3 | 2023-06-29 08:56 | 245 | FTS | 49000 | 200 | 14 | 11 | 6 | 0 | 0 | 0 | 245
23-0086928 | Lake | KONOCTI 1102 | KONOCTI 1102354890 | Unknown Cause | 2023-06-29 07:00 | 6/27 - 7/3 | 2023-06-29 09:55 | 175 | FTS | 117425 | 671 | 52 | 34 | 18 | 17 | 0 | 0 | 175
23-0086759 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Animal | 2023-06-28 15:03 | 6/27 - 7/3 | 2023-06-29 15:54 | 1250.6923 | FTS | 32518 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 1491
23-0087276 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 21012056 | Company Initiated | 2023-06-29 14:59 | 6/27 - 7/3 | 2023-06-29 16:01 | 62 | FTS | 48794 | 787 | 34 | 25 | 9 | 0 | 3 | 0 | 62
23-0087317 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Unknown Cause | 2023-06-29 16:18 | 6/27 - 7/3 | 2023-06-29 18:39 | 130.8941 | FTS | 182990 | 1398 | 34 | 24 | 16 | 3 | 0 | 0 | 141
23-0087319 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104Y24 | Unknown Cause | 2023-06-29 16:15 | 6/27 - 7/3 | 2023-06-29 18:44 | 149 | FTS | 10132 | 68 | 4 | 4 | 1 | 0 | 0 | 0 | 149
23-0087324 | Contra Costa | ROSSMOOR 1109 | ROSSMOOR 1109724062 | Unknown Cause | 2023-06-29 16:42 | 6/27 - 7/3 | 2023-06-29 18:51 | 129 | FTS | 1032 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 129
23-0087270 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R56 | Unknown Cause | 2023-06-29 14:48 | 6/27 - 7/3 | 2023-06-29 19:18 | 163.1848 | FTS | 68864 | 422 | 14 | 13 | 10 | 0 | 0 | 1 | 270
23-0086905 | Napa | SILVERADO 2104 | SILVERADO 2104806500 | Unknown Cause | 2023-06-29 03:13 | 6/27 - 7/3 | 2023-06-29 21:11 | 486.814 | FTS | 1248678 | 2565 | 137 | 90 | 59 | 8 | 18 | 4 | 1078
23-0087265 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210152456 | Equipment Failure/Involved | 2023-06-29 14:34 | 6/27 - 7/3 | 2023-06-29 22:51 | 190.8642 | FTS | 193918 | 1016 | 25 | 17 | 54 | 1 | 0 | 0 | 497
23-0087031 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-06-29 09:40 | 6/27 - 7/3 | 2023-06-29 23:05 | 805 | FTS | 45885 | 57 | 10 | 6 | 7 | 0 | 0 | 0 | 805
23-0087296 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR292 | Equipment Failure/Involved | 2023-06-29 15:28 | 6/27 - 7/3 | 2023-06-30 00:58 | 154.0831 | FTS | 118644 | 770 | 59 | 47 | 17 | 0 | 0 | 3 | 570
23-0087361 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown Cause | 2023-06-29 20:14 | 6/27 - 7/3 | 2023-06-30 01:03 | 189.0746 | FTS | 25336 | 134 | 11 | 9 | 5 | 2 | 0 | 0 | 289
23-0087325 | Humboldt | FORT SEWARD 1122 | FORT SEWARD 1122CB | Vegetation | 2023-06-29 16:44 | 6/27 - 7/3 | 2023-06-30 01:56 | 214.1584 | FTS | 21630 | 101 | 1 | 1 | 1 | 1 | 0 | 0 | 552
23-0087420 | Solano | VACA DIXON 1105 | VACA DIXON 11059792 | Unknown Cause | 2023-06-30 00:24 | 6/27 - 7/3 | 2023-06-30 03:06 | 162 | FTS | 1944 | 12 | 3 | 3 | 0 | 0 | 0 | 0 | 162
23-0087414 | Tuolumne | PEORIA 1701 | PEORIA 17013186 | 3rd Party | 2023-06-29 23:45 | 6/27 - 7/3 | 2023-06-30 09:24 | 273.0143 | FTS | 343998 | 1260 | 82 | 65 | 14 | 0 | 0 | 0 | 579
23-0087355 | Shasta | JESSUP 1101 | JESSUP 11011496 | Equipment Failure/Involved | 2023-06-29 19:34 | 6/27 - 7/3 | 2023-06-30 10:59 | 521.4085 | FTS | 444240 | 852 | 89 | 67 | 9 | 2 | 0 | 0 | 925
23-0087372 | Sonoma | DUNBAR 1102 | DUNBAR 1102448 | Vegetation | 2023-06-29 21:43 | 6/27 - 7/3 | 2023-06-30 11:28 | 268.509 | FTS | 164059 | 611 | 38 | 28 | 12 | 0 | 0 | 6 | 825
23-0087595 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210136820 | Company Initiated | 2023-06-30 11:25 | 6/27 - 7/3 | 2023-06-30 11:34 | 9 | FTS | 1017 | 113 | 2 | 2 | 0 | 0 | 0 | 2 | 9
23-0087557 | Contra Costa | LAKEWOOD 1103 | ROSSMOOR 1107857172 | Unknown Cause | 2023-06-30 10:35 | 6/27 - 7/3 | 2023-06-30 12:05 | 90 | FTS | 7110 | 79 | 7 | 5 | 1 | 0 | 0 | 0 | 90
23-0087522 | Lake | KONOCTI 1108 | KONOCTI 11081278 | Animal | 2023-06-30 09:29 | 6/27 - 7/3 | 2023-06-30 12:25 | 176 | FTS | 78672 | 447 | 42 | 32 | 7 | 0 | 0 | 2 | 176
23-0087431 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121134 | Vegetation | 2023-06-30 05:16 | 6/27 - 7/3 | 2023-06-30 14:54 | 138.8043 | FTS | 32619 | 235 | 6 | 5 | 8 | 0 | 0 | 0 | 578
23-0087738 | Humboldt | FRUITLAND 1142 | FRUITLAND 1141200856 | Vegetation | 2023-06-30 15:59 | 6/27 - 7/3 | 2023-06-30 19:20 | 84.6723 | FTS | 14987 | 177 | 5 | 3 | 6 | 1 | 0 | 0 | 201
23-0087804 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110560528 | Unknown Cause | 2023-06-30 20:51 | 6/27 - 7/3 | 2023-06-30 22:35 | 104 | FTS | 196872 | 1893 | 106 | 72 | 28 | 2 | 0 | 2 | 104
23-0087827 | Calaveras | FROGTOWN 1702 | FROGTOWN 17028482 | Equipment Failure/Involved | 2023-06-30 22:27 | 6/27 - 7/3 | 2023-06-30 22:42 | 15 | FTS | 14160 | 944 | 46 | 30 | 39 | 2 | 0 | 2 | 15
23-0087788 | Tuolumne | MIWUK 1702 | MIWUK 17029270 | Equipment Failure/Involved | 2023-06-30 20:19 | 6/27 - 7/3 | 2023-06-30 23:44 | 56.9333 | FTS | 29890 | 525 | 52 | 35 | 5 | 0 | 0 | 0 | 205
23-0087743 | Contra Costa | TASSAJARA 2107 | TASSAJARA 2112D569R | Vegetation | 2023-06-30 16:28 | 6/27 - 7/3 | 2023-06-30 23:59 | 328.0005 | FTS | 1261490 | 3846 | 257 | 165 | 86 | 18 | 0 | 0 | 451
23-0087828 | Marin | BOLINAS 1101 | BOLINAS 11011064 | Unknown Cause | 2023-06-30 22:36 | 6/27 - 7/3 | 2023-07-01 01:00 | 114.3976 | FTS | 37408 | 327 | 3 | 3 | 7 | 2 | 0 | 0 | 144
23-0087698 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | 3rd Party | 2023-06-30 14:51 | 6/27 - 7/3 | 2023-07-01 01:34 | 281.9331 | FTS | 147451 | 523 | 64 | 44 | 4 | 0 | 0 | 0 | 643
23-0087807 | Butte | WYANDOTTE 1107 | WYANDOTTE 110737472 | Unknown Cause | 2023-06-30 21:53 | 6/27 - 7/3 | 2023-07-01 07:32 | 108.3734 | FTS | 50502 | 466 | 53 | 40 | 5 | 0 | 0 | 2 | 579
23-0087853 | Yolo | PUTAH CREEK 1102 | PUTAH CREEK 1102202158 | Animal | 2023-07-01 06:50 | 6/27 - 7/3 | 2023-07-01 07:51 | 61 | FTS | 3843 | 63 | 4 | 3 | 0 | 0 | 0 | 2 | 61
23-0087694 | Contra Costa | KIRKER 2104 | KIRKER 2104CB | Equipment Failure/Involved | 2023-06-30 14:45 | 6/27 - 7/3 | 2023-07-01 08:31 | 124.7511 | FTS | 639100 | 5123 | 466 | 298 | 43 | 9 | 0 | 0 | 1066
23-0087857 | Monterey | SOLEDAD 2105 | SOLEDAD 2105526864 | Animal | 2023-07-01 07:50 | 6/27 - 7/3 | 2023-07-01 09:41 | 111 | FTS | 1221 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 111
23-0087805 | Madera | OAKHURST 1103 | OAKHURST 110377384 | Equipment Failure/Involved | 2023-06-30 21:41 | 6/27 - 7/3 | 2023-07-01 10:30 | 372.638 | FTS | 515731 | 1384 | 67 | 53 | 24 | 0 | 0 | 0 | 769
23-0087790 | Alameda | CAYETANO 2109 | CAYETANO 2109884904 | Unknown Cause | 2023-06-30 19:52 | 6/27 - 7/3 | 2023-07-01 10:58 | 906 | FTS | 166704 | 184 | 12 | 6 | 10 | 0 | 0 | 2 | 906
23-0087803 | Santa Cruz | BURNS 2101 | BIG BASIN 110210254 | Vegetation | 2023-06-30 21:37 | 6/27 - 7/3 | 2023-07-01 13:35 | 593.017 | FTS | 2401719 | 4050 | 312 | 246 | 69 | 4 | 0 | 2 | 958
23-0087952 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Unknown Cause | 2023-07-01 15:15 | 6/27 - 7/3 | 2023-07-01 16:47 | 92 | FTS | 165140 | 1795 | 65 | 39 | 9 | 2 | 0 | 0 | 92
23-0087867 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Animal | 2023-07-01 09:17 | 6/27 - 7/3 | 2023-07-01 16:53 | 256.916 | FTS | 33656 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 456
23-0087917 | Mendocino | GARBERVILLE 1101 | GARBERVILLE 110197300 | Vegetation | 2023-07-01 12:00 | 6/27 - 7/3 | 2023-07-01 18:31 | 212.7143 | FTS | 37225 | 175 | 4 | 4 | 5 | 0 | 0 | 0 | 391
23-0087948 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 1103N44 | Company Initiated | 2023-07-01 15:23 | 6/27 - 7/3 | 2023-07-01 19:18 | 230 | FTS | 273010 | 1187 | 36 | 20 | 25 | 1 | 0 | 3 | 235
23-0087947 | Monterey | SPENCE 1104 | SPENCE 1104965598 | 3rd Party | 2023-07-01 15:15 | 6/27 - 7/3 | 2023-07-01 21:36 | 381 | FTS | 64008 | 168 | 5 | 4 | 2 | 0 | 0 | 1 | 381
23-0087962 | Calaveras | PEORIA 1704 | PEORIA 17046090 | Unknown Cause | 2023-07-01 16:45 | 6/27 - 7/3 | 2023-07-01 22:17 | 322.2321 | FTS | 1015031 | 3150 | 287 | 209 | 68 | 2 | 1 | 1 | 332
23-0087966 | Calaveras | STANISLAUS 1702 | STANISLAUS 170275348 | Equipment Failure/Involved | 2023-07-01 17:12 | 6/27 - 7/3 | 2023-07-01 22:50 | 144.3929 | FTS | 60645 | 420 | 17 | 14 | 3 | 0 | 0 | 0 | 338
23-0088058 | Napa | CALISTOGA 1102 | CALISTOGA 1102706 | Company Initiated | 2023-07-01 22:03 | 6/27 - 7/3 | 2023-07-02 00:03 | 120 | FTS | 160200 | 1335 | 39 | 20 | 21 | 6 | 0 | 0 | 120
23-0087723 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106LB44 | Equipment Failure/Involved | 2023-06-30 15:38 | 6/27 - 7/3 | 2023-07-02 00:58 | 89.0955 | FTS | 29847 | 335 | 25 | 21 | 8 | 4 | 0 | 1 | 2000
23-0088061 | Napa | CALISTOGA 1101 | CALISTOGA 110143924 | Company Initiated | 2023-07-01 22:05 | 6/27 - 7/3 | 2023-07-02 01:22 | 197 | FTS | 116427 | 591 | 22 | 17 | 8 | 0 | 0 | 3 | 197
23-0088086 | Napa | CALISTOGA 1102 | CALISTOGA 1102706 | Company Initiated | 2023-07-02 01:25 | 6/27 - 7/3 | 2023-07-02 02:19 | 54 | FTS | 72090 | 1335 | 39 | 20 | 21 | 6 | 0 | 0 | 54
23-0088085 | Napa | CALISTOGA 1101 | CALISTOGA 110143924 | Company Initiated | 2023-07-02 01:27 | 6/27 - 7/3 | 2023-07-02 02:27 | 60 | FTS | 35460 | 591 | 22 | 17 | 8 | 0 | 0 | 3 | 60
23-0087963 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Equipment Failure/Involved | 2023-07-01 17:05 | 6/27 - 7/3 | 2023-07-02 02:35 | 67.5465 | FTS | 121246 | 1795 | 65 | 39 | 9 | 2 | 0 | 0 | 570
23-0088060 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101890 | Company Initiated | 2023-07-01 22:04 | 6/27 - 7/3 | 2023-07-02 03:13 | 309 | FTS | 52530 | 170 | 4 | 4 | 1 | 0 | 0 | 0 | 309
23-0088059 | Napa | CALISTOGA 1101 | CALISTOGA 11015934 | Company Initiated | 2023-07-01 22:03 | 6/27 - 7/3 | 2023-07-02 04:36 | 393 | FTS | 149340 | 380 | 13 | 10 | 1 | 0 | 0 | 1 | 393
23-0088083 | Lake | KONOCTI 1108 | KONOCTI 11081278 | Unknown Cause | 2023-07-02 00:25 | 6/27 - 7/3 | 2023-07-02 05:12 | 287 | FTS | 128289 | 447 | 44 | 34 | 7 | 0 | 0 | 2 | 287
23-0088070 | Napa | CALISTOGA 1102 | CALISTOGA 1102634 | Company Initiated | 2023-07-01 23:17 | 6/27 - 7/3 | 2023-07-02 05:57 | 400 | FTS | 114000 | 285 | 6 | 6 | 4 | 0 | 0 | 0 | 400
23-0088055 | Napa | CALISTOGA 1102 | CALISTOGA 1102769230 | Company Initiated | 2023-07-01 22:02 | 6/27 - 7/3 | 2023-07-02 06:27 | 505 | FTS | 93425 | 185 | 0 | 0 | 4 | 0 | 0 | 1 | 505
23-0088003 | Sonoma | SONOMA 1104 | SONOMA 1104914376 | Unknown Cause | 2023-07-01 19:30 | 6/27 - 7/3 | 2023-07-02 08:48 | 263.9457 | FTS | 204030 | 773 | 38 | 26 | 11 | 1 | 0 | 5 | 798
23-0088102 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y36 | Unknown Cause | 2023-07-02 05:07 | 6/27 - 7/3 | 2023-07-02 08:48 | 108.0345 | FTS | 31330 | 290 | 11 | 7 | 24 | 1 | 0 | 0 | 221
23-0088103 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y26 | Unknown Cause | 2023-07-02 05:08 | 6/27 - 7/3 | 2023-07-02 09:50 | 152.4084 | FTS | 29110 | 191 | 7 | 5 | 6 | 0 | 0 | 0 | 282
23-0088017 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 210769586 | Equipment Failure/Involved | 2023-07-01 20:03 | 6/27 - 7/3 | 2023-07-02 11:00 | 59.0202 | FTS | 73185 | 1240 | 86 | 66 | 14 | 0 | 0 | 0 | 897
23-0088131 | Lake | KONOCTI 1108 | KONOCTI 11081278 | Unknown Cause | 2023-07-02 08:50 | 6/27 - 7/3 | 2023-07-02 11:17 | 147 | FTS | 65709 | 447 | 44 | 34 | 7 | 0 | 0 | 2 | 147
23-0087989 | Tuolumne | MIWUK 1702 | MIWUK 17028130 | Equipment Failure/Involved | 2023-07-01 18:40 | 6/27 - 7/3 | 2023-07-02 12:49 | 90.8993 | FTS | 39723 | 437 | 44 | 32 | 2 | 1 | 0 | 0 | 1089
23-0088012 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210819622 | Equipment Failure/Involved | 2023-07-01 20:07 | 6/27 - 7/3 | 2023-07-02 12:52 | 173.3496 | FTS | 333178 | 1922 | 180 | 126 | 16 | 2 | 0 | 0 | 1005
23-0087976 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Equipment Failure/Involved | 2023-07-01 17:56 | 6/27 - 7/3 | 2023-07-02 14:06 | 369.3087 | FTS | 330162 | 894 | 62 | 41 | 16 | 0 | 0 | 0 | 1210
23-0088112 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101370948 | Equipment Failure/Involved | 2023-07-02 07:15 | 6/27 - 7/3 | 2023-07-02 15:43 | 179.9164 | FTS | 129180 | 718 | 57 | 47 | 12 | 0 | 0 | 0 | 508
23-0088018 | Alameda | SUNOL 1101 | SUNOL 1101605520 | Equipment Failure/Involved | 2023-07-01 20:12 | 6/27 - 7/3 | 2023-07-02 16:18 | 342.4951 | FTS | 35277 | 103 | 5 | 1 | 1 | 0 | 0 | 0 | 1206
23-0087852 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Unknown Cause | 2023-07-01 07:00 | 6/27 - 7/3 | 2023-07-02 16:24 | 784.2291 | FTS | 4826146 | 6154 | 212 | 158 | 44 | 1 | 0 | 5 | 2004
23-0088126 | Butte | WYANDOTTE 1109 | WYANDOTTE 110913052 | Animal | 2023-07-02 08:28 | 6/27 - 7/3 | 2023-07-02 16:28 | 131.4611 | FTS | 45617 | 347 | 33 | 26 | 2 | 0 | 0 | 1 | 480
23-0088118 | Monterey | DEL MONTE 2104 | DEL MONTE 21042624 | Unknown Cause | 2023-07-02 07:57 | 6/27 - 7/3 | 2023-07-02 16:36 | 240.9422 | FTS | 354426 | 1471 | 76 | 57 | 52 | 1 | 0 | 1 | 519
23-0088125 | Monterey | SAN ARDO 1102 | SAN ARDO 11027066 | Equipment Failure/Involved | 2023-07-02 08:41 | 6/27 - 7/3 | 2023-07-02 17:46 | 545 | FTS | 159140 | 292 | 4 | 3 | 12 | 4 | 0 | 0 | 545
23-0088175 | Contra Costa | CAYETANO 2109 | CAYETANO 2109884904 | Unknown Cause | 2023-07-02 09:44 | 6/27 - 7/3 | 2023-07-02 18:30 | 526 | FTS | 32612 | 62 | 6 | 4 | 8 | 0 | 0 | 1 | 526
23-0088222 | Tuolumne | PEORIA 1701 | PEORIA 17013186 | Equipment Failure/Involved | 2023-07-02 18:23 | 6/27 - 7/3 | 2023-07-02 20:50 | 139.381 | FTS | 175620 | 1260 | 82 | 65 | 14 | 0 | 0 | 0 | 147
23-0088230 | Tehama | PANORAMA 1101 | PANORAMA 1101713592 | Unknown Cause | 2023-07-02 19:06 | 6/27 - 7/3 | 2023-07-02 21:33 | 137.2407 | FTS | 110616 | 806 | 103 | 74 | 11 | 0 | 0 | 0 | 147
23-0088108 | Trinity | WILDWOOD 1101 | WILDWOOD 11011576 | Unknown Cause | 2023-07-02 06:44 | 6/27 - 7/3 | 2023-07-02 21:58 | 138.4819 | FTS | 11494 | 83 | 4 | 1 | 6 | 1 | 0 | 0 | 914
23-0088204 | Contra Costa | SOBRANTE 1103 | SOBRANTE 1103CB | 3rd Party | 2023-07-02 17:16 | 6/27 - 7/3 | 2023-07-03 01:00 | 400.2916 | FTS | 1378204 | 3443 | 156 | 114 | 46 | 9 | 0 | 0 | 464
23-0088217 | Tuolumne | CURTIS 1701 | CURTIS 1701CB | Equipment Failure/Involved | 2023-07-02 18:22 | 6/27 - 7/3 | 2023-07-03 01:33 | 401.9518 | FTS | 1308755 | 3256 | 205 | 150 | 48 | 8 | 9 | 0 | 431
23-0088178 | Nevada | HIGGINS 1110 | HIGGINS 1110CB | Vegetation | 2023-07-02 14:21 | 6/27 - 7/3 | 2023-07-03 01:38 | 183.952 | FTS | 256981 | 1397 | 120 | 80 | 16 | 3 | 0 | 9 | 677
23-0088099 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Vegetation | 2023-07-02 02:59 | 6/27 - 7/3 | 2023-07-03 02:20 | 476.2095 | HLT | 745744 | 1566 | 225 | 170 | 25 | 0 | 0 | 1 | 1401
23-0088149 | Monterey | SAN BENITO 2104 | SAN BENITO 210488772 | Equipment Failure/Involved | 2023-07-02 10:30 | 6/27 - 7/3 | 2023-07-03 02:39 | 13.4191 | FTS | 16841 | 1255 | 93 | 79 | 21 | 2 | 0 | 3 | 969
23-0088215 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Vegetation | 2023-07-02 18:13 | 6/27 - 7/3 | 2023-07-03 03:25 | 102.3912 | FTS | 176420 | 1723 | 130 | 81 | 29 | 7 | 0 | 4 | 552
23-0088297 | Butte | WYANDOTTE 1103 | WYANDOTTE 11031508 | Company Initiated | 2023-07-03 02:40 | 6/27 - 7/3 | 2023-07-03 03:35 | 55 | FTS | 32945 | 599 | 25 | 17 | 6 | 0 | 0 | 2 | 55
23-0088309 | Placer | LINCOLN 1101 | LINCOLN 110195756 | Animal | 2023-07-03 05:23 | 6/27 - 7/3 | 2023-07-03 07:04 | 101 | FTS | 27472 | 272 | 29 | 22 | 0 | 0 | 0 | 6 | 101
23-0088167 | Tehama | RED BLUFF 1104 | RED BLUFF 110451238 | Equipment Failure/Involved | 2023-07-02 13:35 | 6/27 - 7/3 | 2023-07-03 08:05 | 217.1271 | FTS | 78600 | 362 | 34 | 20 | 10 | 0 | 0 | 1 | 1110
23-0088231 | Santa Cruz | BURNS 2101 | BURNS 2101CB | Vegetation | 2023-07-02 19:05 | 6/27 - 7/3 | 2023-07-03 09:48 | 439.132 | FTS | 1780241 | 4054 | 11 | 8 | 11 | 0 | 0 | 0 | 883
23-0088130 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022044 | Equipment Failure/Involved | 2023-07-02 08:59 | 6/27 - 7/3 | 2023-07-03 10:03 | 153.8551 | FTS | 10616 | 69 | 5 | 2 | 1 | 0 | 0 | 0 | 1504
23-0088226 | Yuba | EAST MARYSVILLE 1108 | EAST MARYSVILLE 1108900690 | Unknown Cause | 2023-07-02 18:35 | 6/27 - 7/3 | 2023-07-03 10:15 | 790.6351 | FTS | 793007 | 1003 | 94 | 64 | 11 | 1 | 0 | 10 | 940
23-0088294 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A16 | Unknown Cause | 2023-07-03 01:36 | 6/27 - 7/3 | 2023-07-03 10:21 | 332.0044 | FTS | 74701 | 225 | 8 | 4 | 3 | 0 | 0 | 0 | 525
23-0088370 | Merced | ORO LOMA 1106 | ORO LOMA 11069790 | 3rd Party | 2023-07-03 08:44 | 6/27 - 7/3 | 2023-07-03 11:42 | 110.3238 | FTS | 23168 | 210 | 0 | 0 | 7 | 0 | 0 | 0 | 178
23-0088199 | Contra Costa | CLAYTON 2215 | CLAYTON 2215CB | Equipment Failure/Involved | 2023-07-02 16:44 | 6/27 - 7/3 | 2023-07-03 11:47 | 290.199 | FTS | 1341880 | 4624 | 342 | 236 | 65 | 6 | 0 | 0 | 1143
23-0088475 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 110137454 | Unknown Cause | 2023-07-03 11:38 | 6/27 - 7/3 | 2023-07-03 12:48 | 70 | FTS | 8330 | 119 | 4 | 3 | 1 | 0 | 0 | 1 | 70
23-0088541 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2104CB | Unknown Cause | 2023-07-03 13:17 | 6/27 - 7/3 | 2023-07-03 14:32 | 75 | FTS | 213600 | 2848 | 157 | 110 | 29 | 4 | 0 | 5 | 75
23-0088247 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Equipment Failure/Involved | 2023-07-02 21:33 | 6/27 - 7/3 | 2023-07-03 14:40 | 959.1899 | FTS | 1833971 | 1912 | 140 | 98 | 22 | 1 | 0 | 4 | 1027
23-0088219 | Tuolumne | CURTIS 1703 | CURTIS 170390320 | Equipment Failure/Involved | 2023-07-02 18:22 | 6/27 - 7/3 | 2023-07-03 14:42 | 1215.6959 | FTS | 1415070 | 1164 | 72 | 60 | 22 | 0 | 0 | 1 | 1220
23-0088453 | Calaveras | PEORIA 1704 | PEORIA 170413494 | Equipment Failure/Involved | 2023-07-03 08:32 | 6/27 - 7/3 | 2023-07-03 14:42 | 93.8369 | FTS | 62120 | 662 | 63 | 46 | 8 | 0 | 0 | 0 | 370
23-0088352 | Madera | COARSEGOLD 2102 | COARSEGOLD 210210330 | Company Initiated | 2023-07-03 07:57 | 6/27 - 7/3 | 2023-07-03 15:04 | 402.8281 | FTS | 618744 | 1536 | 133 | 99 | 40 | 5 | 0 | 2 | 427
23-0088291 | Plumas | GANSNER 1101 | GANSNER 110199388 | 3rd Party | 2023-07-03 01:08 | 6/27 - 7/3 | 2023-07-03 15:20 | 100.7738 | FTS | 107828 | 1070 | 37 | 31 | 26 | 87 | 0 | 2 | 852
23-0088350 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Vegetation | 2023-07-03 07:56 | 6/27 - 7/3 | 2023-07-03 16:17 | 72.6267 | FTS | 190863 | 2628 | 308 | 223 | 59 | 8 | 0 | 0 | 501
23-0088434 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | Unknown Cause | 2023-07-03 10:24 | 6/27 - 7/3 | 2023-07-03 16:48 | 89.5476 | FTS | 246614 | 2754 | 247 | 181 | 40 | 8 | 0 | 17 | 384
23-0088627 | Contra Costa | ROSSMOOR 1106 | ROSSMOOR 1106L522R | Unknown Cause | 2023-07-03 16:24 | 7/4 - 7/10 | 2023-07-03 17:05 | 39.323 | FTS | 53086 | 1350 | 47 | 33 | 9 | 7 | 0 | 0 | 41
23-0088639 | Contra Costa | ROSSMOOR 1102 | ROSSMOOR 1102457174 | Equipment Failure/Involved | 2023-07-03 16:47 | 7/4 - 7/10 | 2023-07-03 18:00 | 73 | FTS | 225935 | 3095 | 316 | 223 | 17 | 0 | 0 | 0 | 73
23-0088668 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110560528 | Unknown Cause | 2023-07-03 19:44 | 7/4 - 7/10 | 2023-07-03 20:51 | 67 | FTS | 126831 | 1893 | 108 | 73 | 28 | 2 | 0 | 2 | 67
23-0088667 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Unknown Cause | 2023-07-03 19:52 | 7/4 - 7/10 | 2023-07-03 21:00 | 68 | FTS | 6936 | 102 | 2 | 2 | 12 | 11 | 0 | 0 | 68
23-0088654 | Yolo | MADISON 2101 | MADISON 21019512 | Environmental/External | 2023-07-03 18:04 | 7/4 - 7/10 | 2023-07-04 03:29 | 62.093 | FTS | 8010 | 129 | 1 | 0 | 6 | 0 | 0 | 0 | 565
23-0088699 | Butte | ORO FINO 1102 | ORO FINO 110276008 | Equipment Failure/Involved | 2023-07-03 23:31 | 7/4 - 7/10 | 2023-07-04 04:45 | 63.3697 | FTS | 23827 | 376 | 35 | 21 | 4 | 0 | 0 | 0 | 314
23-0088705 | Monterey | LAURELES 1111 | LAURELES 11112028 | Unknown Cause | 2023-07-04 02:59 | 7/4 - 7/10 | 2023-07-04 07:06 | 247 | FTS | 120783 | 489 | 35 | 25 | 7 | 0 | 0 | 0 | 247
23-0088716 | Solano | VACAVILLE 1104 | VACAVILLE 1104CB | Animal | 2023-07-04 06:33 | 7/4 - 7/10 | 2023-07-04 07:27 | 45.1619 | FTS | 132234 | 2928 | 218 | 152 | 41 | 5 | 0 | 2 | 54
23-0088106 | Santa Cruz | SAN BENITO 2104 | SAN BENITO 210488772 | Equipment Failure/Involved | 2023-07-02 06:41 | 7/4 - 7/10 | 2023-07-04 07:43 | 94.0574 | FTS | 118042 | 1255 | 93 | 79 | 21 | 2 | 0 | 3 | 2942
23-0088712 | Monterey | SOLEDAD 2102 | SOLEDAD 2102858388 | Unknown Cause | 2023-07-04 05:50 | 7/4 - 7/10 | 2023-07-04 10:18 | 220.3362 | FTS | 25559 | 116 | 4 | 3 | 0 | 1 | 0 | 0 | 268
23-0088697 | Fresno | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-07-03 23:08 | 7/4 - 7/10 | 2023-07-04 10:29 | 679.3689 | FTS | 209925 | 309 | 10 | 6 | 7 | 0 | 0 | 0 | 681
23-0088696 | Sonoma | MIRABEL 1102 | MIRABEL 1102503294 | Equipment Failure/Involved | 2023-07-03 22:46 | 7/4 - 7/10 | 2023-07-04 11:04 | 282.5727 | FTS | 153437 | 543 | 21 | 11 | 10 | 0 | 0 | 0 | 738
23-0088707 | Contra Costa | MEADOW LANE 2106 | MEADOW LANE 2106C558R | Vegetation | 2023-07-04 03:36 | 7/4 - 7/10 | 2023-07-04 14:52 | 255.4154 | FTS | 760627 | 2978 | 219 | 157 | 31 | 6 | 0 | 0 | 676
23-0088741 | Monterey | SAN MIGUEL 1106 | SAN MIGUEL 1106605393 | Unknown Cause | 2023-07-04 09:38 | 7/4 - 7/10 | 2023-07-04 14:57 | 205.6667 | FTS | 18510 | 90 | 2 | 1 | 1 | 0 | 0 | 0 | 319
23-0088751 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Unknown Cause | 2023-07-04 12:27 | 7/4 - 7/10 | 2023-07-04 16:01 | 214 | FTS | 123264 | 576 | 35 | 17 | 5 | 0 | 0 | 0 | 214
23-0088732 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X08 | Animal | 2023-07-04 08:51 | 7/4 - 7/10 | 2023-07-04 16:04 | 433 | FTS | 32042 | 74 | 4 | 0 | 1 | 0 | 0 | 0 | 433
23-0088761 | Calaveras | WEST POINT 1102 | WEST POINT 110293116 | Vegetation | 2023-07-04 15:35 | 7/4 - 7/10 | 2023-07-04 17:18 | 103 | FTS | 62521 | 607 | 49 | 34 | 7 | 0 | 0 | 0 | 103
23-0088807 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102CB | Animal | 2023-07-04 23:28 | 7/4 - 7/10 | 2023-07-05 02:02 | 154 | FTS | 361284 | 2346 | 57 | 35 | 44 | 1 | 3 | 0 | 154
23-0088776 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401944178 | Unknown Cause | 2023-07-04 20:12 | 7/4 - 7/10 | 2023-07-05 02:46 | 286.5485 | FTS | 253882 | 886 | 81 | 63 | 16 | 3 | 0 | 1 | 394
23-0088808 | Placer | HALSEY 1101 | HALSEY 1101CB | Animal | 2023-07-05 01:00 | 7/4 - 7/10 | 2023-07-05 03:27 | 147 | FTS | 348243 | 2369 | 186 | 133 | 28 | 5 | 0 | 5 | 147
23-0088811 | Lake | LUCERNE 1106 | LUCERNE 1106664 | Equipment Failure/Involved | 2023-07-05 04:32 | 7/4 - 7/10 | 2023-07-05 09:22 | 67.0384 | FTS | 78502 | 1171 | 91 | 65 | 23 | 0 | 3 | 1 | 290
23-0088862 | Tuolumne | CURTIS 1702 | CURTIS 170210940 | Vegetation | 2023-07-05 08:25 | 7/4 - 7/10 | 2023-07-05 09:24 | 59 | FTS | 37819 | 641 | 67 | 45 | 3 | 1 | 0 | 0 | 59
23-0088854 | Lake | HARTLEY 1101 | HARTLEY 1101658 | Equipment Failure/Involved | 2023-07-05 08:14 | 7/4 - 7/10 | 2023-07-05 12:29 | 125.0136 | FTS | 73758 | 590 | 33 | 21 | 9 | 0 | 0 | 2 | 255
23-0088861 | Amador | MARTELL 1101 | MARTELL 110111244 | 3rd Party | 2023-07-05 08:19 | 7/4 - 7/10 | 2023-07-05 17:54 | 310.25 | FTS | 19856 | 64 | 4 | 2 | 0 | 0 | 0 | 0 | 575
23-0089072 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 1101CB | Equipment Failure/Involved | 2023-07-05 14:17 | 7/4 - 7/10 | 2023-07-05 20:57 | 399.2512 | FTS | 328983 | 824 | 33 | 25 | 17 | 3 | 0 | 0 | 400
23-0089119 | Shasta | JESSUP 1101 | JESSUP 11011496 | Equipment Failure/Involved | 2023-07-05 15:46 | 7/4 - 7/10 | 2023-07-06 05:24 | 267.7556 | FTS | 227860 | 851 | 91 | 69 | 9 | 2 | 0 | 0 | 818
23-0089291 | Merced | SANTA NELLA 1101 | SANTA NELLA 11037200 | Equipment Failure/Involved | 2023-07-06 08:58 | 7/4 - 7/10 | 2023-07-06 09:50 | 52 | FTS | 5772 | 111 | 1 | 1 | 9 | 0 | 0 | 0 | 52
23-0089278 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21011703 | 3rd Party | 2023-07-06 08:30 | 7/4 - 7/10 | 2023-07-06 10:21 | 111 | FTS | 111 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 111
23-0089232 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A80 | 3rd Party | 2023-07-06 06:59 | 7/4 - 7/10 | 2023-07-06 12:17 | 197.8669 | FTS | 101110 | 511 | 26 | 20 | 7 | 1 | 0 | 0 | 318
23-0089372 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | Unknown Cause | 2023-07-06 11:18 | 7/4 - 7/10 | 2023-07-06 15:21 | 229.0714 | FTS | 118659 | 518 | 34 | 21 | 14 | 4 | 0 | 7 | 243
23-0089567 | Lake | HIGHLANDS 1104 | HIGHLANDS 110476156 | 3rd Party | 2023-07-06 16:49 | 7/4 - 7/10 | 2023-07-06 17:34 | 45 | FTS | 5850 | 130 | 11 | 9 | 8 | 0 | 0 | 0 | 45
23-0089443 | Shasta | VOLTA 1102 | VOLTA 11021504 | Unknown Cause | 2023-07-06 13:08 | 7/4 - 7/10 | 2023-07-06 18:59 | 308.7993 | FTS | 363148 | 1176 | 119 | 86 | 17 | 3 | 0 | 0 | 351
23-0089204 | Calaveras | CORRAL 1101 | CORRAL 110175204 | Vegetation | 2023-07-06 04:40 | 7/4 - 7/10 | 2023-07-06 20:45 | 254.9011 | FTS | 46392 | 182 | 3 | 2 | 4 | 0 | 0 | 0 | 965
23-0089599 | Placer | PENRYN 1103 | PENRYN 1103660 | Unknown Cause | 2023-07-06 20:14 | 7/4 - 7/10 | 2023-07-07 00:56 | 202.4768 | FTS | 91722 | 453 | 32 | 19 | 3 | 0 | 0 | 4 | 282
23-0089592 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2023-07-06 18:04 | 7/4 - 7/10 | 2023-07-07 03:09 | 346.3652 | FTS | 39832 | 115 | 2 | 2 | 8 | 1 | 0 | 0 | 545
23-0089582 | El Dorado | APPLE HILL 1104 | APPLE HILL 110412842 | Unknown Cause | 2023-07-06 17:20 | 7/4 - 7/10 | 2023-07-07 04:12 | 448.7229 | FTS | 252631 | 563 | 52 | 36 | 3 | 0 | 0 | 1 | 652
23-0089603 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102350 | Unknown Cause | 2023-07-06 20:43 | 7/4 - 7/10 | 2023-07-07 09:15 | 75.3843 | FTS | 17263 | 229 | 8 | 3 | 4 | 1 | 0 | 0 | 752
23-0089646 | Shasta | JESSUP 1101 | JESSUP 11011496 | 3rd Party | 2023-07-07 05:45 | 7/4 - 7/10 | 2023-07-07 10:57 | 124.7876 | FTS | 106319 | 852 | 91 | 69 | 9 | 2 | 0 | 0 | 312
23-0089671 | Merced | SANTA NELLA 1101 | SANTA NELLA 11037200 | Unknown Cause | 2023-07-07 07:28 | 7/4 - 7/10 | 2023-07-07 11:18 | 230 | FTS | 25530 | 111 | 1 | 1 | 9 | 0 | 0 | 0 | 230
23-0089648 | Sonoma | DUNBAR 1102 | DUNBAR 1102386158 | Unknown Cause | 2023-07-07 05:51 | 7/4 - 7/10 | 2023-07-07 11:28 | 329.0523 | FTS | 176043 | 535 | 25 | 15 | 8 | 0 | 0 | 6 | 337
23-0089773 | Calaveras | SALT SPRINGS 2101 | SALT SPRINGS 21011232 | Equipment Failure/Involved | 2023-07-07 09:29 | 7/4 - 7/10 | 2023-07-07 13:12 | 220.6033 | FTS | 202955 | 920 | 17 | 14 | 9 | 2 | 0 | 0 | 223
23-0089883 | Madera | COARSEGOLD 2102 | COARSEGOLD 2102383092 | Equipment Failure/Involved | 2023-07-07 12:30 | 7/4 - 7/10 | 2023-07-07 14:52 | 63.5329 | FTS | 86913 | 1368 | 120 | 88 | 34 | 5 | 0 | 2 | 142
23-0089636 | Butte | BANGOR 1101 | BANGOR 110131502 | Unknown Cause | 2023-07-06 22:52 | 7/4 - 7/10 | 2023-07-07 15:36 | 304.4445 | FTS | 400649 | 1316 | 144 | 97 | 6 | 0 | 0 | 9 | 1004
23-0089890 | San Luis Obispo | CUYAMA 1103 | CUYAMA 1103684566 | Unknown Cause | 2023-07-07 12:21 | 7/4 - 7/10 | 2023-07-07 16:14 | 233 | FTS | 1398 | 6 | 0 | 0 | 3 | 0 | 0 | 0 | 233
23-0090007 | El Dorado | APPLE HILL 1104 | APPLE HILL 110412842 | Animal | 2023-07-07 18:31 | 7/4 - 7/10 | 2023-07-07 20:42 | 131 | FTS | 73753 | 563 | 52 | 36 | 3 | 0 | 0 | 1 | 131
23-0090044 | Mendocino | PHILO 1102 | PHILO 1102920 | Unknown Cause | 2023-07-07 23:13 | 7/4 - 7/10 | 2023-07-08 02:27 | 149.8719 | FTS | 110006 | 734 | 18 | 12 | 13 | 1 | 0 | 1 | 194
23-0090030 | Calaveras | CORRAL SUB | N/A | 3rd Party | 2023-07-07 20:26 | 7/4 - 7/10 | 2023-07-08 05:55 | 162.2143 | T-EPSS | 928190 | 5722 | 550 | 361 | 85 | 1 | 0 | 7 | 569
23-0090052 | San Benito | HOLLISTER 2104 | HOLLISTER 210491424 | Unknown Cause | 2023-07-08 05:35 | 7/4 - 7/10 | 2023-07-08 06:42 | 67 | FTS | 9581 | 143 | 3 | 2 | 6 | 0 | 0 | 0 | 67
23-0090080 | Placer | PLACER 1103 | PLACER 1103CB | Unknown Cause | 2023-07-08 09:19 | 7/4 - 7/10 | 2023-07-08 15:06 | 306.673 | FTS | 709028 | 2312 | 155 | 83 | 29 | 3 | 0 | 0 | 347
23-0090108 | Sierra | PIKE CITY 1101 | PIKE CITY 1101935730 | Unknown Cause | 2023-07-08 12:05 | 7/4 - 7/10 | 2023-07-08 16:43 | 278 | FTS | 24186 | 87 | 1 | 1 | 1 | 0 | 0 | 0 | 278
23-0090138 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108CB | Unknown Cause | 2023-07-08 16:09 | 7/4 - 7/10 | 2023-07-08 19:52 | 80.5901 | FTS | 676957 | 8400 | 424 | 289 | 137 | 25 | 0 | 0 | 223
23-0090120 | Santa Cruz | BURNS 2101 | BURNS 210136516 | Vegetation | 2023-07-08 13:53 | 7/4 - 7/10 | 2023-07-08 21:02 | 137.7879 | FTS | 54564 | 396 | 29 | 20 | 9 | 0 | 0 | 7 | 429
23-0090183 | Tulare | REEDLEY 1104 | REEDLEY 1104887932 | Unknown Cause | 2023-07-08 23:22 | 7/4 - 7/10 | 2023-07-09 01:35 | 133 | FTS | 3458 | 26 | 1 | 1 | 0 | 0 | 0 | 0 | 133
23-0090196 | Placer | SHADY GLEN 1101 | SHADY GLEN 110151696 | Unknown Cause | 2023-07-09 06:53 | 7/4 - 7/10 | 2023-07-09 11:43 | 133.0262 | FTS | 131829 | 991 | 70 | 48 | 13 | 1 | 0 | 4 | 290
23-0090222 | Placer | PENRYN 1107 | PENRYN 11072708 | Animal | 2023-07-09 10:24 | 7/4 - 7/10 | 2023-07-09 12:25 | 121 | FTS | 46222 | 382 | 35 | 25 | 6 | 0 | 0 | 1 | 121
23-0090190 | Sonoma | MONTE RIO 1113 | MONTE RIO 11133970 | Vegetation | 2023-07-09 02:02 | 7/4 - 7/10 | 2023-07-09 13:43 | 371.6441 | FTS | 956612 | 2574 | 156 | 100 | 45 | 6 | 0 | 0 | 701
23-0090236 | Contra Costa | TASSAJARA 2108 | TASSAJARA 210883368 | Equipment Failure/Involved | 2023-07-09 11:56 | 7/4 - 7/10 | 2023-07-09 14:18 | 142 | FTS | 180482 | 1271 | 60 | 39 | 23 | 6 | 0 | 0 | 142
23-0090193 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A16 | Vegetation | 2023-07-09 05:22 | 7/4 - 7/10 | 2023-07-09 16:53 | 168.0222 | FTS | 37805 | 225 | 8 | 4 | 3 | 0 | 0 | 0 | 691
23-0090168 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102613456 | Equipment Failure/Involved | 2023-07-08 20:52 | 7/4 - 7/10 | 2023-07-09 19:30 | 1259.7864 | FTS | 129758 | 103 | 1 | 1 | 0 | 0 | 0 | 1 | 1358
23-0090284 | Calaveras | Valley Springs 1101 | Valley Springs 110111158 | Company Initiated | 2023-07-10 02:05 | 7/4 - 7/10 | 2023-07-10 02:40 | 35 | FTS | 9240 | 264 | 18 | 9 | 9 | 0 | 0 | 3 | 35
23-0090279 | Sonoma | SONOMA 1104 | SONOMA 1104414 | Unknown Cause | 2023-07-09 23:27 | 7/4 - 7/10 | 2023-07-10 09:00 | 573 | FTS | 14898 | 26 | 180 | 114 | 48 | 8 | 0 | 5 | 573
23-0090255 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102851902 | Animal | 2023-07-09 17:42 | 7/4 - 7/10 | 2023-07-10 09:06 | 349.9319 | FTS | 935018 | 2672 | 196 | 141 | 40 | 6 | 0 | 2 | 924
23-0090314 | El Dorado | DIAMOND SPRINGS 1104 | DIAMOND SPRINGS 1104705100 | Animal | 2023-07-10 07:31 | 7/4 - 7/10 | 2023-07-10 09:11 | 100 | FTS | 10500 | 105 | 12 | 10 | 7 | 5 | 0 | 0 | 100
23-0090287 | Placer | PENRYN 1103 | PENRYN 11032198 | Animal | 2023-07-10 04:40 | 7/4 - 7/10 | 2023-07-10 10:20 | 71.1894 | FTS | 32320 | 454 | 26 | 16 | 4 | 0 | 0 | 8 | 340
23-0090378 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Company Initiated | 2023-07-10 09:54 | 7/4 - 7/10 | 2023-07-10 10:55 | 60 | FTS | 79620 | 1327 | 122 | 85 | 17 | 0 | 0 | 11 | 61
23-0090312 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110560528 | Unknown Cause | 2023-07-10 07:25 | 7/4 - 7/10 | 2023-07-10 11:31 | 76.2108 | FTS | 144267 | 1893 | 108 | 73 | 28 | 2 | 0 | 2 | 246
23-0090466 | Colusa | MAXWELL 1105 | MAXWELL 11053008 | Animal | 2023-07-10 12:16 | 7/4 - 7/10 | 2023-07-10 14:29 | 133 | FTS | 6517 | 49 | 1 | 0 | 4 | 0 | 0 | 0 | 133
23-0090281 | Solano | VACAVILLE 1108 | VACAVILLE 1108CB | Equipment Failure/Involved | 2023-07-10 00:51 | 7/4 - 7/10 | 2023-07-10 15:00 | 221.7739 | FTS | 726975 | 3278 | 275 | 195 | 57 | 14 | 0 | 3 | 849
23-0090528 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103248212 | Unknown Cause | 2023-07-10 13:48 | 7/11 - 7/17 | 2023-07-10 17:25 | 205.3478 | FTS | 37784 | 184 | 11 | 8 | 8 | 0 | 0 | 0 | 217
23-0090620 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104Y24 | Unknown Cause | 2023-07-10 17:57 | 7/11 - 7/17 | 2023-07-10 19:59 | 122 | FTS | 8296 | 68 | 4 | 4 | 1 | 0 | 0 | 0 | 122
23-0090444 | Sonoma | DUNBAR 1101 | DUNBAR 1101904852 | Equipment Failure/Involved | 2023-07-10 11:34 | 7/11 - 7/17 | 2023-07-10 20:19 | 234.2904 | FTS | 509816 | 2176 | 105 | 64 | 38 | 5 | 0 | 8 | 525
23-0090636 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Equipment Failure/Involved | 2023-07-10 21:13 | 7/11 - 7/17 | 2023-07-11 00:08 | 173.2356 | FTS | 393418 | 2271 | 97 | 65 | 47 | 2 | 0 | 4 | 175
23-0090446 | Sonoma | DUNBAR 1103 | DUNBAR 1103CB | 3rd Party | 2023-07-10 11:43 | 7/11 - 7/17 | 2023-07-11 02:21 | 325.616 | FTS | 1070951 | 3289 | 326 | 254 | 44 | 7 | 0 | 15 | 878
23-0090562 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | 3rd Party | 2023-07-10 14:52 | 7/11 - 7/17 | 2023-07-11 03:16 | 119.2886 | FTS | 59525 | 499 | 19 | 8 | 4 | 0 | 0 | 0 | 744
23-0090671 | San Luis Obispo | PERRY 1101 | PERRY 1101986322 | Animal | 2023-07-11 06:09 | 7/11 - 7/17 | 2023-07-11 08:00 | 111 | FTS | 174825 | 1575 | 66 | 44 | 10 | 0 | 0 | 0 | 111
23-0090672 | El Dorado | APPLE HILL 1104 | APPLE HILL 110412832 | Unknown Cause | 2023-07-11 06:10 | 7/11 - 7/17 | 2023-07-11 09:04 | 174 | FTS | 135198 | 777 | 70 | 44 | 7 | 0 | 0 | 8 | 174
23-0090721 | Contra Costa | ROSSMOOR 1109 | ROSSMOOR 1109724062 | Company Initiated | 2023-07-11 08:11 | 7/11 - 7/17 | 2023-07-11 09:10 | 59 | FTS | 472 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 59
23-0090690 | Santa Clara | SARATOGA 1107 | SARATOGA 1107413816 | Animal | 2023-07-11 07:28 | 7/11 - 7/17 | 2023-07-11 11:03 | 174.0723 | FTS | 28896 | 166 | 9 | 4 | 2 | 2 | 0 | 1 | 215
23-0090778 | San Mateo | MENLO 1102 | MENLO 11029152 | Vegetation | 2023-07-11 10:22 | 7/11 - 7/17 | 2023-07-11 12:35 | 133 | FTS | 20482 | 154 | 7 | 6 | 1 | 0 | 0 | 0 | 133
23-0090691 | Mendocino | PHILO 1102 | PHILO 1102920 | Unknown Cause | 2023-07-11 07:18 | 7/11 - 7/17 | 2023-07-11 13:47 | 283.0218 | FTS | 207455 | 733 | 18 | 12 | 13 | 1 | 0 | 1 | 389
23-0090665 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101518 | Unknown Cause | 2023-07-11 01:36 | 7/11 - 7/17 | 2023-07-11 14:26 | 767.6129 | FTS | 356940 | 465 | 33 | 24 | 14 | 4 | 0 | 0 | 770
23-0091026 | El Dorado | PLACERVILLE 1111 | PLACERVILLE 11118582 | Equipment Failure/Involved | 2023-07-11 19:08 | 7/11 - 7/17 | 2023-07-11 20:57 | 109 | FTS | 41529 | 381 | 24 | 14 | 13 | 0 | 0 | 0 | 109
23-0091028 | Sonoma | PETALUMA A SUB | N/A | Animal | 2023-07-11 19:31 | 7/11 - 7/17 | 2023-07-11 22:33 | 180.962 | T-EPSS | 228374 | 1262 | 29 | 22 | 11 | 0 | 0 | 0 | 182
23-0090782 | Kings | AVENAL 2101 | AVENAL 21019070 | 3rd Party | 2023-07-11 10:29 | 7/11 - 7/17 | 2023-07-11 23:08 | 141.2206 | FTS | 9603 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 759
23-0090767 | Santa Cruz | BURNS 2101 | BURNS 2101CB | Vegetation | 2023-07-11 10:08 | 7/11 - 7/17 | 2023-07-12 02:21 | 208.6612 | FTS | 1691616 | 8107 | 314 | 248 | 69 | 4 | 0 | 2 | 973
23-0091001 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110656026 | Equipment Failure/Involved | 2023-07-11 16:57 | 7/11 - 7/17 | 2023-07-12 04:14 | 174.3333 | FTS | 40794 | 234 | 21 | 13 | 2 | 0 | 0 | 0 | 677
23-0091044 | Monterey | JOLON 1102 | JOLON 11027002 | Equipment Failure/Involved | 2023-07-11 21:42 | 7/11 - 7/17 | 2023-07-12 04:46 | 272.8986 | FTS | 37660 | 138 | 9 | 7 | 3 | 2 | 0 | 3 | 424
23-0091081 | Contra Costa | TASSAJARA 2113 | TASSAJARA 2113MR276 | Animal | 2023-07-12 01:21 | 7/11 - 7/17 | 2023-07-12 05:37 | 256 | FTS | 138752 | 542 | 45 | 36 | 15 | 0 | 0 | 2 | 256
23-0091142 | Shasta | VOLTA 1102 | VOLTA 11021502 | Company Initiated | 2023-07-12 08:05 | 7/11 - 7/17 | 2023-07-12 09:14 | 69 | FTS | 97635 | 1415 | 150 | 122 | 14 | 0 | 0 | 0 | 69
23-0091131 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101518 | Vegetation | 2023-07-12 07:51 | 7/11 - 7/17 | 2023-07-12 10:25 | 154 | FTS | 14630 | 95 | 7 | 6 | 6 | 1 | 0 | 0 | 154
23-0091089 | Sonoma | MONTE RIO 1113 | MONTE RIO 11133970 | Unknown Cause | 2023-07-12 05:11 | 7/11 - 7/17 | 2023-07-12 12:48 | 207.79 | FTS | 534436 | 2572 | 156 | 100 | 45 | 6 | 0 | 0 | 457
23-0091160 | Calaveras | Valley Springs 1101 | Valley Springs 110111158 | Unknown Cause | 2023-07-12 08:24 | 7/11 - 7/17 | 2023-07-12 12:56 | 170.3578 | FTS | 69506 | 408 | 30 | 18 | 12 | 0 | 0 | 3 | 272
23-0091102 | Placer | FORESTHILL 1101 | FORESTHILL 110150486 | Animal | 2023-07-12 06:34 | 7/11 - 7/17 | 2023-07-12 13:41 | 147.213 | FTS | 135436 | 920 | 102 | 68 | 10 | 0 | 0 | 0 | 427
23-0091158 | Monterey | JOLON 1102 | JOLON 1102CB | 3rd Party | 2023-07-12 08:27 | 7/11 - 7/17 | 2023-07-12 13:42 | 247.4323 | FTS | 149944 | 606 | 24 | 18 | 24 | 2 | 0 | 7 | 315
23-0091326 | Napa | SILVERADO 2104 | SILVERADO 2104209359 | Unknown Cause | 2023-07-12 11:00 | 7/11 - 7/17 | 2023-07-12 13:53 | 173 | FTS | 346 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 173
23-0091202 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | 3rd Party | 2023-07-12 09:30 | 7/11 - 7/17 | 2023-07-12 14:26 | 144.264 | FTS | 121326 | 841 | 68 | 39 | 11 | 0 | 0 | 3 | 296
23-0091353 | Placer | HALSEY 1101 | HALSEY 11011704 | Unknown Cause | 2023-07-12 12:59 | 7/11 - 7/17 | 2023-07-12 14:55 | 81.8831 | FTS | 37830 | 462 | 42 | 31 | 5 | 1 | 0 | 2 | 116
23-0091316 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105CB | 3rd Party | 2023-07-12 11:57 | 7/11 - 7/17 | 2023-07-12 15:33 | 153.7148 | FTS | 573510 | 3731 | 351 | 291 | 52 | 5 | 0 | 7 | 216
23-0091345 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110990 | Unknown Cause | 2023-07-12 12:47 | 7/11 - 7/17 | 2023-07-12 16:08 | 201 | FTS | 105525 | 525 | 53 | 45 | 4 | 0 | 0 | 0 | 201
23-0091398 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Animal | 2023-07-12 14:29 | 7/11 - 7/17 | 2023-07-12 16:17 | 108 | FTS | 33156 | 307 | 19 | 17 | 10 | 5 | 0 | 0 | 108
23-0091441 | Santa Clara | MENLO 1103 | MENLO 1103866118 | Vegetation | 2023-07-12 15:11 | 7/11 - 7/17 | 2023-07-12 16:32 | 81 | FTS | 12717 | 157 | 9 | 7 | 2 | 0 | 0 | 0 | 81
23-0091274 | Nevada | BRUNSWICK 1103 | BRUNSWICK 11032784 | Vegetation | 2023-07-12 10:47 | 7/11 - 7/17 | 2023-07-12 17:22 | 49.5406 | FTS | 63412 | 1280 | 80 | 48 | 12 | 1 | 0 | 5 | 395
23-0091515 | Yolo | MADISON 2101 | MADISON 2101760730 | Unknown Cause | 2023-07-12 19:02 | 7/11 - 7/17 | 2023-07-12 21:07 | 125 | FTS | 2125 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 125
23-0091514 | Placer | WISE 1102 | WISE 1102697216 | Animal | 2023-07-12 18:54 | 7/11 - 7/17 | 2023-07-12 21:20 | 146 | FTS | 32266 | 221 | 19 | 14 | 0 | 0 | 0 | 4 | 146
23-0091333 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-07-12 12:33 | 7/11 - 7/17 | 2023-07-13 00:40 | 726.9474 | FTS | 41436 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 727
23-0091479 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210611006 | Vegetation | 2023-07-12 16:40 | 7/11 - 7/17 | 2023-07-13 01:41 | 179.3269 | FTS | 18650 | 104 | 9 | 8 | 2 | 0 | 0 | 0 | 541
23-0091445 | Santa Clara | MENLO 1103 | MENLO 1103866118 | Vegetation | 2023-07-12 15:13 | 7/11 - 7/17 | 2023-07-13 05:51 | 311.8185 | FTS | 91051 | 292 | 13 | 10 | 17 | 0 | 0 | 7 | 878
23-0091589 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Company Initiated | 2023-07-13 04:58 | 7/11 - 7/17 | 2023-07-13 06:49 | 111 | FTS | 99345 | 895 | 62 | 41 | 16 | 0 | 0 | 0 | 111
23-0091651 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103258688 | Unknown Cause | 2023-07-13 08:21 | 7/11 - 7/17 | 2023-07-13 09:09 | 48 | FTS | 624 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 48
23-0091586 | Amador | CLAY 1103 | CLAY 11037142 | Animal | 2023-07-13 02:42 | 7/11 - 7/17 | 2023-07-13 10:06 | 444 | FTS | 35964 | 81 | 0 | 0 | 5 | 0 | 0 | 0 | 444
23-0091592 | Yuba | SMARTVILLE 1101 | SMARTVILLE 1101CB | Unknown Cause | 2023-07-13 05:29 | 7/11 - 7/17 | 2023-07-13 10:11 | 252.8416 | FTS | 142097 | 562 | 46 | 34 | 13 | 0 | 0 | 5 | 282
23-0091647 | Tehama | RED BLUFF 1103 | RED BLUFF 11031702 | Animal | 2023-07-13 08:17 | 7/11 - 7/17 | 2023-07-13 11:34 | 197 | FTS | 42946 | 218 | 22 | 16 | 0 | 0 | 0 | 3 | 197
23-0091587 | Monterey | SAN ARDO 1102 | SAN ARDO 11027030 | Unknown Cause | 2023-07-13 02:48 | 7/11 - 7/17 | 2023-07-13 12:01 | 553 | FTS | 58618 | 106 | 1 | 0 | 8 | 0 | 0 | 0 | 553
23-0091904 | Lake | HARTLEY 1102 | HARTLEY 1102841676 | Equipment Failure/Involved | 2023-07-13 13:55 | 7/11 - 7/17 | 2023-07-13 15:25 | 90 | FTS | 82980 | 922 | 95 | 73 | 10 | 0 | 0 | 0 | 90
23-0091811 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-07-13 12:07 | 7/11 - 7/17 | 2023-07-13 15:45 | 171.0656 | FTS | 354448 | 2072 | 120 | 81 | 16 | 6 | 0 | 0 | 218
23-0091869 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Equipment Failure/Involved | 2023-07-13 13:14 | 7/11 - 7/17 | 2023-07-13 17:45 | 263.3457 | FTS | 761069 | 2890 | 234 | 170 | 26 | 1 | 0 | 1 | 271
23-0092030 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Company Initiated | 2023-07-13 17:26 | 7/11 - 7/17 | 2023-07-13 18:01 | 35 | FTS | 31325 | 895 | 62 | 41 | 16 | 0 | 0 | 0 | 35
23-0092055 | Lake | REDBUD 1101 | REDBUD 1101558812 | Company Initiated | 2023-07-13 19:55 | 7/11 - 7/17 | 2023-07-13 20:22 | 27 | FTS | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 27
23-0092063 | Placer | PENRYN 1107 | PENRYN 11072706 | Vegetation | 2023-07-13 20:48 | 7/11 - 7/17 | 2023-07-13 22:07 | 79 | FTS | 29546 | 374 | 29 | 22 | 5 | 1 | 0 | 4 | 79
23-0092001 | Nevada | HIGGINS 1110 | HIGGINS 1110861610 | 3rd Party | 2023-07-13 16:21 | 7/11 - 7/17 | 2023-07-14 06:02 | 174.2204 | FTS | 210284 | 1207 | 108 | 72 | 12 | 0 | 0 | 7 | 821
23-0092064 | Mendocino | POINT ARENA 1101 | POINT ARENA 1101476 | Unknown Cause | 2023-07-13 20:58 | 7/11 - 7/17 | 2023-07-14 07:36 | 138.9961 | FTS | 35444 | 255 | 12 | 8 | 9 | 1 | 0 | 0 | 638
23-0092141 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-07-14 07:22 | 7/11 - 7/17 | 2023-07-14 09:07 | 85.444 | FTS | 177040 | 2072 | 120 | 81 | 16 | 6 | 0 | 0 | 105
23-0092125 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 110139524 | Vegetation | 2023-07-14 04:30 | 7/11 - 7/17 | 2023-07-14 10:29 | 104.0413 | FTS | 52957 | 509 | 8 | 7 | 12 | 0 | 0 | 0 | 359
23-0092082 | Lake | REDBUD 1101 | REDBUD 1101558812 | Unknown Cause | 2023-07-13 21:57 | 7/11 - 7/17 | 2023-07-14 11:18 | 801 | FTS | 6408 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 801
23-0092123 | Santa Clara | PIERCY 2110 | PIERCY 2110XR258 | Unknown Cause | 2023-07-14 02:30 | 7/11 - 7/17 | 2023-07-14 12:29 | 156.3865 | FTS | 115726 | 740 | 33 | 21 | 12 | 0 | 0 | 0 | 599
23-0092298 | Tehama | RED BLUFF 1101 | RED BLUFF 11011556 | Animal | 2023-07-14 11:11 | 7/11 - 7/17 | 2023-07-14 12:41 | 90 | FTS | 43200 | 480 | 54 | 37 | 3 | 0 | 0 | 0 | 90
23-0092204 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101548 | Unknown Cause | 2023-07-14 09:04 | 7/11 - 7/17 | 2023-07-14 13:09 | 228.9827 | FTS | 212267 | 927 | 40 | 29 | 17 | 1 | 0 | 0 | 245
23-0091830 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-07-13 12:27 | 7/11 - 7/17 | 2023-07-14 13:23 | 1124.9123 | FTS | 64120 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 1496
23-0092363 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101644756 | Unknown Cause | 2023-07-14 12:21 | 7/11 - 7/17 | 2023-07-14 14:41 | 140 | FTS | 2240 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 140
23-0092174 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Unknown Cause | 2023-07-14 08:12 | 7/11 - 7/17 | 2023-07-14 16:28 | 332.3864 | FTS | 691696 | 2081 | 178 | 137 | 32 | 2 | 0 | 2 | 496
23-0092263 | Mendocino | POINT ARENA 1101 | POINT ARENA 1101476 | Vegetation | 2023-07-14 10:19 | 7/11 - 7/17 | 2023-07-14 16:41 | 70.9922 | FTS | 18103 | 255 | 12 | 8 | 9 | 1 | 0 | 0 | 382
23-0092127 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101454176 | Vegetation | 2023-07-14 05:12 | 7/11 - 7/17 | 2023-07-14 17:40 | 89.9038 | HLT | 4675 | 52 | 1 | 1 | 0 | 0 | 0 | 0 | 748
23-0092357 | Monterey | SOLEDAD 2101 | SOLEDAD 21017048 | 3rd Party | 2023-07-14 12:54 | 7/11 - 7/17 | 2023-07-14 20:42 | 367.5607 | FTS | 63588 | 173 | 2 | 2 | 2 | 0 | 0 | 0 | 468
23-0092362 | San Benito | LOS OSITOS 2103 | LOS OSITOS 21033010 | Unknown Cause | 2023-07-14 13:04 | 7/11 - 7/17 | 2023-07-14 21:33 | 421.6796 | FTS | 196081 | 465 | 9 | 5 | 7 | 0 | 0 | 0 | 509
23-0092487 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Company Initiated | 2023-07-14 21:27 | 7/11 - 7/17 | 2023-07-14 21:58 | 31 | FTS | 27745 | 895 | 62 | 41 | 16 | 0 | 0 | 0 | 31
23-0092483 | Amador | CLAY 1102 | CLAY 1102CB | 3rd Party | 2023-07-14 20:45 | 7/11 - 7/17 | 2023-07-15 00:08 | 121.6667 | FTS | 365 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 203
23-0092166 | Lassen | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Equipment Failure/Involved | 2023-07-14 08:01 | 7/11 - 7/17 | 2023-07-15 04:22 | 355.0697 | FTS | 86637 | 244 | 18 | 15 | 3 | 0 | 0 | 0 | 1221
23-0092517 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 11062100 | Unknown Cause | 2023-07-15 00:38 | 7/11 - 7/17 | 2023-07-15 05:57 | 292.302 | FTS | 348424 | 1192 | 110 | 79 | 12 | 0 | 0 | 20 | 319
23-0092510 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 11021584 | Unknown Cause | 2023-07-14 23:06 | 7/11 - 7/17 | 2023-07-15 07:33 | 351.9641 | FTS | 88343 | 251 | 32 | 27 | 3 | 0 | 0 | 0 | 507
23-0092519 | Napa | PUEBLO 2104 | PUEBLO 2102656 | Unknown Cause | 2023-07-15 00:20 | 7/11 - 7/17 | 2023-07-15 08:32 | 480.4038 | FTS | 99924 | 208 | 4 | 2 | 9 | 0 | 0 | 0 | 492
23-0092537 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101CB | Animal | 2023-07-15 06:22 | 7/11 - 7/17 | 2023-07-15 09:32 | 111.7107 | FTS | 518896 | 4645 | 445 | 309 | 99 | 11 | 0 | 17 | 190
23-0092438 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212992 | Vegetation | 2023-07-14 16:00 | 7/11 - 7/17 | 2023-07-15 10:11 | 362.1499 | FTS | 299498 | 827 | 58 | 43 | 14 | 1 | 0 | 1 | 1091
23-0092524 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A20 | 3rd Party | 2023-07-15 02:11 | 7/11 - 7/17 | 2023-07-15 10:33 | 158.7013 | FTS | 497370 | 3134 | 183 | 139 | 50 | 2 | 1 | 20 | 502
23-0092531 | Sonoma | MOLINO 1102 | MOLINO 1102104 | Vegetation | 2023-07-15 03:41 | 7/11 - 7/17 | 2023-07-15 11:59 | 144.5111 | FTS | 221391 | 1532 | 90 | 58 | 21 | 1 | 0 | 15 | 498
23-0092550 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108MR190 | Unknown Cause | 2023-07-15 08:38 | 7/11 - 7/17 | 2023-07-15 15:43 | 254.2209 | FTS | 476410 | 1874 | 94 | 71 | 28 | 0 | 2 | 0 | 425
23-0092532 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | Vegetation | 2023-07-15 04:34 | 7/11 - 7/17 | 2023-07-15 16:02 | 263.4275 | FTS | 101683 | 386 | 27 | 18 | 10 | 0 | 0 | 0 | 688
23-0092542 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V46 | Vegetation | 2023-07-15 07:55 | 7/11 - 7/17 | 2023-07-15 16:35 | 237.1889 | FTS | 51470 | 217 | 4 | 4 | 10 | 0 | 0 | 0 | 520
23-0092632 | Yuba | CHALLENGE 1102 | CHALLENGE 11021064 | Equipment Failure/Involved | 2023-07-15 13:53 | 7/11 - 7/17 | 2023-07-15 18:51 | 177.5455 | FTS | 35154 | 198 | 15 | 11 | 0 | 0 | 0 | 0 | 298
23-0092672 | Humboldt | MAPLE CREEK 1101 | MAPLE CREEK 11016906 | Equipment Failure/Involved | 2023-07-15 16:51 | 7/11 - 7/17 | 2023-07-16 03:16 | 553.9541 | FTS | 60381 | 109 | 7 | 5 | 16 | 2 | 0 | 2 | 625
23-0092683 | Alameda | CAYETANO 2109 | CAYETANO 2109MR572 | Equipment Failure/Involved | 2023-07-15 17:27 | 7/11 - 7/17 | 2023-07-16 05:46 | 203.513 | FTS | 641066 | 3150 | 178 | 122 | 46 | 8 | 0 | 2 | 739
23-0092696 | Kern | CUYAMA 2102 | CUYAMA 21021000 | Unknown Cause | 2023-07-15 18:16 | 7/11 - 7/17 | 2023-07-16 08:52 | 876 | FTS | 18396 | 21 | 0 | 0 | 2 | 0 | 0 | 0 | 876
23-0092785 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Animal | 2023-07-16 09:43 | 7/11 - 7/17 | 2023-07-16 11:02 | 76.2467 | FTS | 142810 | 1873 | 144 | 103 | 19 | 1 | 0 | 4 | 79
23-0092767 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Company Initiated | 2023-07-16 10:31 | 7/11 - 7/17 | 2023-07-16 11:24 | 36.6987 | FTS | 106096 | 2891 | 234 | 170 | 26 | 1 | 0 | 1 | 53
23-0092713 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Equipment Failure/Involved | 2023-07-15 19:56 | 7/11 - 7/17 | 2023-07-16 11:52 | 675.5662 | FTS | 703940 | 1042 | 83 | 61 | 18 | 5 | 0 | 2 | 956
23-0092775 | Nevada | HIGGINS 1110 | HIGGINS 1110166282 | Equipment Failure/Involved | 2023-07-16 07:46 | 7/11 - 7/17 | 2023-07-16 12:04 | 258 | FTS | 84882 | 329 | 29 | 18 | 4 | 0 | 0 | 6 | 258
23-0092750 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105922576 | Vegetation | 2023-07-16 01:13 | 7/11 - 7/17 | 2023-07-16 13:10 | 286.6895 | FTS | 87727 | 306 | 31 | 23 | 7 | 0 | 0 | 0 | 717
23-0092746 | Amador | PINE GROVE 1102 | PINE GROVE 110235576 | Vegetation | 2023-07-15 22:49 | 7/11 - 7/17 | 2023-07-16 13:10 | 672.3067 | FTS | 50423 | 75 | 10 | 9 | 1 | 0 | 0 | 0 | 861
23-0092764 | Fresno | AUBERRY 1102 | AUBERRY 110237466 | Animal | 2023-07-16 06:20 | 7/11 - 7/17 | 2023-07-16 13:27 | 162.7868 | FTS | 71789 | 441 | 47 | 33 | 2 | 0 | 0 | 1 | 427
23-0092822 | San Mateo | HALF MOON BAY 1101 | HALF MOON BAY 1101CB | 3rd Party | 2023-07-16 13:22 | 7/11 - 7/17 | 2023-07-16 14:48 | 86 | FTS | 226782 | 2637 | 89 | 70 | 64 | 6 | 0 | 1 | 86
23-0092811 | Merced | ORO LOMA 1106 | ORO LOMA 11063650 | Unknown Cause | 2023-07-16 12:11 | 7/11 - 7/17 | 2023-07-16 14:52 | 104.2153 | FTS | 21781 | 209 | 0 | 0 | 7 | 0 | 0 | 0 | 161
23-0092885 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011750 | Vegetation | 2023-07-16 17:00 | 7/11 - 7/17 | 2023-07-16 18:19 | 79 | FTS | 7268 | 92 | 2 | 1 | 2 | 0 | 0 | 0 | 79
23-0092851 | Humboldt | WILLOW CREEK 1101 | WILLOW CREEK 11015002 | Unknown Cause | 2023-07-16 16:13 | 7/11 - 7/17 | 2023-07-16 19:13 | 156.3832 | FTS | 93048 | 595 | 29 | 21 | 5 | 0 | 1 | 0 | 180
23-0092875 | Contra Costa | SOBRANTE 1103 | SOBRANTE 11033342 | Company Initiated | 2023-07-16 17:41 | 7/11 - 7/17 | 2023-07-16 19:31 | 49.8248 | FTS | 21325 | 428 | 29 | 23 | 4 | 0 | 0 | 0 | 110
23-0092890 | Contra Costa | SOBRANTE 1101 | SOBRANTE 1101CB | Unknown Cause | 2023-07-16 17:41 | 7/11 - 7/17 | 2023-07-16 19:46 | 125 | FTS | 45625 | 365 | 25 | 20 | 7 | 1 | 0 | 1 | 125
23-0092869 | Tehama | PANORAMA 1101 | PANORAMA 1101713592 | Equipment Failure/Involved | 2023-07-16 16:56 | 7/11 - 7/17 | 2023-07-16 20:08 | 48.0358 | FTS | 124749 | 2597 | 123 | 85 | 12 | 0 | 0 | 0 | 192
23-0092896 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 21035402 | Vegetation | 2023-07-16 18:52 | 7/11 - 7/17 | 2023-07-16 20:17 | 85 | FTS | 80920 | 952 | 76 | 52 | 10 | 0 | 0 | 3 | 85
23-0092876 | Contra Costa | SOBRANTE 1103 | MORAGA 1102161484 | Unknown Cause | 2023-07-16 17:42 | 7/11 - 7/17 | 2023-07-16 20:48 | 186 | FTS | 67518 | 363 | 27 | 18 | 3 | 0 | 0 | 0 | 186
23-0092779 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21011703 | 3rd Party | 2023-07-16 08:42 | 7/11 - 7/17 | 2023-07-16 21:36 | 774 | FTS | 774 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 774
23-0092903 | Contra Costa | LAKEWOOD 2224 | LAKEWOOD 2224568670 | Unknown Cause | 2023-07-16 19:14 | 7/11 - 7/17 | 2023-07-17 01:09 | 139.2415 | FTS | 44975 | 323 | 24 | 16 | 10 | 4 | 0 | 0 | 355
23-0092967 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 2108294550 | Unknown Cause | 2023-07-16 23:58 | 7/11 - 7/17 | 2023-07-17 02:36 | 158 | FTS | 161950 | 1025 | 104 | 76 | 8 | 1 | 0 | 0 | 158
23-0092918 | Shasta | COTTONWOOD 1102 | COTTONWOOD 11021578 | Equipment Failure/Involved | 2023-07-16 20:19 | 7/11 - 7/17 | 2023-07-17 03:19 | 387.4335 | FTS | 101895 | 263 | 37 | 29 | 2 | 0 | 0 | 1 | 420
23-0092844 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Vegetation | 2023-07-16 15:30 | 7/11 - 7/17 | 2023-07-17 04:20 | 116.2733 | FTS | 58718 | 505 | 29 | 21 | 11 | 0 | 0 | 2 | 770
23-0092894 | Fresno | SAND CREEK 1103 | SAND CREEK 1103818064 | Equipment Failure/Involved | 2023-07-16 18:41 | 7/11 - 7/17 | 2023-07-17 05:32 | 280.3827 | FTS | 145799 | 520 | 57 | 37 | 5 | 0 | 0 | 0 | 651
23-0092848 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104905960 | Equipment Failure/Involved | 2023-07-16 16:06 | 7/11 - 7/17 | 2023-07-17 07:42 | 219.2718 | FTS | 576904 | 2631 | 308 | 223 | 59 | 8 | 0 | 0 | 936
23-0092989 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 11011302 | Animal | 2023-07-17 06:40 | 7/11 - 7/17 | 2023-07-17 08:12 | 92 | FTS | 48484 | 527 | 39 | 25 | 8 | 0 | 1 | 0 | 92
23-0093022 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 1104Y04 | Company Initiated | 2023-07-17 08:03 | 7/11 - 7/17 | 2023-07-17 08:14 | 11 | FTS | 4884 | 444 | 8 | 3 | 7 | 2 | 0 | 0 | 11
23-0092984 | Monterey | JOLON 1103 | JOLON 1103CB | Unknown Cause | 2023-07-17 06:07 | 7/11 - 7/17 | 2023-07-17 09:27 | 200 | FTS | 4000 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 200
23-0092919 | Merced | GUSTINE 1102 | GUSTINE 11029100 | Equipment Failure/Involved | 2023-07-16 20:13 | 7/11 - 7/17 | 2023-07-17 09:50 | 149.3444 | FTS | 98866 | 662 | 16 | 13 | 13 | 0 | 0 | 0 | 817
23-0092902 | Monterey | OILFIELDS 1102 | OILFIELDS 110241992 | Vegetation | 2023-07-16 19:13 | 7/11 - 7/17 | 2023-07-17 09:57 | 884 | FTS | 40664 | 46 | 1 | 0 | 1 | 0 | 0 | 0 | 884
23-0093074 | San Mateo | RALSTON 1102 | RALSTON 1102CB | 3rd Party | 2023-07-17 09:31 | 7/11 - 7/17 | 2023-07-17 10:21 | 50 | FTS | 5800 | 116 | 4 | 4 | 0 | 0 | 0 | 0 | 50
23-0092981 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Animal | 2023-07-17 05:55 | 7/11 - 7/17 | 2023-07-17 10:26 | 235.1382 | FTS | 245014 | 1042 | 83 | 61 | 18 | 5 | 0 | 2 | 271
23-0093139 | Santa Clara | MILPITAS 1109 | MILPITAS 1109XR374 | Animal | 2023-07-17 10:44 | 7/11 - 7/17 | 2023-07-17 12:14 | 90 | FTS | 1350 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 90
23-0093131 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Equipment Failure/Involved | 2023-07-17 08:43 | 7/11 - 7/17 | 2023-07-17 12:48 | 233.7601 | FTS | 484351 | 2072 | 177 | 136 | 32 | 2 | 0 | 2 | 245
23-0093144 | San Mateo | RALSTON 1102 | RALSTON 1102CB | 3rd Party | 2023-07-17 11:52 | 7/11 - 7/17 | 2023-07-17 13:02 | 70 | FTS | 8120 | 116 | 4 | 4 | 0 | 0 | 0 | 0 | 70
23-0093171 | Santa Cruz | BEN LOMOND 1101 | BEN LOMOND 1101BL 1101 | Unknown Cause | 2023-07-17 12:28 | 7/11 - 7/17 | 2023-07-17 13:52 | 65.0323 | FTS | 48384 | 744 | 52 | 42 | 12 | 0 | 0 | 0 | 84
23-0092911 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110560528 | 3rd Party | 2023-07-16 19:41 | 7/11 - 7/17 | 2023-07-17 14:36 | 190.2562 | FTS | 360155 | 1893 | 108 | 73 | 28 | 2 | 0 | 2 | 1135
23-0093265 | Tehama | CORNING 1102 | CORNING 11021900 | Company Initiated | 2023-07-17 14:23 | 7/11 - 7/17 | 2023-07-17 14:40 | 17 | FTS | 5219 | 307 | 18 | 13 | 10 | 3 | 0 | 1 | 17
23-0093241 | Yuba | CHALLENGE 1101 | CHALLENGE 11015460 | Company Initiated | 2023-07-17 13:46 | 7/11 - 7/17 | 2023-07-17 15:11 | 85 | FTS | 8415 | 99 | 6 | 3 | 3 | 0 | 0 | 0 | 85
23-0093110 | Contra Costa | MEADOW LANE 2106 | MEADOW LANE 2106C558R | 3rd Party | 2023-07-17 10:31 | 7/11 - 7/17 | 2023-07-17 15:39 | 84.1775 | FTS | 250428 | 2975 | 219 | 157 | 31 | 6 | 0 | 0 | 308
23-0093173 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Unknown Cause | 2023-07-17 12:28 | 7/11 - 7/17 | 2023-07-17 16:07 | 219 | FTS | 125925 | 575 | 35 | 17 | 5 | 0 | 0 | 0 | 219
23-0093130 | Sonoma | MONTE RIO 1113 | MONTE RIO 11133970 | Unknown Cause | 2023-07-17 11:29 | 7/11 - 7/17 | 2023-07-17 16:15 | 195.4347 | FTS | 502658 | 2572 | 156 | 100 | 45 | 6 | 0 | 0 | 286
23-0093282 | Sonoma | COTATI 1105 | COTATI 1105328 | Animal | 2023-07-17 14:45 | 7/18 - 7/24 | 2023-07-17 17:49 | 111.1464 | FTS | 110813 | 997 | 57 | 40 | 11 | 1 | 0 | 1 | 184
23-0093142 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110990 | Equipment Failure/Involved | 2023-07-17 11:46 | 7/18 - 7/24 | 2023-07-17 19:02 | 213.6565 | FTS | 111956 | 524 | 53 | 45 | 4 | 0 | 0 | 0 | 436
23-0093386 | Monterey | DEL MONTE 2104 | DEL MONTE 21042762 | Vegetation | 2023-07-17 17:27 | 7/18 - 7/24 | 2023-07-17 19:18 | 110.8024 | FTS | 46537 | 420 | 22 | 15 | 5 | 1 | 0 | 0 | 111
23-0093228 | Sonoma | SONOMA 1105 | SONOMA 1105138 | Vegetation | 2023-07-17 13:42 | 7/18 - 7/24 | 2023-07-17 23:18 | 91.9487 | FTS | 64548 | 702 | 30 | 21 | 6 | 0 | 0 | 8 | 576
23-0093224 | Humboldt | RIO DELL 1101 | RIO DELL 11018768 | Vegetation | 2023-07-17 13:40 | 7/18 - 7/24 | 2023-07-18 03:41 | 742.5168 | FTS | 508624 | 685 | 22 | 16 | 15 | 1 | 0 | 0 | 841
23-0093483 | Butte | NOTRE DAME 1103 | NOTRE DAME 1103317782 | Equipment Failure/Involved | 2023-07-18 05:00 | 7/18 - 7/24 | 2023-07-18 06:48 | 108 | FTS | 12204 | 113 | 7 | 4 | 9 | 0 | 0 | 0 | 108
23-0093519 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Company Initiated | 2023-07-18 07:25 | 7/18 - 7/24 | 2023-07-18 08:54 | 87.1448 | HLT | 134813 | 1547 | 223 | 168 | 24 | 0 | 0 | 1 | 89
23-0093542 | Mendocino | PHILO 1102 | PHILO 1102920 | Company Initiated | 2023-07-18 08:18 | 7/18 - 7/24 | 2023-07-18 08:54 | 36 | FTS | 24012 | 667 | 18 | 12 | 13 | 1 | 0 | 1 | 36
23-0093413 | Solano | JAMESON 1105 | JAMESON 110560052 | Equipment Failure/Involved | 2023-07-17 17:50 | 7/18 - 7/24 | 2023-07-18 09:00 | 355.5616 | FTS | 51912 | 146 | 7 | 5 | 1 | 0 | 0 | 2 | 910
23-0093417 | Tulare | OROSI 1102 | OROSI 1102CB | Unknown Cause | 2023-07-17 19:55 | 7/18 - 7/24 | 2023-07-18 10:01 | 301.8355 | FTS | 113792 | 377 | 6 | 5 | 1 | 0 | 0 | 0 | 846
23-0093561 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102654084 | Unknown Cause | 2023-07-18 08:48 | 7/18 - 7/24 | 2023-07-18 10:10 | 82 | HLT | 246 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 82
23-0093447 | Placer | PENRYN 1107 | PENRYN 11072410 | Vegetation | 2023-07-17 22:08 | 7/18 - 7/24 | 2023-07-18 10:24 | 90.7299 | FTS | 15787 | 174 | 8 | 4 | 4 | 1 | 0 | 0 | 736
23-0093560 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Unknown Cause | 2023-07-18 08:51 | 7/18 - 7/24 | 2023-07-18 10:52 | 98.5641 | FTS | 49972 | 507 | 55 | 32 | 4 | 0 | 0 | 3 | 121
23-0093623 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 21055232 | Unknown Cause | 2023-07-18 10:52 | 7/18 - 7/24 | 2023-07-18 12:07 | 75 | FTS | 59100 | 788 | 70 | 55 | 11 | 0 | 0 | 6 | 75
23-0093703 | Mendocino | PHILO 1102 | PHILO 1102920 | Company Initiated | 2023-07-18 12:17 | 7/18 - 7/24 | 2023-07-18 12:32 | 15 | FTS | 10005 | 667 | 18 | 12 | 13 | 1 | 0 | 1 | 15
23-0093588 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101829164 | Unknown Cause | 2023-07-18 09:38 | 7/18 - 7/24 | 2023-07-18 14:47 | 242.2669 | FTS | 510214 | 2106 | 98 | 69 | 37 | 7 | 0 | 5 | 309
23-0093938 | Napa | SILVERADO 2102 | SILVERADO 210298998 | Animal | 2023-07-18 19:37 | 7/18 - 7/24 | 2023-07-18 22:40 | 48.9863 | FTS | 17929 | 366 | 3 | 1 | 8 | 0 | 0 | 0 | 183
23-0093982 | Lake | HIGHLANDS 1104 | HIGHLANDS 110448262 | Unknown Cause | 2023-07-18 22:55 | 7/18 - 7/24 | 2023-07-19 00:45 | 110 | FTS | 48510 | 441 | 48 | 33 | 3 | 0 | 0 | 0 | 110
23-0093593 | Butte | WYANDOTTE 1107 | WYANDOTTE 11071026 | Vegetation | 2023-07-18 09:52 | 7/18 - 7/24 | 2023-07-19 00:58 | 195.931 | FTS | 56820 | 290 | 27 | 23 | 3 | 0 | 0 | 2 | 906
23-0093696 | San Mateo | BAY MEADOWS 2102 | BAY MEADOWS 210257886 | Equipment Failure/Involved | 2023-07-18 12:07 | 7/18 - 7/24 | 2023-07-19 02:28 | 107.3319 | FTS | 124505 | 1160 | 60 | 40 | 26 | 3 | 0 | 0 | 861
23-0093997 | Napa | MONTICELLO 1101 | MONTICELLO 110152910 | Animal | 2023-07-19 05:46 | 7/18 - 7/24 | 2023-07-19 07:51 | 125 | FTS | 34750 | 278 | 15 | 8 | 7 | 1 | 0 | 0 | 125
23-0093991 | Madera | COARSEGOLD 2103 | COARSEGOLD 21036110 | Unknown Cause | 2023-07-19 03:46 | 7/18 - 7/24 | 2023-07-19 08:27 | 234.2282 | FTS | 48251 | 206 | 11 | 7 | 33 | 4 | 0 | 0 | 281
23-0086272 | Amador | ELECTRA SUB | ELECTRA 11017104 | Company Initiated | 2023-07-19 07:44 | 7/18 - 7/24 | 2023-07-19 08:45 | 58.343 | FTS | 64294 | 1102 | 128 | 94 | 12 | 0 | 0 | 13 | 61
23-0094039 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062104 | Animal | 2023-07-19 07:45 | 7/18 - 7/24 | 2023-07-19 09:30 | 73.3246 | FTS | 156108 | 2129 | 163 | 123 | 19 | 3 | 0 | 14 | 105
23-0093992 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Animal | 2023-07-19 05:14 | 7/18 - 7/24 | 2023-07-19 09:45 | 271 | FTS | 331433 | 1223 | 114 | 91 | 17 | 3 | 0 | 4 | 271
23-0094032 | Sonoma | MONTE RIO 1111 | MONTE RIO 1111292 | Animal | 2023-07-19 07:41 | 7/18 - 7/24 | 2023-07-19 10:08 | 147 | FTS | 55860 | 380 | 12 | 10 | 8 | 0 | 0 | 2 | 147
23-0094149 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Company Initiated | 2023-07-19 10:20 | 7/18 - 7/24 | 2023-07-19 11:21 | 58.1427 | FTS | 48084 | 827 | 70 | 41 | 11 | 0 | 0 | 3 | 61
23-0094002 | Butte | ORO FINO 1101 | ORO FINO 11012022 | Animal | 2023-07-19 06:20 | 7/18 - 7/24 | 2023-07-19 12:49 | 85.5824 | FTS | 89348 | 1044 | 131 | 98 | 10 | 1 | 0 | 0 | 389
23-0093986 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A10 | Equipment Failure/Involved | 2023-07-19 00:23 | 7/18 - 7/24 | 2023-07-19 13:10 | 226.9805 | FTS | 93062 | 410 | 33 | 25 | 8 | 0 | 0 | 7 | 767
23-0094218 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 2101CB | Unknown Cause | 2023-07-19 12:22 | 7/18 - 7/24 | 2023-07-19 14:00 | 37.551 | FTS | 57115 | 1521 | 71 | 53 | 24 | 2 | 4 | 0 | 98
23-0094292 | Contra Costa | CLAYTON 2212 | CLAYTON 2212CB | Animal | 2023-07-19 14:09 | 7/18 - 7/24 | 2023-07-19 15:13 | 64 | FTS | 214464 | 3351 | 300 | 204 | 76 | 8 | 0 | 5 | 64
23-0094302 | Butte | ORO FINO 1102 | ORO FINO 110265932 | Vegetation | 2023-07-19 14:51 | 7/18 - 7/24 | 2023-07-19 16:38 | 106.5256 | FTS | 116539 | 1094 | 88 | 55 | 13 | 1 | 0 | 0 | 107
23-0094338 | Contra Costa | CLAYTON 2212 | CLAYTON 2212614950 | Company Initiated | 2023-07-19 14:09 | 7/18 - 7/24 | 2023-07-19 16:56 | 167 | FTS | 8016 | 48 | 4 | 3 | 0 | 0 | 0 | 0 | 167
23-0094197 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11028652 | Unknown Cause | 2023-07-19 11:56 | 7/18 - 7/24 | 2023-07-19 17:31 | 190.9055 | FTS | 48490 | 254 | 7 | 4 | 7 | 1 | 0 | 0 | 335
23-0094308 | Lake | REDBUD 1101 | REDBUD 1101754544 | Animal | 2023-07-19 14:55 | 7/18 - 7/24 | 2023-07-19 17:39 | 159.3918 | FTS | 89897 | 564 | 55 | 40 | 4 | 0 | 0 | 0 | 164
23-0093985 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103828 | Equipment Failure/Involved | 2023-07-18 23:25 | 7/18 - 7/24 | 2023-07-19 19:47 | 989.7166 | FTS | 1309395 | 1323 | 123 | 73 | 16 | 0 | 0 | 2 | 1222
23-0094402 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212124 | Vegetation | 2023-07-19 20:59 | 7/18 - 7/24 | 2023-07-19 21:54 | 55 | FTS | 26345 | 479 | 32 | 25 | 4 | 0 | 0 | 0 | 55
23-0094307 | Tuolumne | RACETRACK 1703 | RACETRACK 1703CB | 3rd Party | 2023-07-19 15:04 | 7/18 - 7/24 | 2023-07-19 22:42 | 105.3741 | FTS | 327292 | 3106 | 269 | 203 | 62 | 16 | 1 | 0 | 458
23-0094554 | Sonoma | PETALUMA C 1109 | PETALUMA C 1109857148 | Animal | 2023-07-20 08:43 | 7/18 - 7/24 | 2023-07-20 09:52 | 69 | FTS | 245709 | 3561 | 167 | 131 | 63 | 7 | 0 | 0 | 69
23-0094512 | Tehama | RED BLUFF 1101 | RED BLUFF 11011556 | Animal | 2023-07-20 07:10 | 7/18 - 7/24 | 2023-07-20 10:43 | 213 | FTS | 102240 | 480 | 54 | 37 | 3 | 0 | 0 | 0 | 213
23-0094586 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-07-20 09:57 | 7/18 - 7/24 | 2023-07-20 11:24 | 87 | FTS | 180264 | 2072 | 120 | 81 | 16 | 6 | 0 | 0 | 87
23-0094462 | Sonoma | DUNBAR 1102 | DUNBAR 1102448 | Vegetation | 2023-07-19 23:58 | 7/18 - 7/24 | 2023-07-20 12:54 | 403.459 | FTS | 246110 | 610 | 40 | 29 | 12 | 0 | 0 | 6 | 776
23-0094613 | Monterey | JOLON 1102 | JOLON 11027004 | Unknown Cause | 2023-07-20 10:49 | 7/18 - 7/24 | 2023-07-20 13:18 | 149 | FTS | 22201 | 149 | 5 | 4 | 9 | 0 | 0 | 3 | 149
23-0094762 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Unknown Cause | 2023-07-20 10:45 | 7/18 - 7/24 | 2023-07-20 13:57 | 192 | FTS | 3456 | 18 | 2 | 1 | 0 | 0 | 0 | 0 | 192
23-0094510 | Santa Clara | CAMP EVERS 2106 | CAMP EVERS 210660124 | Equipment Failure/Involved | 2023-07-20 07:01 | 7/18 - 7/24 | 2023-07-20 14:54 | 194.6145 | FTS | 88355 | 454 | 49 | 35 | 3 | 0 | 0 | 5 | 473
23-0094405 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown Cause | 2023-07-19 21:10 | 7/18 - 7/24 | 2023-07-20 14:59 | 796.212 | FTS | 664837 | 835 | 77 | 56 | 13 | 0 | 0 | 0 | 1069
23-0094737 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21011350 | Unknown Cause | 2023-07-20 13:15 | 7/18 - 7/24 | 2023-07-20 15:56 | 137.6299 | FTS | 118637 | 862 | 77 | 53 | 10 | 1 | 0 | 2 | 161
23-0094745 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Unknown Cause | 2023-07-20 13:25 | 7/18 - 7/24 | 2023-07-20 16:06 | 161 | FTS | 92414 | 574 | 35 | 17 | 5 | 0 | 0 | 0 | 161
23-0094725 | Contra Costa | MORAGA 1101 | MORAGA 1101772406 | Equipment Failure/Involved | 2023-07-20 12:45 | 7/18 - 7/24 | 2023-07-20 16:11 | 176.3345 | FTS | 51666 | 293 | 13 | 10 | 2 | 0 | 0 | 0 | 206
23-0094816 | Nevada | GRASS VALLEY 1101 | GRASS VALLEY 1101CB | Unknown Cause | 2023-07-20 14:43 | 7/18 - 7/24 | 2023-07-20 16:26 | 103 | FTS | 109077 | 1059 | 64 | 52 | 19 | 3 | 0 | 2 | 103
23-0094463 | Santa Barbara | SISQUOC 1101 | PALMER 1101M88 | Equipment Failure/Involved | 2023-07-20 00:24 | 7/18 - 7/24 | 2023-07-20 17:46 | 680.5128 | FTS | 26540 | 39 | 0 | 0 | 1 | 0 | 0 | 0 | 1042
23-0094485 | San Luis Obispo | SANTA MARIA 1108 | SANTA MARIA 1108M80 | Equipment Failure/Involved | 2023-07-20 03:19 | 7/18 - 7/24 | 2023-07-20 20:25 | 844.7101 | FTS | 375896 | 445 | 15 | 14 | 4 | 0 | 0 | 4 | 1026
23-0094720 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | 3rd Party | 2023-07-20 12:57 | 7/18 - 7/24 | 2023-07-20 21:48 | 75.8803 | FTS | 39306 | 518 | 34 | 21 | 14 | 4 | 0 | 7 | 531
23-0095000 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-07-21 04:13 | 7/18 - 7/24 | 2023-07-21 05:48 | 95 | FTS | 196840 | 2072 | 120 | 81 | 16 | 6 | 0 | 0 | 95
23-0094901 | Calaveras | PEORIA 1704 | PEORIA 170411232 | 3rd Party | 2023-07-20 18:28 | 7/18 - 7/24 | 2023-07-21 06:23 | 203.025 | FTS | 260075 | 1281 | 139 | 99 | 12 | 0 | 0 | 0 | 715
23-0095074 | Yuba | BANGOR 1101 | BANGOR 11011958 | Company Initiated | 2023-07-21 09:03 | 7/18 - 7/24 | 2023-07-21 09:33 | 30 | FTS | 11370 | 379 | 46 | 32 | 2 | 0 | 0 | 3 | 30
23-0095024 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 1104Y04 | Company Initiated | 2023-07-21 07:32 | 7/18 - 7/24 | 2023-07-21 09:38 | 126 | FTS | 102690 | 815 | 11 | 6 | 35 | 2 | 0 | 0 | 126
23-0095022 | Plumas | EAST QUINCY 1101 | EAST QUINCY 11012452 | Unknown Cause | 2023-07-21 07:32 | 7/18 - 7/24 | 2023-07-21 10:15 | 163 | FTS | 163163 | 1001 | 57 | 39 | 7 | 0 | 0 | 0 | 163
23-0095081 | Yuba | BANGOR 1101 | BANGOR 110182350 | Animal | 2023-07-21 09:03 | 7/18 - 7/24 | 2023-07-21 10:34 | 65.125 | FTS | 16672 | 256 | 25 | 15 | 0 | 0 | 0 | 2 | 91
23-0095131 | Placer | PENRYN 1105 | PENRYN 110550548 | Animal | 2023-07-21 09:57 | 7/18 - 7/24 | 2023-07-21 10:40 | 42.5934 | FTS | 10265 | 241 | 19 | 13 | 0 | 0 | 0 | 2 | 43
23-0095049 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Unknown Cause | 2023-07-21 08:18 | 7/18 - 7/24 | 2023-07-21 12:52 | 256.942 | FTS | 190394 | 741 | 40 | 23 | 17 | 3 | 0 | 1 | 274
23-0095014 | Alameda | VASCO 1102 | VASCO 1102886522 | Animal | 2023-07-21 06:30 | 7/18 - 7/24 | 2023-07-21 13:38 | 405.1503 | FTS | 61988 | 153 | 12 | 11 | 0 | 0 | 0 | 0 | 428
23-0095307 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311056 | Company Initiated | 2023-07-21 13:33 | 7/18 - 7/24 | 2023-07-21 13:58 | 25 | FTS | 8625 | 345 | 32 | 22 | 2 | 0 | 0 | 3 | 25
23-0095258 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | 3rd Party | 2023-07-21 12:30 | 7/18 - 7/24 | 2023-07-21 14:17 | 107 | FTS | 41409 | 387 | 27 | 18 | 10 | 0 | 0 | 0 | 107
23-0095007 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-07-21 06:04 | 7/18 - 7/24 | 2023-07-21 15:39 | 375.0877 | FTS | 21380 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 575
23-0095293 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102414 | Equipment Failure/Involved | 2023-07-21 13:18 | 7/18 - 7/24 | 2023-07-21 20:30 | 129.7664 | FTS | 57227 | 441 | 23 | 16 | 7 | 0 | 0 | 0 | 432
23-0089076 | San Mateo | MENLO 1102 | MENLO 1102154024 | Company Initiated | 2023-07-21 19:07 | 7/18 - 7/24 | 2023-07-21 20:37 | 89 | FTS | 5607 | 63 | 4 | 3 | 5 | 0 | 0 | 0 | 90
23-0095407 | Santa Clara | EDENVALE 1102 | EDENVALE 1102XR064 | Unknown Cause | 2023-07-21 17:06 | 7/18 - 7/24 | 2023-07-21 20:55 | 189.3933 | FTS | 192613 | 1017 | 66 | 46 | 15 | 4 | 0 | 0 | 229
23-0095448 | Marin | STAFFORD 1102 | STAFFORD 11021202 | Unknown Cause | 2023-07-21 21:00 | 7/18 - 7/24 | 2023-07-21 22:24 | 84 | FTS | 4452 | 53 | 1 | 1 | 1 | 0 | 0 | 0 | 84
23-0095449 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Unknown Cause | 2023-07-21 21:03 | 7/18 - 7/24 | 2023-07-21 23:01 | 118 | FTS | 60416 | 512 | 55 | 32 | 4 | 0 | 0 | 3 | 118
23-0095098 | Placer | DRUM 1101 | DRUM 1101CB | Equipment Failure/Involved | 2023-07-21 09:05 | 7/18 - 7/24 | 2023-07-22 00:46 | 253.4208 | FTS | 51191 | 202 | 8 | 4 | 19 | 1 | 0 | 1 | 941
23-0095486 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q08 | Animal | 2023-07-22 01:10 | 7/18 - 7/24 | 2023-07-22 03:11 | 121 | FTS | 45133 | 373 | 14 | 12 | 0 | 1 | 0 | 8 | 121
23-0095522 | Lake | HARTLEY 1101 | HARTLEY 1101658 | Company Initiated | 2023-07-22 08:14 | 7/18 - 7/24 | 2023-07-22 08:27 | 13 | FTS | 7072 | 544 | 32 | 20 | 9 | 0 | 0 | 2 | 13
23-0095496 | Monterey | SAN ARDO 1102 | SAN ARDO 11027066 | Unknown Cause | 2023-07-22 04:41 | 7/18 - 7/24 | 2023-07-22 08:37 | 235.8801 | FTS | 68877 | 292 | 4 | 3 | 12 | 4 | 0 | 0 | 236
23-0095524 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103917328 | Company Initiated | 2023-07-22 08:27 | 7/18 - 7/24 | 2023-07-22 08:50 | 23 | FTS | 1058 | 46 | 0 | 0 | 1 | 0 | 0 | 0 | 23
23-0095502 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Unknown Cause | 2023-07-22 06:07 | 7/18 - 7/24 | 2023-07-22 09:22 | 195 | FTS | 44655 | 229 | 4 | 2 | 9 | 0 | 0 | 0 | 195
23-0095505 | Tehama | CORNING 1102 | CORNING 110253184 | Unknown Cause | 2023-07-22 06:13 | 7/18 - 7/24 | 2023-07-22 09:33 | 200 | FTS | 42000 | 210 | 15 | 15 | 7 | 1 | 0 | 1 | 200
23-0095519 | Contra Costa | SOBRANTE 1101 | SOBRANTE 1101CB | Unknown Cause | 2023-07-22 08:06 | 7/18 - 7/24 | 2023-07-22 09:43 | 95.5041 | FTS | 34859 | 365 | 25 | 20 | 7 | 1 | 0 | 1 | 97
23-0095527 | Lake | LUCERNE 1103 | LUCERNE 1103630 | Animal | 2023-07-22 08:59 | 7/18 - 7/24 | 2023-07-22 10:28 | 89 | FTS | 137772 | 1548 | 146 | 90 | 21 | 1 | 0 | 1 | 89
23-0095508 | Shasta | DESCHUTES 1101 | DESCHUTES 11011380 | Unknown Cause | 2023-07-22 06:42 | 7/18 - 7/24 | 2023-07-22 11:06 | 159.8929 | FTS | 94017 | 588 | 48 | 32 | 8 | 1 | 0 | 2 | 264
23-0095501 | Shasta | STILLWATER 1102 | STILLWATER 1102CB | Unknown Cause | 2023-07-22 06:01 | 7/18 - 7/24 | 2023-07-22 11:12 | 127.8452 | FTS | 180901 | 1415 | 133 | 95 | 16 | 0 | 0 | 0 | 311
23-0095543 | Santa Clara | LLAGAS 2101 | LLAGAS 2101984552 | Company Initiated | 2023-07-22 11:04 | 7/18 - 7/24 | 2023-07-22 11:32 | 28 | FTS | 980 | 35 | 7 | 5 | 1 | 0 | 0 | 2 | 28
23-0095491 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210911092 | Vegetation | 2023-07-22 02:50 | 7/18 - 7/24 | 2023-07-22 13:53 | 302.9661 | FTS | 277214 | 915 | 52 | 43 | 10 | 1 | 0 | 27 | 663
23-0095552 | Humboldt | RIO DELL 1101 | RIO DELL 11018768 | Vegetation | 2023-07-22 12:14 | 7/18 - 7/24 | 2023-07-22 13:55 | 95.5606 | FTS | 65459 | 685 | 22 | 16 | 15 | 1 | 0 | 0 | 101
23-0095417 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110R06 | Equipment Failure/Involved | 2023-07-21 18:05 | 7/18 - 7/24 | 2023-07-22 14:01 | 383.9674 | FTS | 837049 | 2180 | 87 | 64 | 26 | 2 | 0 | 13 | 1196
23-0095426 | Napa | SILVERADO 2104 | SILVERADO 2104806500 | Vegetation | 2023-07-21 18:57 | 7/18 - 7/24 | 2023-07-22 14:51 | 836.8745 | FTS | 1154050 | 1379 | 72 | 43 | 29 | 6 | 0 | 2 | 1194
23-0095581 | Santa Clara | LOS GATOS 1106 | LOS GATOS 110660116 | Equipment Failure/Involved | 2023-07-22 15:39 | 7/18 - 7/24 | 2023-07-22 17:52 | 129.7949 | FTS | 147447 | 1136 | 107 | 87 | 24 | 3 | 0 | 3 | 133
23-0095499 | San Luis Obispo | CHOLAME 1101 | CHOLAME 1101X14 | Animal | 2023-07-22 05:49 | 7/18 - 7/24 | 2023-07-22 18:01 | 227.7885 | FTS | 130295 | 572 | 27 | 14 | 9 | 1 | 0 | 0 | 732
23-0095436 | Fresno | COPPERMINE 1104 | COPPERMINE 1104556430 | Vegetation | 2023-07-21 19:49 | 7/18 - 7/24 | 2023-07-22 18:13 | 959.2593 | FTS | 103600 | 108 | 9 | 9 | 0 | 0 | 0 | 0 | 1344
23-0095576 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 1103CB | Unknown Cause | 2023-07-22 14:23 | 7/18 - 7/24 | 2023-07-22 18:31 | 197.5977 | FTS | 493599 | 2498 | 214 | 156 | 43 | 1 | 0 | 2 | 248
23-0095587 | Monterey | KING CITY 1102 | KING CITY 1102728782 | Unknown Cause | 2023-07-22 16:44 | 7/18 - 7/24 | 2023-07-22 19:04 | 102.3065 | FTS | 6343 | 62 | 0 | 0 | 1 | 0 | 0 | 0 | 140
23-0095601 | Nevada | HIGGINS 1110 | HIGGINS 1110861610 | 3rd Party | 2023-07-22 18:50 | 7/18 - 7/24 | 2023-07-22 20:16 | 62.1359 | FTS | 74998 | 1207 | 108 | 72 | 12 | 0 | 0 | 7 | 86
23-0094515 | Shasta | PIT NO 3 2101 | PIT NO 3 21011480 | Equipment Failure/Involved | 2023-07-20 07:25 | 7/18 - 7/24 | 2023-07-23 03:03 | 211.0543 | FTS | 27226 | 129 | 4 | 4 | 3 | 0 | 0 | 0 | 4058
23-0095600 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103CB | Equipment Failure/Involved | 2023-07-22 18:50 | 7/18 - 7/24 | 2023-07-23 03:40 | 178.3417 | FTS | 879938 | 4934 | 188 | 134 | 50 | 6 | 0 | 0 | 530
23-0095652 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 210769586 | Animal | 2023-07-23 02:44 | 7/18 - 7/24 | 2023-07-23 04:21 | 97 | FTS | 120280 | 1240 | 86 | 66 | 14 | 0 | 0 | 0 | 97
23-0095640 | Alameda | VINEYARD 2110 | VINEYARD 2110CB | Unknown Cause | 2023-07-22 22:36 | 7/18 - 7/24 | 2023-07-23 04:41 | 365 | FTS | 2523610 | 6914 | 203 | 127 | 39 | 10 | 0 | 0 | 365
23-0095616 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 1102CB | 3rd Party | 2023-07-22 20:48 | 7/18 - 7/24 | 2023-07-23 06:21 | 163.7021 | FTS | 143403 | 876 | 97 | 78 | 12 | 1 | 0 | 0 | 573
23-0095619 | Alameda | VINEYARD 2107 | VINEYARD 2107CB | Vegetation | 2023-07-22 20:58 | 7/18 - 7/24 | 2023-07-23 06:47 | 376.0177 | FTS | 1338247 | 3559 | 159 | 96 | 46 | 3 | 0 | 0 | 589
23-0095655 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Unknown Cause | 2023-07-23 06:37 | 7/18 - 7/24 | 2023-07-23 08:08 | 91 | FTS | 27937 | 307 | 19 | 17 | 10 | 5 | 0 | 0 | 91
23-0095613 | Placer | PENRYN 1105 | PENRYN 1105168616 | Equipment Failure/Involved | 2023-07-22 20:29 | 7/18 - 7/24 | 2023-07-23 09:14 | 120.5427 | FTS | 23988 | 199 | 17 | 12 | 2 | 0 | 0 | 1 | 765
23-0095661 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X22 | Unknown Cause | 2023-07-23 07:57 | 7/18 - 7/24 | 2023-07-23 12:10 | 253 | FTS | 21505 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 253
23-0095665 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 2108294550 | Unknown Cause | 2023-07-23 07:58 | 7/18 - 7/24 | 2023-07-23 12:36 | 278 | FTS | 284950 | 1025 | 104 | 76 | 8 | 1 | 0 | 0 | 278
23-0095584 | Santa Clara | MILPITAS 1109 | MILPITAS 1109903328 | Equipment Failure/Involved | 2023-07-22 16:19 | 7/18 - 7/24 | 2023-07-23 14:50 | 704.3868 | FTS | 149330 | 212 | 14 | 10 | 1 | 0 | 0 | 0 | 1351
23-0095677 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210694770 | Vegetation | 2023-07-23 10:43 | 7/18 - 7/24 | 2023-07-23 15:14 | 80.4606 | FTS | 189887 | 2360 | 208 | 163 | 44 | 7 | 0 | 20 | 271
23-0095639 | Nevada | NARROWS 2105 | NARROWS 21052426 | Vegetation | 2023-07-22 22:27 | 7/18 - 7/24 | 2023-07-23 15:32 | 673.8495 | FTS | 2027613 | 3009 | 258 | 153 | 32 | 4 | 0 | 23 | 1025
23-0095707 | Monterey | HATTON 1101 | HATTON 110175304 | Animal | 2023-07-23 16:17 | 7/18 - 7/24 | 2023-07-23 16:57 | 21.7419 | FTS | 20046 | 922 | 44 | 35 | 24 | 0 | 0 | 0 | 40
23-0095694 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210694770 | Equipment Failure/Involved | 2023-07-23 13:48 | 7/18 - 7/24 | 2023-07-23 18:04 | 75.1972 | FTS | 142649 | 1897 | 159 | 128 | 41 | 7 | 0 | 15 | 256
23-0095664 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101648 | Equipment Failure/Involved | 2023-07-23 08:08 | 7/18 - 7/24 | 2023-07-23 18:30 | 101.7285 | FTS | 30722 | 302 | 19 | 15 | 3 | 0 | 0 | 9 | 622
23-0095720 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104570682 | Unknown Cause | 2023-07-23 18:38 | 7/18 - 7/24 | 2023-07-23 20:55 | 136.709 | FTS | 155028 | 1134 | 111 | 82 | 15 | 0 | 0 | 0 | 137
23-0074153 | Placer | HALSEY 1102 | HALSEY 1102CB | Equipment Failure/Involved | 2023-07-23 16:19 | 7/18 - 7/24 | 2023-07-23 21:55 | 126.1985 | FTS | 298207 | 2363 | 183 | 129 | 47 | 10 | 0 | 14 | 336
23-0095753 | Monterey | DEL MONTE 2104 | DEL MONTE 21042624 | Unknown Cause | 2023-07-23 23:08 | 7/18 - 7/24 | 2023-07-24 01:09 | 121 | FTS | 553696 | 4576 | 206 | 146 | 127 | 3 | 0 | 3 | 121
23-0095706 | Shasta | JESSUP 1102 | JESSUP 1102158468 | 3rd Party | 2023-07-23 16:04 | 7/18 - 7/24 | 2023-07-24 01:31 | 101.6144 | FTS | 154149 | 1517 | 161 | 124 | 13 | 2 | 0 | 0 | 567
23-0095685 | Tulare | REEDLEY 1104 | REEDLEY 1104887932 | Unknown Cause | 2023-07-23 12:33 | 7/18 - 7/24 | 2023-07-24 02:05 | 213.5 | FTS | 5551 | 26 | 1 | 1 | 0 | 0 | 0 | 0 | 812
23-0095768 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 1103451760 | Unknown Cause | 2023-07-24 02:46 | 7/18 - 7/24 | 2023-07-24 05:24 | 111.665 | FTS | 111665 | 1000 | 58 | 45 | 17 | 1 | 0 | 0 | 158
23-0095731 | Sonoma | MOLINO 1102 | MOLINO 1102104 | Vegetation | 2023-07-23 20:24 | 7/18 - 7/24 | 2023-07-24 06:14 | 74.2913 | FTS | 113740 | 1531 | 90 | 58 | 21 | 1 | 0 | 15 | 590
23-0095732 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 11051904 | Unknown Cause | 2023-07-23 20:54 | 7/18 - 7/24 | 2023-07-24 07:28 | 634 | FTS | 26628 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 634
23-0095752 | Sonoma | PETALUMA C 1109 | PETALUMA C 110948000 | Animal | 2023-07-23 22:59 | 7/18 - 7/24 | 2023-07-24 09:28 | 629 | FTS | 86802 | 138 | 4 | 4 | 13 | 0 | 0 | 0 | 629
23-0095713 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R56 | Unknown Cause | 2023-07-23 17:30 | 7/18 - 7/24 | 2023-07-24 09:33 | 547.5071 | FTS | 231048 | 422 | 14 | 13 | 10 | 0 | 0 | 1 | 963
23-0095771 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Company Initiated | 2023-07-24 05:27 | 7/18 - 7/24 | 2023-07-24 10:33 | 306 | FTS | 223074 | 729 | 20 | 12 | 14 | 1 | 0 | 0 | 306
23-0095830 | Nevada | NARROWS 2102 | NARROWS 210248484 | Animal | 2023-07-24 08:29 | 7/18 - 7/24 | 2023-07-24 10:36 | 79.2908 | FTS | 49081 | 619 | 41 | 27 | 17 | 5 | 0 | 10 | 127
23-0095873 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101335190 | Vegetation | 2023-07-24 09:38 | 7/18 - 7/24 | 2023-07-24 11:09 | 50.5298 | FTS | 15260 | 302 | 19 | 15 | 3 | 0 | 0 | 9 | 91
23-0095904 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103492068 | Unknown Cause | 2023-07-24 10:23 | 7/18 - 7/24 | 2023-07-24 11:24 | 61 | FTS | 106018 | 1738 | 78 | 55 | 23 | 2 | 0 | 1 | 61
23-0095836 | Stanislaus | WESTLEY 1101 | WESTLEY 110111730 | 3rd Party | 2023-07-24 08:43 | 7/18 - 7/24 | 2023-07-24 12:15 | 212 | FTS | 15900 | 75 | 0 | 0 | 1 | 0 | 0 | 0 | 212
23-0095916 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 2107396264 | Unknown Cause | 2023-07-24 10:50 | 7/18 - 7/24 | 2023-07-24 12:43 | 113 | FTS | 66331 | 587 | 41 | 34 | 8 | 0 | 0 | 0 | 113
23-0095930 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052100 | 3rd Party | 2023-07-24 11:09 | 7/18 - 7/24 | 2023-07-24 13:16 | 122.514 | FTS | 245518 | 2004 | 125 | 84 | 32 | 0 | 0 | 13 | 127
23-0096002 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Company Initiated | 2023-07-24 12:38 | 7/18 - 7/24 | 2023-07-24 13:50 | 72 | FTS | 41904 | 582 | 58 | 44 | 3 | 4 | 0 | 2 | 72
23-0095777 | Contra Costa | CLAYTON 2215 | CLAYTON 2215CB | Equipment Failure/Involved | 2023-07-24 06:17 | 7/18 - 7/24 | 2023-07-24 16:35 | 227.5174 | FTS | 1028151 | 4519 | 342 | 236 | 65 | 6 | 0 | 0 | 618
23-0096001 | Tuolumne | CURTIS 1701 | CURTIS 17019230 | Company Initiated | 2023-07-24 12:38 | 7/18 - 7/24 | 2023-07-24 16:56 | 65.9221 | FTS | 137975 | 2093 | 156 | 114 | 30 | 5 | 6 | 0 | 258
23-0096192 | Humboldt | WILLOW CREEK 1101 | WILLOW CREEK 11015002 | 3rd Party | 2023-07-24 16:24 | 7/25 - 7/31 | 2023-07-24 17:34 | 70 | FTS | 350 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 70
23-0096209 | Sonoma | MOLINO 1102 | MOLINO 1102658 | Unknown Cause | 2023-07-24 17:09 | 7/25 - 7/31 | 2023-07-24 19:20 | 131 | FTS | 1703 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 131
23-0096150 | Sonoma | MOLINO 1102 | MOLINO 1102658 | Vegetation | 2023-07-24 15:13 | 7/25 - 7/31 | 2023-07-24 22:55 | 188.6364 | FTS | 24900 | 132 | 6 | 1 | 1 | 0 | 0 | 0 | 462
23-0096202 | Sonoma | MOLINO 1102 | MOLINO 1102178 | 3rd Party | 2023-07-24 22:24 | 7/25 - 7/31 | 2023-07-24 23:47 | 36.2707 | FTS | 76386 | 2106 | 125 | 85 | 25 | 1 | 0 | 20 | 83
23-0096037 | Yolo | MADISON 2101 | MADISON 21011606 | Equipment Failure/Involved | 2023-07-24 13:19 | 7/25 - 7/31 | 2023-07-25 02:39 | 82.0194 | FTS | 42322 | 516 | 19 | 10 | 6 | 0 | 0 | 1 | 800
23-0096270 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Animal | 2023-07-25 01:09 | 7/25 - 7/31 | 2023-07-25 03:00 | 111 | FTS | 207903 | 1873 | 144 | 103 | 19 | 1 | 0 | 4 | 111
23-0080603 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210619552 | Company Initiated | 2023-07-25 07:22 | 7/25 - 7/31 | 2023-07-25 07:37 | 15 | FTS | 2385 | 159 | 14 | 6 | 3 | 0 | 0 | 0 | 15
23-0096381 | El Dorado | APPLE HILL 1104 | APPLE HILL 110412832 | Company Initiated | 2023-07-25 08:30 | 7/25 - 7/31 | 2023-07-25 09:29 | 59 | FTS | 36875 | 625 | 54 | 34 | 3 | 0 | 0 | 8 | 59
23-0096290 | Butte | WYANDOTTE 1107 | WYANDOTTE 1107CB | Vegetation | 2023-07-25 06:13 | 7/25 - 7/31 | 2023-07-25 10:17 | 226.936 | FTS | 673319 | 2967 | 341 | 257 | 79 | 2 | 0 | 5 | 244
23-0096366 | Napa | CALISTOGA 1102 | CALISTOGA 1102131531 | Unknown Cause | 2023-07-25 08:55 | 7/25 - 7/31 | 2023-07-25 11:39 | 164 | FTS | 11644 | 71 | 1 | 1 | 2 | 0 | 0 | 0 | 164
23-0096400 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Equipment Failure/Involved | 2023-07-25 09:47 | 7/25 - 7/31 | 2023-07-25 14:12 | 61.3977 | FTS | 168107 | 2738 | 185 | 148 | 41 | 6 | 0 | 0 | 265
23-0096465 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052204 | Unknown Cause | 2023-07-25 11:25 | 7/25 - 7/31 | 2023-07-25 14:21 | 115.9406 | FTS | 232345 | 2004 | 125 | 84 | 32 | 0 | 0 | 13 | 176
23-0096535 | San Luis Obispo | SAN MIGUEL 1104 | SAN MIGUEL 1104R88 | Animal | 2023-07-25 13:07 | 7/25 - 7/31 | 2023-07-25 14:46 | 82.6349 | FTS | 19915 | 241 | 9 | 6 | 4 | 2 | 0 | 0 | 99
23-0096613 | Monterey | DEL MONTE 2104 | DEL MONTE 21049500 | Vegetation | 2023-07-25 14:21 | 7/25 - 7/31 | 2023-07-25 15:57 | 96 | FTS | 351744 | 3664 | 165 | 112 | 85 | 3 | 0 | 3 | 96
23-0096338 | Mendocino | PHILO 1102 | PHILO 1102920 | Vegetation | 2023-07-25 07:59 | 7/25 - 7/31 | 2023-07-25 16:32 | 136.6825 | FTS | 144200 | 1055 | 24 | 15 | 20 | 4 | 0 | 2 | 513
23-0096770 | Solano | PEABODY 2113 | PEABODY 2113CB | Company Initiated | 2023-07-25 20:10 | 7/25 - 7/31 | 2023-07-25 20:39 | 29 | FTS | 152917 | 5273 | 418 | 298 | 53 | 3 | 0 | 0 | 29
23-0096738 | Monterey | DEL MONTE 2104 | LAURELES 1112779322 | Vegetation | 2023-07-25 17:01 | 7/25 - 7/31 | 2023-07-26 02:50 | 24.3609 | FTS | 4117 | 169 | 6 | 3 | 5 | 0 | 0 | 0 | 589
23-0096759 | Sonoma | MIRABEL 1101 | MIRABEL 1101774276 | Vegetation | 2023-07-25 19:27 | 7/25 - 7/31 | 2023-07-26 03:43 | 241.9265 | FTS | 16451 | 68 | 2 | 1 | 0 | 0 | 0 | 0 | 496
23-0096713 | Yuba | NARROWS 2101 | NARROWS 21011202 | 3rd Party | 2023-07-25 16:08 | 7/25 - 7/31 | 2023-07-26 03:44 | 254.511 | FTS | 127510 | 501 | 42 | 27 | 2 | 0 | 0 | 4 | 696
23-0096809 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | Vegetation | 2023-07-25 22:32 | 7/25 - 7/31 | 2023-07-26 05:50 | 246.6179 | FTS | 60668 | 246 | 25 | 17 | 3 | 0 | 0 | 9 | 438
23-0096821 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11022540 | Vegetation | 2023-07-26 00:49 | 7/25 - 7/31 | 2023-07-26 06:54 | 365 | FTS | 116070 | 318 | 8 | 7 | 14 | 4 | 0 | 0 | 365
23-0096757 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101V12 | Unknown Cause | 2023-07-25 19:32 | 7/25 - 7/31 | 2023-07-26 08:40 | 788 | FTS | 161540 | 205 | 5 | 1 | 47 | 0 | 0 | 1 | 788
23-0096817 | Fresno | BALCH NO 1 1101 | BALCH NO 1 1101105414 | Unknown Cause | 2023-07-26 00:11 | 7/25 - 7/31 | 2023-07-26 10:36 | 625 | FTS | 16875 | 27 | 1 | 1 | 1 | 2 | 0 | 0 | 625
23-0096824 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-07-26 01:58 | 7/25 - 7/31 | 2023-07-26 12:49 | 604.9298 | FTS | 34481 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 651
23-0096816 | Monterey | LAURELES 1111 | LAURELES 1112438 | Unknown Cause | 2023-07-26 00:09 | 7/25 - 7/31 | 2023-07-26 13:25 | 708.2041 | FTS | 173510 | 245 | 15 | 12 | 3 | 0 | 0 | 0 | 796
23-0096781 | Sonoma | MOLINO 1102 | MOLINO 1102178 | Unknown Cause | 2023-07-25 20:54 | 7/25 - 7/31 | 2023-07-26 13:55 | 829.9022 | FTS | 1747774 | 2106 | 125 | 85 | 25 | 1 | 0 | 20 | 1021
23-0096988 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103248212 | Animal | 2023-07-26 10:24 | 7/25 - 7/31 | 2023-07-26 14:55 | 224.9528 | FTS | 28569 | 127 | 6 | 4 | 1 | 0 | 0 | 0 | 271
23-0097119 | Napa | CALISTOGA 1101 | CALISTOGA 1101727772 | Unknown Cause | 2023-07-26 14:15 | 7/25 - 7/31 | 2023-07-26 16:20 | 125 | FTS | 2375 | 19 | 3 | 2 | 0 | 0 | 0 | 0 | 125
23-0097156 | San Mateo | SNEATH LANE 1101 | SNEATH LANE 11016525 | Unknown Cause | 2023-07-26 15:01 | 7/25 - 7/31 | 2023-07-26 18:34 | 194.4868 | FTS | 162202 | 834 | 56 | 40 | 7 | 1 | 0 | 0 | 213
23-0097199 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 110582622 | Unknown Cause | 2023-07-26 15:25 | 7/25 - 7/31 | 2023-07-26 19:46 | 173.7659 | FTS | 71244 | 410 | 38 | 22 | 10 | 0 | 0 | 4 | 261
23-0097247 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104570682 | Unknown Cause | 2023-07-26 18:21 | 7/25 - 7/31 | 2023-07-26 20:38 | 107.9259 | FTS | 171818 | 1592 | 164 | 125 | 21 | 1 | 0 | 0 | 137
23-0097265 | Contra Costa | ROSSMOOR 1106 | ROSSMOOR 1106CB | Unknown Cause | 2023-07-26 19:38 | 7/25 - 7/31 | 2023-07-26 21:38 | 48.068 | FTS | 114546 | 2383 | 103 | 76 | 22 | 9 | 0 | 0 | 120
23-0097131 | Sonoma | MONTE RIO 1112 | MONTE RIO 111264682 | Vegetation | 2023-07-26 14:26 | 7/25 - 7/31 | 2023-07-26 23:32 | 160.7551 | FTS | 23631 | 147 | 10 | 7 | 4 | 0 | 0 | 0 | 546
23-0097348 | Lake | HIGHLANDS 1104 | HIGHLANDS 110439458 | Animal | 2023-07-27 04:31 | 7/25 - 7/31 | 2023-07-27 05:46 | 75 | FTS | 43425 | 579 | 77 | 62 | 7 | 2 | 0 | 0 | 75
23-0097370 | Yuba | BANGOR 1101 | BANGOR 11011806 | Unknown Cause | 2023-07-27 06:37 | 7/25 - 7/31 | 2023-07-27 09:44 | 180.0233 | FTS | 108374 | 602 | 66 | 45 | 4 | 0 | 0 | 3 | 187
23-0097450 | Shasta | DESCHUTES 1104 | DESCHUTES 1104622260 | Unknown Cause | 2023-07-27 08:48 | 7/25 - 7/31 | 2023-07-27 10:47 | 119 | FTS | 14994 | 126 | 7 | 5 | 1 | 0 | 0 | 0 | 119
23-0097388 | San Luis Obispo | TEMPLETON 2108 | TEMPLETON 2108A64 | Unknown Cause | 2023-07-27 07:08 | 7/25 - 7/31 | 2023-07-27 11:10 | 206.973 | FTS | 637270 | 3079 | 139 | 90 | 45 | 17 | 1 | 0 | 242
23-0097544 | Sonoma | DUNBAR 1103 | DUNBAR 1103234 | Equipment Failure/Involved | 2023-07-27 10:39 | 7/25 - 7/31 | 2023-07-27 11:54 | 75 | FTS | 186075 | 2481 | 277 | 218 | 20 | 0 | 0 | 13 | 75
23-0097568 | Tuolumne | PEORIA 1701 | PEORIA 170176030 | Unknown Cause | 2023-07-27 11:25 | 7/25 - 7/31 | 2023-07-27 13:19 | 78.4667 | FTS | 15301 | 195 | 9 | 8 | 7 | 2 | 0 | 0 | 114
23-0097745 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown Cause | 2023-07-27 16:20 | 7/25 - 7/31 | 2023-07-27 19:37 | 87.7035 | FTS | 45255 | 516 | 19 | 10 | 6 | 0 | 0 | 1 | 197
23-0097668 | Fresno | COPPERMINE 1104 | COPPERMINE 1104613086 | 3rd Party | 2023-07-27 14:28 | 7/25 - 7/31 | 2023-07-27 20:14 | 128.4746 | FTS | 7580 | 59 | 1 | 0 | 1 | 0 | 0 | 0 | 346
23-0097874 | San Luis Obispo | FOOTHILL 1101 | FOOTHILL 1101CB | Unknown Cause | 2023-07-28 00:42 | 7/25 - 7/31 | 2023-07-28 02:33 | 73.9606 | FTS | 28179 | 381 | 13 | 6 | 7 | 1 | 0 | 0 | 111
23-0097764 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Equipment Failure/Involved | 2023-07-27 16:48 | 7/25 - 7/31 | 2023-07-28 02:54 | 118.6993 | FTS | 222205 | 1872 | 144 | 103 | 19 | 1 | 0 | 4 | 606
23-0097856 | San Joaquin | TEMPORARY CARBONA 1101 | TEMPORARY CARBONA 110145186 | Unknown Cause | 2023-07-27 22:06 | 7/25 - 7/31 | 2023-07-28 04:05 | 359 | FTS | 47029 | 131 | 6 | 4 | 7 | 0 | 0 | 0 | 359
23-0097890 | Mendocino | UKIAH 1114 | UKIAH 1114943840 | Unknown Cause | 2023-07-28 05:46 | 7/25 - 7/31 | 2023-07-28 07:16 | 48.7606 | FTS | 33401 | 685 | 36 | 23 | 21 | 5 | 0 | 0 | 90
23-0097887 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210694770 | 3rd Party | 2023-07-28 05:09 | 7/25 - 7/31 | 2023-07-28 07:24 | 41.5706 | FTS | 79192 | 1905 | 159 | 128 | 41 | 7 | 0 | 15 | 135
23-0093280 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102867686 | Company Initiated | 2023-07-28 08:48 | 7/25 - 7/31 | 2023-07-28 09:05 | 17 | FTS | 272 | 16 | 0 | 0 | 3 | 0 | 0 | 0 | 17
23-0097923 | Mendocino | GUALALA 1112 | GUALALA 1111402866 | Vegetation | 2023-07-28 07:38 | 7/25 - 7/31 | 2023-07-28 09:13 | 95 | FTS | 3230 | 34 | 4 | 3 | 1 | 0 | 0 | 0 | 95
23-0098042 | Tulare | REEDLEY 1104 | REEDLEY 1104887932 | Unknown Cause | 2023-07-28 10:37 | 7/25 - 7/31 | 2023-07-28 11:37 | 60 | FTS | 1560 | 26 | 1 | 1 | 0 | 0 | 0 | 0 | 60
23-0097956 | Butte | WYANDOTTE 1102 | WYANDOTTE 110213916 | Company Initiated | 2023-07-28 08:24 | 7/25 - 7/31 | 2023-07-28 11:54 | 70.2167 | FTS | 148438 | 2114 | 150 | 119 | 45 | 3 | 0 | 1 | 210
23-0098047 | Lake | HARTLEY 1102 | HARTLEY 1102841676 | Animal | 2023-07-28 10:53 | 7/25 - 7/31 | 2023-07-28 12:00 | 67 | FTS | 61774 | 922 | 95 | 73 | 10 | 0 | 0 | 0 | 67
23-0097873 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11016014 | Vegetation | 2023-07-28 00:40 | 7/25 - 7/31 | 2023-07-28 14:18 | 234.3214 | FTS | 110834 | 473 | 16 | 10 | 22 | 8 | 0 | 0 | 818
23-0098110 | Butte | PARADISE 1103 | PARADISE 11032486 | 3rd Party | 2023-07-28 13:04 | 7/25 - 7/31 | 2023-07-28 14:31 | 87 | FTS | 74646 | 858 | 68 | 50 | 11 | 0 | 0 | 4 | 87
23-0098058 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21061104 | Unknown Cause | 2023-07-28 10:05 | 7/25 - 7/31 | 2023-07-28 14:41 | 259.1873 | FTS | 171582 | 662 | 49 | 39 | 27 | 5 | 0 | 1 | 276
23-0098206 | Placer | BELL 1108 | BELL 11082226 | Animal | 2023-07-28 16:07 | 7/25 - 7/31 | 2023-07-28 18:23 | 106.618 | FTS | 89879 | 843 | 68 | 49 | 9 | 0 | 0 | 6 | 136
23-0098227 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052100 | Equipment Failure/Involved | 2023-07-28 20:32 | 7/25 - 7/31 | 2023-07-28 22:05 | 93 | FTS | 186372 | 2004 | 125 | 84 | 32 | 0 | 0 | 13 | 93
23-0098220 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104570682 | Unknown Cause | 2023-07-28 19:04 | 7/25 - 7/31 | 2023-07-28 23:29 | 264.5926 | FTS | 300048 | 1134 | 0 | 0 | 0 | 0 | 0 | 0 | 265
23-0098261 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | 3rd Party | 2023-07-29 02:34 | 7/25 - 7/31 | 2023-07-29 03:11 | 21.5315 | FTS | 59190 | 2749 | 187 | 135 | 42 | 6 | 0 | 2 | 37
23-0098268 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210151584 | Animal | 2023-07-29 06:05 | 7/25 - 7/31 | 2023-07-29 08:14 | 85.3584 | FTS | 56678 | 664 | 78 | 52 | 9 | 0 | 0 | 13 | 129
23-0098247 | Calaveras | FROGTOWN 1701 | FROGTOWN 1701CB | Company Initiated | 2023-07-28 22:28 | 7/25 - 7/31 | 2023-07-29 08:23 | 201.7032 | FTS | 438301 | 2173 | 145 | 110 | 33 | 6 | 0 | 2 | 595
23-0098262 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q10 | Unknown Cause | 2023-07-29 02:32 | 7/25 - 7/31 | 2023-07-29 08:42 | 370 | FTS | 288600 | 780 | 50 | 43 | 4 | 0 | 0 | 13 | 370
23-0098224 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 21012562 | Unknown Cause | 2023-07-28 20:03 | 7/25 - 7/31 | 2023-07-29 08:55 | 86.3603 | FTS | 131354 | 1521 | 71 | 53 | 24 | 2 | 4 | 0 | 772
23-0098221 | Placer | BELL 1107 | BELL 11072400 | Animal | 2023-07-28 19:11 | 7/25 - 7/31 | 2023-07-29 09:34 | 157.6154 | FTS | 81960 | 520 | 37 | 26 | 2 | 2 | 0 | 5 | 863
23-0098284 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | Company Initiated | 2023-07-29 08:35 | 7/25 - 7/31 | 2023-07-29 10:01 | 76.9043 | FTS | 77135 | 1003 | 95 | 65 | 16 | 0 | 0 | 3 | 86
23-0098276 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | Unknown Cause | 2023-07-29 07:05 | 7/25 - 7/31 | 2023-07-29 11:11 | 246 | FTS | 174660 | 710 | 62 | 41 | 17 | 2 | 0 | 0 | 246
23-0098300 | Monterey | SOLEDAD 2104 | SOLEDAD 2102858388 | Unknown Cause | 2023-07-29 10:26 | 7/25 - 7/31 | 2023-07-29 12:28 | 122 | FTS | 14152 | 116 | 4 | 3 | 0 | 1 | 0 | 0 | 122
23-0098322 | Placer | HALSEY 1102 | HALSEY 1102676064 | Company Initiated | 2023-07-29 11:41 | 7/25 - 7/31 | 2023-07-29 12:42 | 61 | FTS | 1586 | 26 | 4 | 2 | 0 | 0 | 0 | 1 | 61
23-0098323 | Nevada | BRUNSWICK 1107 | BRUNSWICK 1107CB | Animal | 2023-07-29 11:44 | 7/25 - 7/31 | 2023-07-29 13:08 | 84 | FTS | 231000 | 2750 | 179 | 106 | 32 | 3 | 0 | 0 | 84
23-0098344 | Butte | BIG BEND 1102 | BIG BEND 1102CB | Unknown Cause | 2023-07-29 15:13 | 7/25 - 7/31 | 2023-07-29 18:52 | 218.068 | FTS | 73707 | 338 | 11 | 6 | 10 | 0 | 0 | 0 | 219
23-0098368 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown Cause | 2023-07-29 18:47 | 7/25 - 7/31 | 2023-07-29 21:58 | 100.5666 | FTS | 122993 | 1223 | 114 | 91 | 17 | 3 | 0 | 4 | 191
23-0098382 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210598606 | Unknown Cause | 2023-07-29 20:44 | 7/25 - 7/31 | 2023-07-29 22:52 | 44.9125 | FTS | 39523 | 880 | 54 | 31 | 41 | 4 | 0 | 0 | 128
23-0098345 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 2108294550 | Equipment Failure/Involved | 2023-07-29 14:00 | 7/25 - 7/31 | 2023-07-29 23:19 | 334.3951 | FTS | 342755 | 1025 | 104 | 76 | 8 | 1 | 0 | 0 | 559
23-0098385 | Contra Costa | WILLOW PASS 2108 | WILLOW PASS 2108CB | Unknown Cause | 2023-07-29 21:07 | 7/25 - 7/31 | 2023-07-29 23:37 | 89.9733 | FTS | 508709 | 5654 | 302 | 220 | 47 | 6 | 0 | 0 | 150
23-0098383 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113R82 | Animal | 2023-07-29 20:46 | 7/25 - 7/31 | 2023-07-30 00:20 | 186.9811 | FTS | 168096 | 899 | 41 | 29 | 12 | 2 | 0 | 7 | 214
23-0098407 | Madera | OAKHURST 1101 | OAKHURST 1101352740 | Equipment Failure/Involved | 2023-07-29 23:10 | 7/25 - 7/31 | 2023-07-30 01:44 | 122.4658 | FTS | 191659 | 1565 | 175 | 127 | 34 | 3 | 0 | 0 | 154
23-0098426 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102527766 | Unknown Cause | 2023-07-30 06:53 | 7/25 - 7/31 | 2023-07-30 08:01 | 68 | FTS | 68 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 68
23-0098408 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401944178 | Vegetation | 2023-07-29 23:18 | 7/25 - 7/31 | 2023-07-30 08:40 | 509.7065 | FTS | 451600 | 886 | 81 | 63 | 16 | 3 | 0 | 1 | 562
23-0098434 | Santa Cruz | PAUL SWEET 2102 | PAUL SWEET 2102777828 | 3rd Party | 2023-07-30 08:34 | 7/25 - 7/31 | 2023-07-30 09:48 | 74 | FTS | 122766 | 1659 | 69 | 53 | 23 | 26 | 0 | 1 | 74
23-0098411 | Tulare | SAND CREEK 1103 | SAND CREEK 11037110 | Unknown Cause | 2023-07-29 23:42 | 7/25 - 7/31 | 2023-07-30 10:23 | 641 | FTS | 108970 | 170 | 5 | 3 | 8 | 0 | 0 | 0 | 641
23-0098413 | Calaveras | SALT SPRINGS 2101 | SALT SPRINGS 21011232 | Equipment Failure/Involved | 2023-07-30 00:35 | 7/25 - 7/31 | 2023-07-30 10:28 | 584.6196 | FTS | 537850 | 920 | 17 | 14 | 9 | 2 | 0 | 0 | 593
23-0098436 | Contra Costa | SOBRANTE 1101 | SOBRANTE 1101CB | Unknown Cause | 2023-07-30 08:42 | 7/25 - 7/31 | 2023-07-30 11:07 | 133.726 | FTS | 48810 | 365 | 25 | 20 | 7 | 1 | 0 | 1 | 145
23-0098430 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102514690 | Unknown Cause | 2023-07-30 07:07 | 7/25 - 7/31 | 2023-07-30 12:14 | 305.2324 | FTS | 116904 | 383 | 37 | 26 | 8 | 2 | 0 | 1 | 307
23-0098386 | Shasta | JESSUP 1101 | JESSUP 110141356 | Equipment Failure/Involved | 2023-07-29 21:35 | 7/25 - 7/31 | 2023-07-30 14:29 | 586.9518 | FTS | 207194 | 353 | 26 | 22 | 7 | 2 | 0 | 0 | 1014
23-0098400 | Amador | PINE GROVE 1102 | PINE GROVE 11026080 | Vegetation | 2023-07-29 22:05 | 7/25 - 7/31 | 2023-07-30 18:34 | 791.4625 | FTS | 253268 | 320 | 20 | 15 | 4 | 0 | 0 | 5 | 1229
23-0098463 | Yolo | MADISON 2101 | MADISON 210189332 | Unknown Cause | 2023-07-30 16:29 | 7/25 - 7/31 | 2023-07-30 19:03 | 55.3644 | FTS | 39198 | 708 | 20 | 11 | 15 | 13 | 0 | 1 | 154
23-0098443 | San Mateo | EMERALD LAKE SUB | EMERALD LAKE 0401CB | Vegetation | 2023-07-30 10:09 | 7/25 - 7/31 | 2023-07-30 20:29 | 76.9471 | FTS | 48015 | 624 | 38 | 30 | 16 | 1 | 0 | 1 | 620
23-0098485 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 1102CB | Unknown Cause | 2023-07-30 19:38 | 7/25 - 7/31 | 2023-07-30 22:32 | 167.8537 | FTS | 358032 | 2133 | 97 | 70 | 38 | 2 | 0 | 0 | 174
23-0098422 | Butte | CLARK ROAD 1101 | CLARK ROAD 1101CB | Equipment Failure/Involved | 2023-07-30 05:33 | 7/25 - 7/31 | 2023-07-31 02:58 | 1285 | FTS | 32125 | 25 | 0 | 0 | 13 | 8 | 0 | 0 | 1285
23-0098523 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-07-30 23:32 | 7/25 - 7/31 | 2023-07-31 08:16 | 436.6984 | FTS | 196951 | 451 | 44 | 29 | 8 | 0 | 0 | 0 | 524
23-0098494 | Nevada | HIGGINS 1103 | HIGGINS 110332120 | Unknown Cause | 2023-07-30 21:51 | 7/25 - 7/31 | 2023-07-31 08:54 | 427.5603 | FTS | 602860 | 1410 | 132 | 94 | 12 | 1 | 0 | 5 | 663
23-0098478 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101V12 | Unknown Cause | 2023-07-30 18:39 | 7/25 - 7/31 | 2023-07-31 09:16 | 710.8732 | FTS | 145729 | 205 | 5 | 1 | 47 | 0 | 0 | 1 | 877
23-0098556 | Monterey | LOS OSITOS 2102 | LOS OSITOS 21027592 | Unknown Cause | 2023-07-31 07:25 | 7/25 - 7/31 | 2023-07-31 09:38 | 133 | FTS | 12635 | 95 | 1 | 1 | 5 | 0 | 0 | 0 | 133
23-0098669 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104905960 | Company Initiated | 2023-07-31 11:02 | 7/25 - 7/31 | 2023-07-31 11:22 | 20 | FTS | 50080 | 2504 | 293 | 211 | 59 | 8 | 0 | 0 | 20
23-0098592 | Santa Clara | SARATOGA 1107 | SARATOGA 1107413816 | Animal | 2023-07-31 08:45 | 7/25 - 7/31 | 2023-07-31 12:13 | 55.2353 | FTS | 28170 | 510 | 30 | 17 | 13 | 2 | 0 | 2 | 208
23-0098525 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 11032936 | Unknown Cause | 2023-07-30 23:57 | 7/25 - 7/31 | 2023-07-31 12:18 | 741 | FTS | 188214 | 254 | 16 | 10 | 5 | 1 | 0 | 0 | 741
23-0098701 | Shasta | WHITMORE 1101 | WHITMORE 11011594 | 3rd Party | 2023-07-31 11:36 | 7/25 - 7/31 | 2023-07-31 13:12 | 96 | FTS | 11904 | 124 | 11 | 9 | 4 | 0 | 0 | 1 | 96
23-0098532 | Alameda | HERDLYN 1102 | HERDLYN 1102CB | 3rd Party | 2023-07-31 03:48 | 7/25 - 7/31 | 2023-07-31 13:35 | 167.7678 | FTS | 155353 | 926 | 61 | 34 | 36 | 4 | 0 | 0 | 587
23-0098883 | Tuolumne | CURTIS 1705 | CURTIS 17058170 | Animal | 2023-07-31 19:36 | 8/1 - 8/7 | 2023-07-31 20:28 | 52 | FTS | 26052 | 501 | 58 | 46 | 4 | 0 | 0 | 0 | 52
23-0098878 | Sonoma | MIRABEL 1101 | MIRABEL 1101298 | Vegetation | 2023-07-31 18:51 | 8/1 - 8/7 | 2023-07-31 20:28 | 97 | FTS | 22116 | 228 | 12 | 10 | 2 | 0 | 0 | 0 | 97
23-0098911 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106LA64 | Equipment Failure/Involved | 2023-07-31 22:27 | 8/1 - 8/7 | 2023-08-01 01:37 | 185.0969 | FTS | 84034 | 454 | 48 | 34 | 4 | 0 | 0 | 5 | 190
23-0098778 | Santa Cruz | BEN LOMOND 1101 | BEN LOMOND 1101BL 1101 | Vegetation | 2023-07-31 14:41 | 8/1 - 8/7 | 2023-08-01 03:43 | 124.6533 | FTS | 93490 | 750 | 53 | 43 | 11 | 0 | 0 | 0 | 782
23-0098922 | Napa | TULUCAY 1101 | TULUCAY 1101504524 | Unknown Cause | 2023-08-01 01:11 | 8/1 - 8/7 | 2023-08-01 04:27 | 196 | FTS | 2352 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 196
23-0098930 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2023-08-01 03:17 | 8/1 - 8/7 | 2023-08-01 06:11 | 174 | FTS | 11832 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 174
23-0098936 | Yuba | HONCUT 1102 | HONCUT 1102301886 | Unknown Cause | 2023-08-01 06:37 | 8/1 - 8/7 | 2023-08-01 08:33 | 116 | FTS | 10788 | 93 | 9 | 9 | 0 | 0 | 0 | 0 | 116
23-0098953 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210136820 | Unknown Cause | 2023-08-01 06:46 | 8/1 - 8/7 | 2023-08-01 08:55 | 129 | FTS | 19092 | 148 | 4 | 4 | 0 | 0 | 0 | 4 | 129
23-0098945 | Monterey | KING CITY 1106 | KING CITY 1106944510 | Unknown Cause | 2023-08-01 06:51 | 8/1 - 8/7 | 2023-08-01 09:15 | 144 | FTS | 17856 | 124 | 3 | 1 | 5 | 0 | 0 | 0 | 144
23-0098949 | Shasta | FRENCH GULCH 1102 | FRENCH GULCH 11021462 | Animal | 2023-08-01 07:04 | 8/1 - 8/7 | 2023-08-01 09:16 | 132 | FTS | 3564 | 27 | 1 | 1 | 5 | 0 | 0 | 0 | 132
23-0098950 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-08-01 07:12 | 8/1 - 8/7 | 2023-08-01 10:14 | 175.9867 | FTS | 79370 | 451 | 45 | 29 | 8 | 0 | 0 | 0 | 182
23-0098946 | San Benito | HOLLISTER 2104 | HOLLISTER 21044403 | Equipment Failure/Involved | 2023-08-01 06:56 | 8/1 - 8/7 | 2023-08-01 11:07 | 251 | FTS | 9287 | 37 | 0 | 0 | 1 | 0 | 0 | 0 | 251
23-0099177 | Butte | CLARK ROAD 1102 | CLARK ROAD 110292622 | Company Initiated | 2023-08-01 13:35 | 8/1 - 8/7 | 2023-08-01 13:52 | 9.4299 | FTS | 2018 | 214 | 17 | 12 | 2 | 1 | 0 | 0 | 17
23-0099166 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | Company Initiated | 2023-08-01 13:19 | 8/1 - 8/7 | 2023-08-01 15:17 | 52.9613 | FTS | 68426 | 1292 | 53 | 35 | 3 | 0 | 0 | 5 | 118
23-0099322 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612760 | Company Initiated | 2023-08-01 18:10 | 8/1 - 8/7 | 2023-08-01 18:22 | 12 | FTS | 6564 | 547 | 48 | 40 | 9 | 0 | 0 | 6 | 12
23-0099264 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102904170 | Unknown Cause | 2023-08-01 15:41 | 8/1 - 8/7 | 2023-08-01 18:23 | 162 | FTS | 11988 | 74 | 2 | 1 | 8 | 0 | 0 | 0 | 162
23-0099011 | Sonoma | MOLINO 1102 | MOLINO 1102178 | Unknown Cause | 2023-08-01 09:29 | 8/1 - 8/7 | 2023-08-01 19:26 | 433.4886 | FTS | 912927 | 2106 | 127 | 87 | 25 | 1 | 0 | 20 | 597
23-0099330 | Butte | BANGOR 1101 | BANGOR 1101CB | Unknown Cause | 2023-08-01 19:12 | 8/1 - 8/7 | 2023-08-01 20:32 | 80 | FTS | 2560 | 32 | 1 | 1 | 0 | 0 | 0 | 0 | 80
23-0099344 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612760 | Equipment Failure/Involved | 2023-08-01 20:44 | 8/1 - 8/7 | 2023-08-01 21:11 | 27 | FTS | 14769 | 547 | 48 | 40 | 9 | 0 | 0 | 6 | 27
23-0099208 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 211051800 | 3rd Party | 2023-08-01 14:18 | 8/1 - 8/7 | 2023-08-02 02:05 | 105.911 | FTS | 107076 | 1011 | 95 | 64 | 12 | 7 | 0 | 9 | 707
23-0099373 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown Cause | 2023-08-01 23:18 | 8/1 - 8/7 | 2023-08-02 03:05 | 110.0345 | FTS | 188269 | 1711 | 96 | 76 | 19 | 2 | 0 | 12 | 227
23-0099392 | Alameda | CAYETANO 2111 | CAYETANO 2111CB | Unknown Cause | 2023-08-02 03:39 | 8/1 - 8/7 | 2023-08-02 06:24 | 130.1671 | FTS | 271789 | 2088 | 61 | 40 | 23 | 5 | 0 | 0 | 165
23-0099403 | Shasta | JESSUP 1101 | JESSUP 11019002 | Animal | 2023-08-02 06:25 | 8/1 - 8/7 | 2023-08-02 08:08 | 96.403 | FTS | 172465 | 1789 | 192 | 145 | 19 | 4 | 0 | 0 | 103
23-0099383 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A32 | Vegetation | 2023-08-02 02:11 | 8/1 - 8/7 | 2023-08-02 08:12 | 115.8981 | FTS | 145568 | 1256 | 45 | 29 | 14 | 5 | 0 | 0 | 361
23-0099348 | Sonoma | MIRABEL 1101 | MIRABEL 1101228 | Unknown Cause | 2023-08-01 21:09 | 8/1 - 8/7 | 2023-08-02 09:14 | 725 | FTS | 177625 | 245 | 14 | 12 | 4 | 0 | 0 | 3 | 725
23-0099419 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Unknown Cause | 2023-08-02 07:14 | 8/1 - 8/7 | 2023-08-02 10:46 | 202.0975 | FTS | 72553 | 359 | 16 | 15 | 5 | 0 | 0 | 0 | 212
23-0099525 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-08-02 10:18 | 8/1 - 8/7 | 2023-08-02 12:39 | 141 | FTS | 7614 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 141
23-0099593 | Shasta | VOLTA 1102 | VOLTA 11021646 | Unknown Cause | 2023-08-02 12:01 | 8/1 - 8/7 | 2023-08-02 15:02 | 175.5138 | FTS | 95655 | 545 | 48 | 35 | 6 | 3 | 0 | 0 | 181
23-0099389 | El Dorado | OLETA 1102 | OLETA 1102186326 | Equipment Failure/Involved | 2023-08-02 04:15 | 8/1 - 8/7 | 2023-08-02 15:03 | 387.7641 | FTS | 378070 | 975 | 39 | 26 | 19 | 1 | 0 | 6 | 648
23-0099399 | Alameda | LAS POSITAS 2103 | CAYETANO 2111MR444 | Unknown Cause | 2023-08-02 03:39 | 8/1 - 8/7 | 2023-08-02 15:09 | 690 | FTS | 2070 | 3 | 0 | 0 | 3 | 3 | 0 | 0 | 690
23-0099702 | Mendocino | GUALALA 1112 | GUALALA 111135562 | Vegetation | 2023-08-02 14:59 | 8/1 - 8/7 | 2023-08-02 15:42 | 43 | FTS | 17501 | 407 | 24 | 16 | 8 | 0 | 0 | 0 | 43
23-0099526 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Vegetation | 2023-08-02 10:28 | 8/1 - 8/7 | 2023-08-02 19:28 | 180.5678 | FTS | 234377 | 1298 | 64 | 38 | 28 | 6 | 0 | 2 | 540
23-0099632 | Tuolumne | PEORIA 1701 | PEORIA 170190090 | 3rd Party | 2023-08-02 13:02 | 8/1 - 8/7 | 2023-08-02 20:46 | 141.5871 | FTS | 382993 | 2705 | 217 | 164 | 30 | 13 | 0 | 1 | 464
23-0099343 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212124 | Equipment Failure/Involved | 2023-08-01 20:37 | 8/1 - 8/7 | 2023-08-02 22:00 | 67.977 | FTS | 32561 | 479 | 32 | 25 | 4 | 0 | 0 | 0 | 1523
23-0099897 | Placer | PENRYN 1103 | PENRYN 1103660 | Animal | 2023-08-03 06:29 | 8/1 - 8/7 | 2023-08-03 07:42 | 73 | FTS | 33142 | 454 | 32 | 19 | 3 | 0 | 0 | 4 | 73
23-0099878 | Mendocino | CALPELLA 1101 | CALPELLA 1101372366 | Equipment Failure/Involved | 2023-08-03 03:34 | 8/1 - 8/7 | 2023-08-03 07:59 | 265 | FTS | 134355 | 507 | 32 | 20 | 9 | 0 | 0 | 0 | 265
23-0099784 | Amador | IONE 1101 | IONE 1101510200 | Unknown Cause | 2023-08-02 17:32 | 8/1 - 8/7 | 2023-08-03 08:02 | 399.8824 | FTS | 40788 | 102 | 4 | 2 | 2 | 0 | 0 | 1 | 870
23-0099935 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-08-03 07:55 | 8/1 - 8/7 | 2023-08-03 09:34 | 73.5772 | FTS | 152452 | 2072 | 122 | 82 | 16 | 6 | 0 | 0 | 99
23-0099968 | Placer | PENRYN 1103 | PENRYN 1103604 | Animal | 2023-08-03 08:48 | 8/1 - 8/7 | 2023-08-03 10:08 | 44.7545 | FTS | 14948 | 334 | 22 | 14 | 3 | 0 | 0 | 4 | 80
23-0099801 | Napa | SILVERADO 2105 | SILVERADO 2105658898 | Unknown Cause | 2023-08-02 20:46 | 8/1 - 8/7 | 2023-08-03 10:27 | 821 | FTS | 107551 | 131 | 2 | 1 | 2 | 0 | 0 | 0 | 821
23-0100015 | Kern | KERN OIL 1106 | KERN OIL 110646960 | 3rd Party | 2023-08-03 09:52 | 8/1 - 8/7 | 2023-08-03 11:08 | 76 | FTS | 608 | 8 | 0 | 0 | 4 | 0 | 0 | 0 | 76
23-0099960 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 2106737512 | Vegetation | 2023-08-03 08:14 | 8/1 - 8/7 | 2023-08-03 11:32 | 82.6144 | FTS | 75840 | 918 | 76 | 53 | 10 | 0 | 0 | 0 | 198
23-0100045 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 2101CB | Unknown Cause | 2023-08-03 10:28 | 8/1 - 8/7 | 2023-08-03 11:48 | 31.1893 | FTS | 47439 | 1521 | 70 | 52 | 24 | 2 | 4 | 0 | 80
23-0099879 | Shasta | DESCHUTES 1101 | DESCHUTES 11011380 | Vegetation | 2023-08-03 04:16 | 8/1 - 8/7 | 2023-08-03 13:17 | 142.5306 | FTS | 83808 | 588 | 47 | 32 | 8 | 1 | 0 | 2 | 541
23-0099983 | Mendocino | FORT BRAGG A 1102 | FORT BRAGG A 110231304 | Unknown Cause | 2023-08-03 09:08 | 8/1 - 8/7 | 2023-08-03 13:53 | 182.625 | FTS | 26298 | 144 | 7 | 6 | 8 | 0 | 0 | 0 | 285
23-0100057 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-08-03 10:48 | 8/1 - 8/7 | 2023-08-03 14:06 | 198 | FTS | 10692 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 198
23-0100043 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Unknown Cause | 2023-08-03 10:29 | 8/1 - 8/7 | 2023-08-03 14:09 | 206.7967 | FTS | 74240 | 359 | 16 | 15 | 5 | 0 | 0 | 0 | 220
23-0100139 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 1102CB | 3rd Party | 2023-08-03 12:51 | 8/1 - 8/7 | 2023-08-03 14:23 | 79.5799 | FTS | 69712 | 876 | 96 | 77 | 12 | 1 | 0 | 0 | 92
23-0100300 | Contra Costa | ROSSMOOR 1106 | ROSSMOOR 1106CB | Unknown Cause | 2023-08-03 19:01 | 8/1 - 8/7 | 2023-08-03 21:39 | 158 | FTS | 376514 | 2383 | 103 | 76 | 23 | 9 | 0 | 0 | 158
23-0100306 | Santa Clara | LOS GATOS 1107 | LOS GATOS 110760092 | Equipment Failure/Involved | 2023-08-03 19:33 | 8/1 - 8/7 | 2023-08-04 01:06 | 287.1668 | FTS | 359820 | 1253 | 111 | 87 | 38 | 4 | 0 | 14 | 333
23-0100382 | Lake | UPPER LAKE 1101 | UPPER LAKE 1101412 | Unknown Cause | 2023-08-04 05:50 | 8/1 - 8/7 | 2023-08-04 08:14 | 144 | FTS | 23184 | 161 | 19 | 10 | 0 | 0 | 0 | 0 | 144
23-0100413 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210136820 | Unknown Cause | 2023-08-04 06:55 | 8/1 - 8/7 | 2023-08-04 10:43 | 223.4189 | FTS | 33066 | 148 | 4 | 4 | 0 | 0 | 0 | 4 | 228
23-0100317 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | Unknown Cause | 2023-08-03 20:31 | 8/1 - 8/7 | 2023-08-04 10:54 | 839.9608 | FTS | 42838 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 863
23-0100523 | Mendocino | FORT BRAGG A 1102 | FORT BRAGG A 1102418 | 3rd Party | 2023-08-04 09:32 | 8/1 - 8/7 | 2023-08-04 11:51 | 95.2367 | FTS | 62761 | 659 | 40 | 31 | 14 | 0 | 0 | 1 | 139
23-0100623 | Humboldt | HARRIS 1109 | HARRIS 1109700 | Company Initiated | 2023-08-04 11:25 | 8/1 - 8/7 | 2023-08-04 12:15 | 50 | FTS | 800 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 50
23-0100644 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101480 | 3rd Party | 2023-08-04 12:41 | 8/1 - 8/7 | 2023-08-04 13:45 | 52.4955 | FTS | 17376 | 331 | 8 | 6 | 4 | 0 | 0 | 2 | 64
23-0100360 | Monterey | LAURELES 1111 | LAURELES 1111432 | Unknown Cause | 2023-08-04 00:01 | 8/1 - 8/7 | 2023-08-04 14:42 | 858.6347 | FTS | 277339 | 323 | 6 | 5 | 7 | 0 | 0 | 0 | 881
23-0100714 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210912392 | Company Initiated | 2023-08-04 14:04 | 8/1 - 8/7 | 2023-08-04 14:45 | 41 | FTS | 287 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 41
23-0100308 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210312990 | Vegetation | 2023-08-03 19:41 | 8/1 - 8/7 | 2023-08-04 15:01 | 97.4608 | FTS | 76994 | 790 | 64 | 55 | 17 | 2 | 0 | 10 | 1160
23-0100401 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | Equipment Failure/Involved | 2023-08-04 06:49 | 8/1 - 8/7 | 2023-08-04 15:43 | 401.0613 | FTS | 510150 | 1272 | 79 | 59 | 12 | 1 | 0 | 0 | 534
23-0100764 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 21012232 | Unknown Cause | 2023-08-04 15:47 | 8/1 - 8/7 | 2023-08-04 17:33 | 69.3604 | FTS | 105844 | 1526 | 70 | 52 | 24 | 2 | 4 | 0 | 106
23-0100769 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | Equipment Failure/Involved | 2023-08-04 16:13 | 8/1 - 8/7 | 2023-08-04 17:41 | 88 | FTS | 112024 | 1273 | 79 | 59 | 12 | 1 | 0 | 0 | 88
23-0100771 | Yolo | MADISON 2101 | MADISON 2101CB | Unknown Cause | 2023-08-04 16:18 | 8/1 - 8/7 | 2023-08-04 19:42 | 151.7692 | FTS | 407045 | 2682 | 159 | 106 | 49 | 27 | 0 | 2 | 204
23-0100585 | Humboldt | CARLOTTA 1121 | CARLOTTA 11214914 | 3rd Party | 2023-08-04 11:05 | 8/1 - 8/7 | 2023-08-04 20:25 | 86.299 | FTS | 98726 | 1144 | 82 | 58 | 21 | 4 | 0 | 0 | 560
23-0100806 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210596324 | Unknown Cause | 2023-08-04 20:43 | 8/1 - 8/7 | 2023-08-04 22:39 | 114.5 | FTS | 229 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 116
23-0100809 | Contra Costa | TIDEWATER 2106 | TIDEWATER 210657926 | Animal | 2023-08-04 21:42 | 8/1 - 8/7 | 2023-08-05 01:10 | 208 | FTS | 451568 | 2171 | 168 | 115 | 73 | 5 | 0 | 0 | 208
23-0100774 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2023-08-04 16:26 | 8/1 - 8/7 | 2023-08-05 02:12 | 388.7478 | FTS | 44706 | 115 | 2 | 2 | 8 | 1 | 0 | 0 | 586
23-0100831 | Placer | WISE 1102 | WISE 1102307494 | Unknown Cause | 2023-08-05 01:06 | 8/1 - 8/7 | 2023-08-05 03:59 | 108.4312 | FTS | 29927 | 276 | 26 | 19 | 3 | 0 | 0 | 4 | 173
23-0100847 | Calaveras | Valley Springs 1101 | Valley Springs 1101207256 | Animal | 2023-08-05 07:40 | 8/1 - 8/7 | 2023-08-05 08:30 | 48.2089 | FTS | 71542 | 1484 | 117 | 82 | 37 | 5 | 0 | 0 | 50
23-0100852 | Santa Cruz | BEN LOMOND 1101 | BEN LOMOND 1101BL 1101 | Unknown Cause | 2023-08-05 08:11 | 8/1 - 8/7 | 2023-08-05 09:56 | 64.9194 | FTS | 48300 | 744 | 53 | 43 | 11 | 0 | 0 | 0 | 105
23-0100845 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Equipment Failure/Involved | 2023-08-05 07:10 | 8/1 - 8/7 | 2023-08-05 10:31 | 200.2739 | FTS | 261758 | 1307 | 128 | 93 | 20 | 2 | 0 | 2 | 201
23-0100855 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-08-05 08:44 | 8/1 - 8/7 | 2023-08-05 11:10 | 137.3069 | FTS | 169574 | 1235 | 96 | 65 | 13 | 6 | 0 | 0 | 146
23-0100908 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210190860 | Company Initiated | 2023-08-05 13:19 | 8/1 - 8/7 | 2023-08-05 13:28 | 9 | FTS | 495 | 55 | 8 | 7 | 0 | 0 | 0 | 1 | 9
23-0100863 | Monterey | OILFIELDS 1103 | OILFIELDS 11037006 | Unknown Cause | 2023-08-05 09:46 | 8/1 - 8/7 | 2023-08-05 14:06 | 206.8915 | FTS | 53378 | 258 | 11 | 6 | 6 | 0 | 0 | 0 | 260
23-0100801 | Sonoma | MONTE RIO 1112 | MONTE RIO 11125040 | Equipment Failure/Involved | 2023-08-04 19:58 | 8/1 - 8/7 | 2023-08-05 15:51 | 752.4419 | FTS | 291195 | 387 | 16 | 14 | 6 | 0 | 0 | 0 | 1193
23-0100929 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 1102CB | Unknown Cause | 2023-08-05 16:17 | 8/1 - 8/7 | 2023-08-05 17:43 | 81.6958 | FTS | 148523 | 1818 | 45 | 31 | 54 | 9 | 0 | 0 | 86
23-0100840 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | 3rd Party | 2023-08-05 06:26 | 8/1 - 8/7 | 2023-08-05 18:23 | 347.4783 | FTS | 39960 | 115 | 3 | 2 | 9 | 2 | 0 | 0 | 717
23-0100928 | Yolo | MADISON 2101 | MADISON 2101CB | Unknown Cause | 2023-08-05 16:10 | 8/1 - 8/7 | 2023-08-05 18:54 | 93.1633 | FTS | 249864 | 2682 | 159 | 106 | 49 | 27 | 0 | 2 | 164
23-0100885 | Tehama | TYLER 1105 | TYLER 11051704 | 3rd Party | 2023-08-05 11:34 | 8/1 - 8/7 | 2023-08-05 19:11 | 146.8638 | FTS | 122925 | 837 | 88 | 57 | 13 | 2 | 0 | 1 | 457
23-0100927 | Amador | OLETA 1101 | OLETA 1101928252 | Unknown Cause | 2023-08-05 16:05 | 8/1 - 8/7 | 2023-08-05 19:15 | 156.3869 | FTS | 78819 | 504 | 34 | 21 | 10 | 1 | 0 | 1 | 190
23-0100938 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 1101CB | Unknown Cause | 2023-08-05 17:33 | 8/1 - 8/7 | 2023-08-05 21:49 | 127.0416 | FTS | 128312 | 1010 | 25 | 16 | 35 | 4 | 0 | 0 | 256
23-0100958 | Monterey | JOLON 1103 | JOLON 1103CB | Unknown Cause | 2023-08-05 22:00 | 8/1 - 8/7 | 2023-08-06 01:39 | 219 | FTS | 4380 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 219
23-0100981 | San Luis Obispo | PERRY 1101 | PERRY 110179696 | Unknown Cause | 2023-08-06 05:26 | 8/1 - 8/7 | 2023-08-06 08:46 | 200 | FTS | 26400 | 132 | 6 | 5 | 1 | 0 | 0 | 1 | 200
23-0100989 | Placer | PENRYN 1106 | PENRYN 110651674 | Animal | 2023-08-06 08:25 | 8/1 - 8/7 | 2023-08-06 09:05 | 40 | FTS | 36960 | 924 | 67 | 39 | 6 | 3 | 0 | 0 | 40
23-0100982 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Unknown Cause | 2023-08-06 06:10 | 8/1 - 8/7 | 2023-08-06 09:23 | 112.9604 | FTS | 94096 | 833 | 86 | 65 | 14 | 1 | 0 | 24 | 193
23-0100991 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210151584 | Animal | 2023-08-06 08:28 | 8/1 - 8/7 | 2023-08-06 09:48 | 79.9051 | FTS | 53057 | 664 | 82 | 56 | 9 | 0 | 0 | 13 | 80
23-0100985 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-08-06 07:18 | 8/1 - 8/7 | 2023-08-06 09:55 | 153.2417 | FTS | 69112 | 451 | 45 | 29 | 8 | 0 | 0 | 0 | 157
23-0100977 | Plumas | GANSNER 1101 | GANSNER 1101372132 | Unknown Cause | 2023-08-06 00:09 | 8/1 - 8/7 | 2023-08-06 10:05 | 576.8427 | FTS | 194396 | 337 | 24 | 17 | 7 | 2 | 0 | 1 | 596
23-0100940 | Humboldt | RIO DELL 1101 | RIO DELL 11011504 | Vegetation | 2023-08-05 17:33 | 8/1 - 8/7 | 2023-08-06 10:25 | 174.9547 | FTS | 54061 | 309 | 11 | 8 | 3 | 0 | 0 | 0 | 1012
23-0100951 | Napa | SILVERADO 2104 | SILVERADO 210437632 | 3rd Party | 2023-08-05 21:05 | 8/1 - 8/7 | 2023-08-06 10:26 | 714.5582 | FTS | 1578459 | 2209 | 112 | 73 | 57 | 8 | 18 | 4 | 801
23-0100950 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101370948 | Vegetation | 2023-08-05 20:40 | 8/1 - 8/7 | 2023-08-06 11:00 | 142.0348 | FTS | 101981 | 718 | 57 | 47 | 12 | 0 | 0 | 0 | 860
23-0101008 | Amador | PINE GROVE 1101 | PINE GROVE 11013170 | Animal | 2023-08-06 11:55 | 8/1 - 8/7 | 2023-08-06 13:12 | 75.1476 | FTS | 51927 | 691 | 49 | 38 | 15 | 0 | 0 | 5 | 77
23-0101002 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2023-08-06 10:25 | 8/1 - 8/7 | 2023-08-06 14:56 | 267.08 | FTS | 13354 | 50 | 0 | 0 | 2 | 0 | 0 | 0 | 271
23-0101005 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | 3rd Party | 2023-08-06 10:40 | 8/1 - 8/7 | 2023-08-06 16:19 | 161.474 | FTS | 242534 | 1502 | 68 | 59 | 15 | 3 | 0 | 13 | 339
23-0101015 | San Benito | TRES PINOS 1111 | TRES PINOS 1111203126 | Unknown Cause | 2023-08-06 14:01 | 8/1 - 8/7 | 2023-08-06 16:35 | 154 | FTS | 7084 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 154
23-0101011 | Santa Barbara | PURISIMA 1101 | PURISIMA 110149394 | Equipment Failure/Involved | 2023-08-06 12:23 | 8/1 - 8/7 | 2023-08-06 21:50 | 184.9382 | FTS | 388740 | 2102 | 85 | 66 | 20 | 2 | 0 | 0 | 567
23-0101046 | Merced | ORO LOMA 1106 | ORO LOMA 11069790 | Unknown Cause | 2023-08-06 18:46 | 8/1 - 8/7 | 2023-08-07 | 132.7751 | FTS | 27750 | 209 | 0 | 0 | 7 | 0 | 0 | 0 | 314
23-0101149 | Mendocino | WILLITS 1103 | WILLITS 1103564506 | Company Initiated | 2023-08-07 08:28 | 8/1 - 8/7 | 2023-08-07 08:47 | 19 | FTS | 2109 | 111 | 10 | 6 | 4 | 0 | 0 | 1 | 19
23-0101100 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-08-07 05:59 | 8/1 - 8/7 | 2023-08-07 09:14 | 180.0364 | FTS | 222345 | 1235 | 96 | 65 | 13 | 6 | 0 | 0 | 195
23-0101152 | Napa | CALISTOGA 1102 | CALISTOGA 1102141073 | Unknown Cause | 2023-08-07 08:28 | 8/1 - 8/7 | 2023-08-07 10:36 | 128 | FTS | 4992 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 128
23-0101083 | Contra Costa | CLAYTON 2215 | CLAYTON 2215184604 | Animal | 2023-08-07 00:39 | 8/1 - 8/7 | 2023-08-07 10:38 | 387.0923 | FTS | 1426048 | 3684 | 274 | 192 | 55 | 5 | 0 | 0 | 599
23-0101161 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Unknown Cause | 2023-08-07 08:45 | 8/1 - 8/7 | 2023-08-07 12:48 | 243 | FTS | 202419 | 833 | 86 | 65 | 14 | 1 | 0 | 24 | 243
23-0101130 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 110355374 | Animal | 2023-08-07 07:52 | 8/1 - 8/7 | 2023-08-07 12:53 | 157.3577 | FTS | 81826 | 520 | 18 | 12 | 5 | 0 | 0 | 0 | 301
23-0101267 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Company Initiated | 2023-08-07 12:34 | 8/1 - 8/7 | 2023-08-07 13:57 | 42.1018 | FTS | 128242 | 3046 | 176 | 123 | 37 | 2 | 0 | 0 | 83
23-0101293 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Vegetation | 2023-08-07 13:19 | 8/1 - 8/7 | 2023-08-07 14:55 | 96 | FTS | 55104 | 574 | 34 | 16 | 5 | 0 | 0 | 0 | 96
23-0100943 | Amador | CLAY 1103 | CLAY 11037124 | Equipment Failure/Involved | 2023-08-05 18:21 | 8/1 - 8/7 | 2023-08-07 15:55 | 444.7854 | FTS | 487040 | 1095 | 96 | 69 | 25 | 0 | 0 | 1 | 2734
23-0101303 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Unknown Cause | 2023-08-07 13:39 | 8/1 - 8/7 | 2023-08-07 16:32 | 173 | FTS | 21971 | 127 | 2 | 2 | 1 | 0 | 0 | 0 | 173
23-0101301 | El Dorado | CLARKSVILLE 2110 | CLARKSVILLE 211019692 | Equipment Failure/Involved | 2023-08-07 13:31 | 8/1 - 8/7 | 2023-08-07 16:44 | 135.4767 | FTS | 553016 | 4082 | 277 | 165 | 66 | 6 | 0 | 0 | 193
23-0101409 | Amador | PINE GROVE 1101 | PINE GROVE 11013170 | Unknown Cause | 2023-08-07 16:19 | 8/8 - 8/14 | 2023-08-07 17:48 | 56.5832 | FTS | 39099 | 691 | 49 | 38 | 15 | 0 | 0 | 5 | 89
23-0101458 | Nevada | GRASS VALLEY 1101 | GRASS VALLEY 1101CB | Equipment Failure/Involved | 2023-08-07 19:24 | 8/8 - 8/14 | 2023-08-07 20:36 | 72 | FTS | 76248 | 1059 | 65 | 52 | 19 | 3 | 0 | 2 | 72
23-0101386 | Lake | REDBUD 1102 | REDBUD 1102523244 | Equipment Failure/Involved | 2023-08-07 15:31 | 8/8 - 8/14 | 2023-08-07 21:54 | 174.1811 | FTS | 492410 | 2827 | 262 | 163 | 35 | 2 | 1 | 0 | 383
23-0101474 | Lake | HARTLEY 1101 | HARTLEY 1101658 | Equipment Failure/Involved | 2023-08-07 21:37 | 8/8 - 8/14 | 2023-08-07 22:53 | 76 | FTS | 44764 | 589 | 32 | 20 | 9 | 0 | 0 | 2 | 76
23-0101171 | Tehama | RED BLUFF 1103 | RED BLUFF 1103CB | Equipment Failure/Involved | 2023-08-07 09:08 | 8/8 - 8/14 | 2023-08-08 00:46 | 77.9486 | FTS | 212254 | 2723 | 216 | 155 | 29 | 11 | 1 | 3 | 938
23-0101511 | Alameda | OAKLAND K 1104 | OAKLAND K 1104432850 | Unknown Cause | 2023-08-08 05:24 | 8/8 - 8/14 | 2023-08-08 06:31 | 67 | FTS | 61573 | 919 | 43 | 32 | 27 | 1 | 0 | 0 | 67
23-0101506 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110112122 | Unknown Cause | 2023-08-08 05:20 | 8/8 - 8/14 | 2023-08-08 07:27 | 127 | FTS | 8128 | 64 | 2 | 2 | 6 | 0 | 0 | 0 | 127
23-0101517 | San Luis Obispo | CAMBRIA 1102 | PERRY 1101V74 | Unknown Cause | 2023-08-08 06:04 | 8/8 - 8/14 | 2023-08-08 07:41 | 97 | FTS | 32204 | 332 | 16 | 12 | 3 | 0 | 0 | 0 | 97
23-0101496 | Placer | PENRYN 1107 | PENRYN 1107CB | Unknown Cause | 2023-08-07 23:45 | 8/8 - 8/14 | 2023-08-08 09:19 | 225.2205 | FTS | 650662 | 2889 | 214 | 135 | 44 | 7 | 0 | 11 | 574
23-0101615 | Mendocino | FORT BRAGG A 1102 | FORT BRAGG A 1102416218 | Unknown Cause | 2023-08-08 08:52 | 8/8 - 8/14 | 2023-08-08 09:31 | 39 | FTS | 5538 | 142 | 9 | 7 | 2 | 0 | 0 | 0 | 39
23-0101607 | Santa Clara | SARATOGA 1103 | SARATOGA 1103LC16 | Animal | 2023-08-08 08:38 | 8/8 - 8/14 | 2023-08-08 10:05 | 87 | FTS | 57507 | 661 | 20 | 11 | 4 | 0 | 0 | 0 | 87
23-0101633 | Stanislaus | NEWMAN 1105 | NEWMAN 110590430 | Animal | 2023-08-08 09:22 | 8/8 - 8/14 | 2023-08-08 10:46 | 78.0333 | FTS | 14046 | 180 | 4 | 3 | 4 | 0 | 0 | 0 | 84
23-0101552 | Sonoma | SANTA ROSA A 1104 | SANTA ROSA A 1104210 | Unknown Cause | 2023-08-08 07:02 | 8/8 - 8/14 | 2023-08-08 12:13 | 179.1238 | FTS | 293763 | 1640 | 125 | 99 | 24 | 1 | 0 | 14 | 311
23-0101691 | Sonoma | DUNBAR 1103 | DUNBAR 1103234 | Company Initiated | 2023-08-08 10:55 | 8/8 - 8/14 | 2023-08-08 12:38 | 82.6068 | FTS | 205030 | 2482 | 280 | 219 | 20 | 0 | 0 | 14 | 103
23-0101683 | Sonoma | DUNBAR 1101 | DUNBAR 1101904852 | Animal | 2023-08-08 10:54 | 8/8 - 8/14 | 2023-08-08 14:02 | 185.8465 | FTS | 404402 | 2176 | 107 | 66 | 38 | 5 | 0 | 8 | 188
23-0101901 | Sutter | HIGGINS 1104 | HIGGINS 11041006 | Vegetation | 2023-08-08 16:30 | 8/8 - 8/14 | 2023-08-08 18:18 | 108 | FTS | 202284 | 1873 | 143 | 101 | 19 | 1 | 0 | 4 | 108
23-0101919 | Placer | PENRYN 1105 | PENRYN 1105168616 | Unknown Cause | 2023-08-08 17:44 | 8/8 - 8/14 | 2023-08-08 19:27 | 103 | FTS | 20497 | 199 | 17 | 12 | 2 | 0 | 0 | 1 | 103
23-0101914 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 1104Y04 | Equipment Failure/Involved | 2023-08-08 17:45 | 8/8 - 8/14 | 2023-08-08 19:48 | 123 | FTS | 55350 | 450 | 8 | 3 | 7 | 2 | 0 | 0 | 123
23-0101981 | Tulare | REEDLEY 1104 | REEDLEY 1104887932 | Unknown Cause | 2023-08-09 04:26 | 8/8 - 8/14 | 2023-08-09 06:17 | 111 | FTS | 2886 | 26 | 1 | 1 | 0 | 0 | 0 | 0 | 111
23-0101995 | Monterey | HATTON 1101 | HATTON 1101399900 | Unknown Cause | 2023-08-09 06:44 | 8/8 - 8/14 | 2023-08-09 08:50 | 73.4676 | FTS | 24979 | 340 | 0 | 0 | 2 | 0 | 0 | 0 | 126
23-0102022 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210190860 | Vegetation | 2023-08-09 07:42 | 8/8 - 8/14 | 2023-08-09 09:21 | 88.0179 | FTS | 9858 | 112 | 9 | 8 | 0 | 0 | 0 | 1 | 99
23-0101986 | Sonoma | COTATI 1105 | COTATI 1105328 | Unknown Cause | 2023-08-09 06:06 | 8/8 - 8/14 | 2023-08-09 10:31 | 111.4357 | FTS | 110990 | 996 | 57 | 40 | 11 | 1 | 0 | 1 | 265
23-0102136 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-08-09 11:10 | 8/8 - 8/14 | 2023-08-09 12:47 | 97 | FTS | 5238 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 97
23-0101778 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Animal | 2023-08-08 13:06 | 8/8 - 8/14 | 2023-08-09 14:18 | 303.5062 | FTS | 49168 | 162 | 6 | 6 | 4 | 1 | 0 | 0 | 1512
23-0102219 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Company Initiated | 2023-08-09 13:05 | 8/8 - 8/14 | 2023-08-09 15:28 | 33.5885 | FTS | 111749 | 3327 | 234 | 172 | 26 | 1 | 0 | 1 | 143
23-0101980 | Butte | ORO FINO 1102 | ORO FINO 110265932 | Vegetation | 2023-08-09 03:44 | 8/8 - 8/14 | 2023-08-09 16:15 | 100.5402 | FTS | 109991 | 1094 | 87 | 54 | 13 | 1 | 0 | 0 | 751
23-0102293 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311056 | Vegetation | 2023-08-09 14:39 | 8/8 - 8/14 | 2023-08-09 16:17 | 63.1544 | FTS | 60123 | 952 | 75 | 51 | 10 | 0 | 0 | 3 | 98
23-0102036 | Butte | WYANDOTTE 1107 | WYANDOTTE 110777578 | 3rd Party | 2023-08-09 08:08 | 8/8 - 8/14 | 2023-08-09 17:59 | 93.2682 | FTS | 143260 | 1536 | 172 | 127 | 23 | 2 | 0 | 3 | 591
23-0102355 | Butte | BIG BEND 1102 | BIG BEND 1102CB | Unknown Cause | 2023-08-09 16:22 | 8/8 - 8/14 | 2023-08-09 19:21 | 178.0444 | FTS | 60179 | 338 | 11 | 6 | 10 | 0 | 0 | 0 | 179
23-0102470 | Monterey | LAURELES 1111 | LAURELES 11122142 | Animal | 2023-08-10 00:21 | 8/8 - 8/14 | 2023-08-10 01:18 | 57 | FTS | 42693 | 749 | 31 | 23 | 12 | 2 | 0 | 0 | 57
23-0102387 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Equipment Failure/Involved | 2023-08-09 18:04 | 8/8 - 8/14 | 2023-08-10 01:36 | 267.6511 | FTS | 556982 | 2081 | 174 | 135 | 32 | 2 | 0 | 2 | 452
23-0102394 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113775992 | Vegetation | 2023-08-09 20:11 | 8/8 - 8/14 | 2023-08-10 04:30 | 123.75 | FTS | 44550 | 360 | 10 | 6 | 1 | 0 | 0 | 2 | 499
23-0102467 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Unknown Cause | 2023-08-10 00:11 | 8/8 - 8/14 | 2023-08-10 06:47 | 130.8561 | FTS | 155457 | 1188 | 36 | 20 | 25 | 1 | 0 | 3 | 396
23-0102408 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown Cause | 2023-08-09 20:33 | 8/8 - 8/14 | 2023-08-10 09:32 | 778.038 | FTS | 286318 | 368 | 13 | 10 | 20 | 3 | 0 | 0 | 779
23-0102506 | Napa | PUEBLO 2104 | PUEBLO 2102618 | Unknown Cause | 2023-08-10 06:16 | 8/8 - 8/14 | 2023-08-10 10:42 | 259.391 | FTS | 97531 | 376 | 4 | 2 | 7 | 1 | 0 | 3 | 266
23-0102479 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Equipment Failure/Involved | 2023-08-10 02:38 | 8/8 - 8/14 | 2023-08-10 10:55 | 192.3753 | FTS | 400333 | 2081 | 174 | 135 | 32 | 2 | 0 | 2 | 497
23-0102513 | Contra Costa | MORAGA 1101 | MORAGA 1101CB | Unknown Cause | 2023-08-10 06:54 | 8/8 - 8/14 | 2023-08-10 11:07 | 72.4533 | FTS | 168309 | 2323 | 127 | 98 | 50 | 1 | 0 | 1 | 253
23-0102399 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 110184088 | Unknown Cause | 2023-08-09 20:19 | 8/8 - 8/14 | 2023-08-10 11:40 | 348.2727 | FTS | 72789 | 209 | 15 | 11 | 3 | 0 | 0 | 1 | 921
23-0102693 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702737236 | Company Initiated | 2023-08-10 11:39 | 8/8 - 8/14 | 2023-08-10 11:53 | 14 | FTS | 2660 | 190 | 18 | 12 | 0 | 0 | 0 | 1 | 14
23-0102496 | Lake | REDBUD 1102 | REDBUD 1102523244 | Equipment Failure/Involved | 2023-08-10 06:04 | 8/8 - 8/14 | 2023-08-10 12:35 | 149.4436 | FTS | 422477 | 2827 | 263 | 164 | 35 | 2 | 1 | 0 | 391
23-0102379 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Equipment Failure/Involved | 2023-08-09 17:30 | 8/8 - 8/14 | 2023-08-10 13:45 | 232.693 | FTS | 708783 | 3046 | 176 | 123 | 37 | 2 | 0 | 0 | 1215
23-0102789 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Vegetation | 2023-08-10 13:54 | 8/8 - 8/14 | 2023-08-10 16:20 | 85.2629 | FTS | 85604 | 1004 | 64 | 40 | 17 | 1 | 0 | 0 | 146
23-0102840 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104905960 | Vegetation | 2023-08-10 14:58 | 8/8 - 8/14 | 2023-08-10 17:39 | 158.4855 | FTS | 416500 | 2628 | 307 | 222 | 59 | 8 | 0 | 0 | 161
23-0102901 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 11051904 | Company Initiated | 2023-08-10 16:08 | 8/8 - 8/14 | 2023-08-10 18:08 | 49.5556 | FTS | 4014 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 120
23-0102929 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052100 | Company Initiated | 2023-08-10 17:06 | 8/8 - 8/14 | 2023-08-10 18:15 | 69 | FTS | 138276 | 2004 | 127 | 85 | 32 | 0 | 0 | 13 | 69
23-0102977 | Monterey | HATTON 1101 | HATTON 1101CB | Company Initiated | 2023-08-10 18:31 | 8/8 - 8/14 | 2023-08-10 18:40 | 9 | FTS | 31842 | 3538 | 117 | 79 | 85 | 9 | 0 | 0 | 9
23-0102749 | Solano | VACAVILLE 1108 | VACAVILLE 1108CB | Animal | 2023-08-10 13:04 | 8/8 - 8/14 | 2023-08-10 20:25 | 75.612 | FTS | 181998 | 2407 | 206 | 147 | 40 | 13 | 0 | 2 | 441
23-0102903 | Mendocino | GUALALA 1112 | GUALALA 11121294 | 3rd Party | 2023-08-10 16:08 | 8/8 - 8/14 | 2023-08-11 03:09 | 147.172 | FTS | 147172 | 1000 | 41 | 31 | 14 | 0 | 0 | 0 | 661
23-0102905 | Mendocino | POINT ARENA 1101 | POINT ARENA 11013702 | 3rd Party | 2023-08-10 16:08 | 8/8 - 8/14 | 2023-08-11 03:23 | 470.4386 | FTS | 26815 | 57 | 3 | 3 | 1 | 0 | 0 | 0 | 675
23-0102911 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11021510 | Unknown Cause | 2023-08-10 16:35 | 8/8 - 8/14 | 2023-08-11 03:32 | 202.1878 | FTS | 169029 | 836 | 18 | 14 | 29 | 6 | 0 | 0 | 657
23-0102803 | Humboldt | HOOPA 1101 | HOOPA 1101405280 | Vegetation | 2023-08-10 14:12 | 8/8 - 8/14 | 2023-08-11 04:10 | 407.2366 | FTS | 853568 | 2096 | 99 | 72 | 61 | 17 | 1 | 0 | 838
23-0103200 | Mariposa | MARIPOSA 2102 | MARIPOSA 21029590 | Company Initiated | 2023-08-11 10:02 | 8/8 - 8/14 | 2023-08-11 10:20 | 18 | FTS | 9036 | 502 | 38 | 23 | 4 | 0 | 0 | 1 | 18
23-0103212 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-08-11 09:51 | 8/8 - 8/14 | 2023-08-11 12:56 | 185 | FTS | 9990 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 185
23-0103287 | Santa Cruz | BURNS 2101 | BURNS 210139126 | 3rd Party | 2023-08-11 11:50 | 8/8 - 8/14 | 2023-08-11 13:36 | 105.9572 | FTS | 42065 | 397 | 29 | 20 | 9 | 0 | 0 | 7 | 106
23-0103426 | Sonoma | PENNGROVE 1101 | PENNGROVE 1101554 | Unknown Cause | 2023-08-11 15:11 | 8/8 - 8/14 | 2023-08-11 16:03 | 52 | FTS | 3796 | 73 | 3 | 1 | 1 | 0 | 0 | 0 | 52
23-0103492 | Humboldt | FRUITLAND 1141 | FRUITLAND 1141866852 | Company Initiated | 2023-08-11 17:27 | 8/8 - 8/14 | 2023-08-11 17:58 | 31 | FTS | 651 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 31
23-0103465 | Napa | PUEBLO 2104 | PUEBLO 2102656 | Unknown Cause | 2023-08-11 16:23 | 8/8 - 8/14 | 2023-08-11 19:00 | 142.1875 | FTS | 29575 | 208 | 4 | 2 | 9 | 0 | 0 | 0 | 157
23-0102654 | Napa | MONTICELLO 1101 | MONTICELLO 1101666 | Unknown Cause | 2023-08-10 10:59 | 8/8 - 8/14 | 2023-08-11 19:10 | 457.0333 | FTS | 548440 | 1200 | 70 | 48 | 22 | 1 | 0 | 3 | 1931
23-0103464 | Calaveras | SALT SPRINGS 2101 | SALT SPRINGS 21011232 | Environmental/External | 2023-08-11 16:18 | 8/8 - 8/14 | 2023-08-12 08:35 | 231.6065 | FTS | 213078 | 920 | 16 | 13 | 9 | 2 | 0 | 0 | 977
23-0103499 | Mendocino | PHILO 1102 | PHILO 1102928 | Unknown Cause | 2023-08-11 18:34 | 8/8 - 8/14 | 2023-08-12 08:55 | 564.7177 | FTS | 258076 | 457 | 7 | 5 | 8 | 1 | 0 | 0 | 861
23-0103596 | San Luis Obispo | FOOTHILL 1101 | FOOTHILL 1101549904 | Unknown Cause | 2023-08-12 10:06 | 8/8 - 8/14 | 2023-08-12 11:21 | 75 | FTS | 1725 | 23 | 1 | 1 | 0 | 0 | 0 | 0 | 75
23-0103583 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11051030 | Unknown Cause | 2023-08-12 09:23 | 8/8 - 8/14 | 2023-08-12 13:07 | 104.0811 | FTS | 128332 | 1233 | 97 | 53 | 27 | 0 | 0 | 6 | 224
23-0103665 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown Cause | 2023-08-12 18:07 | 8/8 - 8/14 | 2023-08-12 19:17 | 70 | FTS | 9450 | 135 | 9 | 7 | 5 | 2 | 0 | 0 | 70
23-0103653 | Santa Clara | LOS GATOS 1107 | LOS GATOS 1107CB | Vegetation | 2023-08-12 15:40 | 8/8 - 8/14 | 2023-08-12 22:30 | 124.6747 | FTS | 288248 | 2312 | 129 | 92 | 72 | 2 | 0 | 14 | 410
23-0103696 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108MR190 | Unknown Cause | 2023-08-12 23:38 | 8/8 - 8/14 | 2023-08-13 06:42 | 374.6307 | FTS | 702058 | 1874 | 94 | 72 | 28 | 0 | 2 | 0 | 424
23-0103693 | Sonoma | MIRABEL 1101 | MIRABEL 1101228 | Unknown Cause | 2023-08-12 22:43 | 8/8 - 8/14 | 2023-08-13 08:48 | 605 | FTS | 148225 | 245 | 14 | 12 | 4 | 0 | 0 | 3 | 605
23-0103712 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101648 | Unknown Cause | 2023-08-13 06:10 | 8/8 - 8/14 | 2023-08-13 09:25 | 79.484 | FTS | 67005 | 843 | 59 | 48 | 16 | 0 | 0 | 13 | 195
23-0103722 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108636 | Animal | 2023-08-13 09:14 | 8/8 - 8/14 | 2023-08-13 10:39 | 85 | FTS | 12070 | 142 | 5 | 4 | 2 | 0 | 0 | 1 | 85
23-0103707 | Contra Costa | TASSAJARA 2112 | TASSAJARA 2112D514R | Equipment Failure/Involved | 2023-08-13 04:50 | 8/8 - 8/14 | 2023-08-13 10:58 | 131.3309 | FTS | 217484 | 1656 | 77 | 44 | 52 | 13 | 0 | 0 | 368
23-0103734 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Unknown Cause | 2023-08-13 10:57 | 8/8 - 8/14 | 2023-08-13 13:05 | 128 | FTS | 27264 | 213 | 12 | 7 | 3 | 0 | 0 | 4 | 128
23-0103715 | Marin | ALTO 1125 | ALTO 11251158 | Unknown Cause | 2023-08-13 07:23 | 8/8 - 8/14 | 2023-08-13 13:10 | 291.319 | FTS | 767043 | 2633 | 117 | 77 | 42 | 5 | 0 | 1 | 347
23-0103700 | Yolo | MADISON 2101 | MADISON 210189332 | Vegetation | 2023-08-13 00:55 | 8/8 - 8/14 | 2023-08-13 13:26 | 719.2486 | FTS | 509228 | 708 | 21 | 11 | 15 | 13 | 0 | 1 | 751
23-0103667 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Equipment Failure/Involved | 2023-08-12 18:37 | 8/8 - 8/14 | 2023-08-13 14:26 | 1120.8126 | FTS | 622051 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 1189
23-0103755 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | 3rd Party | 2023-08-13 13:32 | 8/8 - 8/14 | 2023-08-13 14:41 | 47.3896 | FTS | 26396 | 557 | 44 | 32 | 6 | 0 | 0 | 0 | 69
23-0103731 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108CB | Unknown Cause | 2023-08-13 10:46 | 8/8 - 8/14 | 2023-08-13 14:59 | 236.9812 | FTS | 884414 | 3732 | 157 | 100 | 69 | 15 | 0 | 0 | 253
23-0103762 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR586 | Animal | 2023-08-13 13:55 | 8/8 - 8/14 | 2023-08-13 15:52 | 117 | FTS | 6786 | 58 | 1 | 1 | 3 | 0 | 0 | 1 | 117
23-0103753 | San Luis Obispo | CAYUCOS 1101 | CAYUCOS 1101W58 | Animal | 2023-08-13 13:23 | 8/8 - 8/14 | 2023-08-13 16:18 | 175 | FTS | 57750 | 330 | 5 | 5 | 7 | 0 | 0 | 0 | 175
23-0103792 | Plumas | CHESTER SUB | N/A | 3rd Party | 2023-08-13 20:16 | 8/8 - 8/14 | 2023-08-13 22:28 | 129.1933 | T-EPSS | 214590 | 1661 | 75 | 61 | 44 | 10 | 5 | 0 | 132
23-0103765 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 1104CB | Environmental/External | 2023-08-13 15:25 | 8/8 - 8/14 | 2023-08-14 00:45 | 79.8571 | FTS | 50310 | 630 | 11 | 9 | 10 | 2 | 0 | 4 | 560
23-0103775 | Tuolumne | MIWUK 1701 | MIWUK 170110600 | Environmental/External | 2023-08-13 17:49 | 8/8 - 8/14 | 2023-08-14 01:39 | 128.9622 | FTS | 109102 | 846 | 53 | 37 | 6 | 0 | 0 | 0 | 470
23-0103784 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101CB | Animal | 2023-08-13 19:05 | 8/8 - 8/14 | 2023-08-14 03:49 | 227.2706 | FTS | 798856 | 3515 | 258 | 182 | 97 | 15 | 5 | 1 | 524
23-0103837 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-08-14 02:08 | 8/8 - 8/14 | 2023-08-14 03:50 | 102 | FTS | 46002 | 451 | 45 | 29 | 8 | 0 | 0 | 0 | 102
23-0103839 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104236895 | Unknown Cause | 2023-08-14 01:17 | 8/8 - 8/14 | 2023-08-14 04:30 | 193 | FTS | 772 | 4 | 0 | 0 | 2 | 0 | 0 | 0 | 193
23-0103828 | Calaveras | STANISLAUS 1701 | STANISLAUS 17011812 | Vegetation | 2023-08-13 23:46 | 8/8 - 8/14 | 2023-08-14 10:01 | 572.047 | FTS | 522851 | 914 | 58 | 47 | 21 | 2 | 0 | 0 | 615
23-0103965 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104236895 | Unknown Cause | 2023-08-14 08:36 | 8/8 - 8/14 | 2023-08-14 10:37 | 121 | FTS | 484 | 4 | 0 | 0 | 2 | 0 | 0 | 0 | 121
23-0103881 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-08-14 08:18 | 8/8 - 8/14 | 2023-08-14 10:40 | 142 | FTS | 64042 | 451 | 45 | 29 | 8 | 0 | 0 | 0 | 142
23-0103777 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Environmental/External | 2023-08-13 18:02 | 8/8 - 8/14 | 2023-08-14 10:44 | 441.4511 | FTS | 888641 | 2013 | 221 | 163 | 23 | 2 | 0 | 3 | 1002
23-0103941 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-08-14 09:52 | 8/8 - 8/14 | 2023-08-14 11:27 | 95 | FTS | 5130 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 95
23-0103832 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 110169866 | Vegetation | 2023-08-14 00:24 | 8/8 - 8/14 | 2023-08-14 11:42 | 409.943 | FTS | 323445 | 789 | 31 | 23 | 14 | 3 | 0 | 0 | 678
23-0104173 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121134 | Vegetation | 2023-08-14 14:58 | 8/15 - 8/21 | 2023-08-14 17:09 | 39.7924 | FTS | 9391 | 236 | 5 | 5 | 8 | 0 | 0 | 0 | 131
23-0104191 | Santa Barbara | SISQUOC 1101 | PALMER 1101M88 | 3rd Party | 2023-08-14 15:19 | 8/15 - 8/21 | 2023-08-14 18:02 | 163 | FTS | 6357 | 39 | 0 | 0 | 1 | 0 | 0 | 0 | 163
23-0104193 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Equipment Failure/Involved | 2023-08-14 15:08 | 8/15 - 8/21 | 2023-08-14 18:34 | 25.1216 | FTS | 37406 | 1489 | 179 | 136 | 39 | 2 | 0 | 0 | 206
23-0104257 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210151584 | Animal | 2023-08-14 18:07 | 8/15 - 8/21 | 2023-08-14 19:48 | 101 | FTS | 67064 | 664 | 82 | 56 | 9 | 0 | 0 | 13 | 101
23-0104225 | Tehama | VOLTA 1101 | VOLTA 1101914816 | Unknown Cause | 2023-08-14 16:07 | 8/15 - 8/21 | 2023-08-14 20:03 | 236 | FTS | 18172 | 77 | 8 | 7 | 2 | 0 | 0 | 0 | 236
23-0104239 | Santa Clara | EDENVALE 2105 | EDENVALE 2105469810 | Unknown Cause | 2023-08-14 16:47 | 8/15 - 8/21 | 2023-08-14 20:23 | 216 | FTS | 3672 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 216
23-0104270 | Mendocino | COVELO 1101 | COVELO 1101562360 | Environmental/External | 2023-08-14 18:53 | 8/15 - 8/21 | 2023-08-14 22:24 | 211 | FTS | 109298 | 518 | 21 | 17 | 2 | 3 | 0 | 0 | 211
23-0104262 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21061104 | Unknown Cause | 2023-08-14 17:26 | 8/15 - 8/21 | 2023-08-14 23:10 | 263.4555 | FTS | 174671 | 663 | 49 | 39 | 27 | 5 | 0 | 1 | 344
23-0104286 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 1103CB | Unknown Cause | 2023-08-14 20:56 | 8/15 - 8/21 | 2023-08-14 23:18 | 140.9293 | FTS | 213226 | 1513 | 90 | 67 | 16 | 2 | 0 | 0 | 142
23-0104304 | Monterey | OTTER SUB | N/A | 3rd Party | 2023-08-14 21:55 | 8/15 - 8/21 | 2023-08-15 | 125 | T-EPSS | 139250 | 1114 | 25 | 16 | 32 | 3 | 1 | 0 | 125
23-0104303 | Monterey | LAURELES SUB | N/A | 3rd Party | 2023-08-14 21:55 | 8/15 - 8/21 | 2023-08-15 05:03 | 351.0278 | T-EPSS | 1237724 | 3526 | 154 | 105 | 80 | 3 | 0 | 2 | 428
23-0104293 | Monterey | RESERVATION ROAD SUB | N/A | 3rd Party | 2023-08-14 21:55 | 8/15 - 8/21 | 2023-08-15 06:09 | 490.082 | T-EPSS | 2228403 | 4547 | 280 | 206 | 89 | 6 | 0 | 0 | 494
23-0104333 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q12 | Unknown Cause | 2023-08-15 06:17 | 8/15 - 8/21 | 2023-08-15 08:20 | 50.7249 | FTS | 76138 | 1501 | 68 | 59 | 15 | 3 | 0 | 13 | 123
23-0104337 | Marin | STAFFORD 1102 | STAFFORD 11021258 | Animal | 2023-08-15 06:23 | 8/15 - 8/21 | 2023-08-15 09:40 | 197 | FTS | 235809 | 1197 | 74 | 48 | 6 | 3 | 0 | 0 | 197
23-0104432 | Placer | HORSESHOE 1101 | HORSESHOE 110151538 | Animal | 2023-08-15 08:35 | 8/15 - 8/21 | 2023-08-15 09:55 | 60.3261 | FTS | 22200 | 368 | 21 | 10 | 8 | 0 | 0 | 0 | 80
23-0104328 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121134 | Vegetation | 2023-08-15 05:24 | 8/15 - 8/21 | 2023-08-15 10:15 | 50.3856 | FTS | 11891 | 236 | 5 | 5 | 8 | 0 | 0 | 0 | 291
23-0104436 | Napa | CALISTOGA 1102 | CALISTOGA 1102279135 | 3rd Party | 2023-08-15 09:27 | 8/15 - 8/21 | 2023-08-15 10:33 | 66 | FTS | 4686 | 71 | 1 | 1 | 1 | 1 | 0 | 0 | 66
23-0104376 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown Cause | 2023-08-15 07:41 | 8/15 - 8/21 | 2023-08-15 12:28 | 287 | FTS | 144935 | 505 | 29 | 21 | 11 | 0 | 0 | 2 | 287
23-0104369 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-08-15 07:33 | 8/15 - 8/21 | 2023-08-15 12:44 | 162.663 | FTS | 73361 | 451 | 45 | 29 | 8 | 0 | 0 | 0 | 311
23-0104306 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Unknown Cause | 2023-08-14 22:11 | 8/15 - 8/21 | 2023-08-15 13:04 | 588.506 | FTS | 1224681 | 2081 | 174 | 135 | 32 | 2 | 0 | 2 | 893
23-0104530 | Calaveras | STANISLAUS 1701 | STANISLAUS 17011812 | Company Initiated | 2023-08-15 11:34 | 8/15 - 8/21 | 2023-08-15 13:18 | 96.5981 | FTS | 174746 | 1809 | 120 | 88 | 37 | 2 | 0 | 0 | 104
23-0104440 | Napa | CALISTOGA 1102 | CALISTOGA 110266730 | 3rd Party | 2023-08-15 09:28 | 8/15 - 8/21 | 2023-08-15 13:53 | 265 | FTS | 795 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 265
23-0104471 | Amador | IONE 1101 | IONE 1101510200 | Unknown Cause | 2023-08-15 10:31 | 8/15 - 8/21 | 2023-08-15 14:24 | 233 | FTS | 23766 | 102 | 4 | 2 | 2 | 0 | 0 | 1 | 233
23-0104279 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101502 | Equipment Failure/Involved | 2023-08-14 19:32 | 8/15 - 8/21 | 2023-08-15 16:41 | 1045.067 | FTS | 1092095 | 1045 | 60 | 47 | 23 | 0 | 0 | 0 | 1269
23-0104635 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101Y52 | Vegetation | 2023-08-15 13:49 | 8/15 - 8/21 | 2023-08-15 17:07 | 198 | FTS | 37818 | 191 | 1 | 1 | 25 | 0 | 0 | 0 | 198
23-0104720 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | Vegetation | 2023-08-15 15:37 | 8/15 - 8/21 | 2023-08-15 17:31 | 114 | FTS | 106818 | 937 | 71 | 46 | 12 | 0 | 0 | 1 | 114
23-0104686 | Nevada | GRASS VALLEY 1101 | GRASS VALLEY 1101CB | Equipment Failure/Involved | 2023-08-15 15:05 | 8/15 - 8/21 | 2023-08-15 17:52 | 167 | FTS | 176853 | 1059 | 65 | 52 | 19 | 3 | 0 | 2 | 167
23-0104776 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Company Initiated | 2023-08-15 17:38 | 8/15 - 8/21 | 2023-08-15 19:16 | 98 | FTS | 47824 | 488 | 9 | 7 | 13 | 3 | 0 | 0 | 98
23-0104750 | Humboldt | FORT SEWARD 1121 | FORT SEWARD 1121CB | Vegetation | 2023-08-15 16:38 | 8/15 - 8/21 | 2023-08-15 19:26 | 168 | FTS | 39312 | 234 | 11 | 7 | 11 | 4 | 0 | 0 | 168
23-0104796 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101277014 | Vegetation | 2023-08-15 18:33 | 8/15 - 8/21 | 2023-08-15 20:20 | 107 | FTS | 38948 | 364 | 3 | 3 | 27 | 0 | 0 | 0 | 107
23-0104780 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 1103CB | Unknown Cause | 2023-08-15 17:44 | 8/15 - 8/21 | 2023-08-15 20:47 | 182.2036 | FTS | 275674 | 1513 | 90 | 67 | 16 | 2 | 0 | 0 | 183
23-0104786 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Unknown Cause | 2023-08-15 17:47 | 8/15 - 8/21 | 2023-08-15 21:28 | 194.9073 | FTS | 168205 | 863 | 70 | 42 | 11 | 0 | 0 | 3 | 221
23-0104781 | Yuba | CHALLENGE 1101 | CHALLENGE 11015460 | Vegetation | 2023-08-15 17:47 | 8/15 - 8/21 | 2023-08-15 21:50 | 237.407 | FTS | 108495 | 457 | 28 | 17 | 7 | 0 | 0 | 0 | 243
23-0104770 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Company Initiated | 2023-08-15 17:27 | 8/15 - 8/21 | 2023-08-16 00:58 | 436.4677 | FTS | 1343011 | 3077 | 214 | 160 | 43 | 1 | 0 | 5 | 451
23-0104870 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 1103CB | Unknown Cause | 2023-08-16 05:53 | 8/15 - 8/21 | 2023-08-16 07:00 | 67 | FTS | 101371 | 1513 | 90 | 67 | 16 | 2 | 0 | 0 | 67
23-0104814 | Sacramento | IONE 1101 | IONE 1101CB | Equipment Failure/Involved | 2023-08-15 20:00 | 8/15 - 8/21 | 2023-08-16 08:11 | 202.2476 | FTS | 207506 | 1026 | 69 | 53 | 6 | 0 | 0 | 1 | 731
23-0104831 | Alameda | CASTRO VALLEY 1111 | CASTRO VALLEY 1111227862 | Equipment Failure/Involved | 2023-08-15 21:04 | 8/15 - 8/21 | 2023-08-16 10:09 | 184.0698 | FTS | 15830 | 86 | 5 | 5 | 1 | 0 | 0 | 0 | 785
23-0104930 | Lake | LUCERNE 1103 | LUCERNE 1103245134 | Animal | 2023-08-16 08:15 | 8/15 - 8/21 | 2023-08-16 11:24 | 189 | FTS | 10395 | 55 | 4 | 2 | 0 | 0 | 0 | 0 | 189
23-0105032 | Tuolumne | TAR FLAT 0402 | TAR FLAT 04023144 | Company Initiated | 2023-08-16 11:14 | 8/15 - 8/21 | 2023-08-16 11:38 | 24 | FTS | 5256 | 219 | 16 | 10 | 1 | 0 | 0 | 0 | 24
23-0104924 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 1103CB | Unknown Cause | 2023-08-16 07:57 | 8/15 - 8/21 | 2023-08-16 12:08 | 221.5321 | FTS | 335178 | 1513 | 90 | 67 | 16 | 2 | 0 | 0 | 251
23-0105026 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | Unknown Cause | 2023-08-16 11:04 | 8/15 - 8/21 | 2023-08-16 15:06 | 185.7057 | FTS | 172892 | 931 | 22 | 17 | 10 | 0 | 0 | 6 | 242
23-0105087 | Nevada | HIGGINS 1103 | HIGGINS 110350072 | 3rd Party | 2023-08-16 12:46 | 8/15 - 8/21 | 2023-08-16 15:20 | 154 | FTS | 100100 | 650 | 46 | 27 | 3 | 0 | 0 | 11 | 154
23-0104851 | Napa | CALISTOGA 1101 | CALISTOGA 1101122350 | Equipment Failure/Involved | 2023-08-15 22:50 | 8/15 - 8/21 | 2023-08-16 17:21 | 205.4962 | FTS | 26920 | 131 | 6 | 2 | 7 | 0 | 0 | 1 | 1111
23-0105204 | Tulare | SAND CREEK 1103 | SAND CREEK 11037110 | Unknown Cause | 2023-08-16 15:29 | 8/15 - 8/21 | 2023-08-16 18:01 | 152 | FTS | 25840 | 170 | 5 | 3 | 8 | 0 | 0 | 0 | 152
23-0105268 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101483444 | Unknown Cause | 2023-08-16 17:20 | 8/15 - 8/21 | 2023-08-16 19:00 | 76.4985 | FTS | 226053 | 2955 | 23 | 14 | 73 | 6 | 0 | 1 | 100
23-0105288 | Fresno | SAND CREEK 1103 | SAND CREEK 1103799118 | Unknown Cause | 2023-08-16 17:58 | 8/15 - 8/21 | 2023-08-16 19:06 | 68 | FTS | 59364 | 873 | 95 | 55 | 8 | 0 | 0 | 0 | 68
23-0104820 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101277014 | Vegetation | 2023-08-15 20:34 | 8/15 - 8/21 | 2023-08-16 19:29 | 830.9148 | FTS | 302453 | 364 | 3 | 3 | 27 | 0 | 0 | 0 | 1375
23-0105260 | Humboldt | FORT SEWARD 1121 | FORT SEWARD 1121CB | Environmental/External | 2023-08-16 16:53 | 8/15 - 8/21 | 2023-08-16 20:27 | 214 | FTS | 18404 | 86 | 1 | 1 | 6 | 3 | 0 | 0 | 214
23-0105179 | Monterey | SAN ARDO 1102 | SAN ARDO 11027030 | Equipment Failure/Involved | 2023-08-16 15:06 | 8/15 - 8/21 | 2023-08-17 00:46 | 231.2642 | FTS | 24514 | 106 | 1 | 0 | 8 | 0 | 0 | 0 | 580
23-0105305 | Tehama | VOLTA 1101 | VOLTA 110165764 | Unknown Cause | 2023-08-16 19:35 | 8/15 - 8/21 | 2023-08-17 02:05 | 390 | FTS | 56940 | 146 | 10 | 8 | 15 | 2 | 0 | 0 | 390
23-0105148 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR243 | 3rd Party | 2023-08-16 14:16 | 8/15 - 8/21 | 2023-08-17 02:24 | 149.2087 | FTS | 58639 | 393 | 31 | 15 | 12 | 0 | 0 | 1 | 728
23-0105296 | Tehama | VOLTA 1101 | VOLTA 11011596 | Unknown Cause | 2023-08-16 18:48 | 8/15 - 8/21 | 2023-08-17 02:44 | 132.2597 | FTS | 98798 | 747 | 36 | 27 | 14 | 1 | 0 | 0 | 476
23-0105266 | Alameda | CAYETANO 2111 | CAYETANO 2111CB | Equipment Failure/Involved | 2023-08-16 17:02 | 8/15 - 8/21 | 2023-08-17 04:01 | 384.1873 | FTS | 802183 | 2088 | 61 | 40 | 23 | 5 | 0 | 0 | 659
23-0105366 | Tehama | RED BLUFF 1101 | RED BLUFF 110176020 | Unknown Cause | 2023-08-17 01:44 | 8/15 - 8/21 | 2023-08-17 04:50 | 104.3203 | FTS | 29314 | 281 | 37 | 24 | 2 | 0 | 0 | 0 | 186
23-0105357 | San Joaquin | HERDLYN 1102 | HERDLYN 1102608254 | 3rd Party | 2023-08-16 23:17 | 8/15 - 8/21 | 2023-08-17 07:12 | 233.1029 | FTS | 154081 | 661 | 49 | 27 | 33 | 3 | 0 | 0 | 475
23-0105378 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Unknown Cause | 2023-08-17 06:06 | 8/15 - 8/21 | 2023-08-17 07:57 | 81.8824 | FTS | 13920 | 170 | 11 | 7 | 13 | 0 | 0 | 1 | 111
23-0105390 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y36 | Unknown Cause | 2023-08-17 06:37 | 8/15 - 8/21 | 2023-08-17 08:02 | 75.5882 | FTS | 21845 | 289 | 4 | 2 | 18 | 1 | 0 | 0 | 85
23-0105520 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2023-08-17 10:22 | 8/15 - 8/21 | 2023-08-17 12:11 | 109 | FTS | 981 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 109
23-0105379 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Unknown Cause | 2023-08-17 06:01 | 8/15 - 8/21 | 2023-08-17 12:23 | 276.9717 | FTS | 205236 | 741 | 39 | 23 | 17 | 3 | 0 | 1 | 382
23-0105321 | Contra Costa | ROSSMOOR 1109 | ROSSMOOR 1109847274 | Vegetation | 2023-08-16 13:18 | 8/15 - 8/21 | 2023-08-17 14:53 | 330.5882 | FTS | 50580 | 153 | 8 | 6 | 0 | 0 | 0 | 1 | 1535
23-0105633 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Equipment Failure/Involved | 2023-08-17 13:53 | 8/15 - 8/21 | 2023-08-17 18:39 | 91 | FTS | 3640 | 40 | 3 | 2 | 0 | 0 | 0 | 0 | 286
23-0105597 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 1101528344 | Vegetation | 2023-08-17 12:13 | 8/15 - 8/21 | 2023-08-17 19:42 | 189.4868 | FTS | 28802 | 152 | 6 | 5 | 5 | 5 | 0 | 2 | 449
23-0105744 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102CB | Equipment Failure/Involved | 2023-08-17 16:47 | 8/15 - 8/21 | 2023-08-17 20:11 | 170.3857 | FTS | 567214 | 3329 | 214 | 152 | 68 | 22 | 2 | 2 | 204
23-0105748 | Placer | PENRYN 1103 | PENRYN 1103660 | Equipment Failure/Involved | 2023-08-17 16:46 | 8/15 - 8/21 | 2023-08-17 22:34 | 86.1586 | FTS | 39116 | 454 | 32 | 19 | 3 | 0 | 0 | 4 | 348
23-0105798 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210611006 | Animal | 2023-08-17 21:07 | 8/15 - 8/21 | 2023-08-17 22:39 | 82.0203 | FTS | 161744 | 1972 | 194 | 158 | 29 | 1 | 0 | 7 | 92
23-0105624 | Placer | LINCOLN 1104 | LINCOLN 11042070 | Vegetation | 2023-08-17 13:39 | 8/15 - 8/21 | 2023-08-17 23:28 | 95.5539 | FTS | 32775 | 343 | 26 | 20 | 2 | 0 | 0 | 5 | 589
23-0105800 | Shasta | STILLWATER 1102 | STILLWATER 1102CB | Unknown Cause | 2023-08-17 21:15 | 8/15 - 8/21 | 2023-08-17 23:59 | 164 | FTS | 232060 | 1415 | 134 | 95 | 16 | 0 | 0 | 0 | 164
23-0105765 | Tuolumne | CURTIS 1703 | CURTIS 17039240 | 3rd Party | 2023-08-17 17:27 | 8/15 - 8/21 | 2023-08-18 01:14 | 241.3043 | FTS | 451963 | 1873 | 131 | 101 | 22 | 1 | 0 | 1 | 467
23-0105780 | Mendocino | UKIAH 1111 | UKIAH 1111433984 | Vegetation | 2023-08-17 19:29 | 8/15 - 8/21 | 2023-08-18 01:44 | 64.6775 | FTS | 75608 | 1169 | 45 | 24 | 21 | 6 | 0 | 0 | 375
23-0105845 | Humboldt | RIO DELL 1101 | RIO DELL 11011504 | Vegetation | 2023-08-17 23:40 | 8/15 - 8/21 | 2023-08-18 09:25 | 177.4706 | FTS | 45255 | 255 | 10 | 7 | 3 | 0 | 0 | 0 | 585
23-0105787 | Monterey | JOLON 1102 | JOLON 11027070 | Unknown Cause | 2023-08-17 20:03 | 8/15 - 8/21 | 2023-08-18 09:27 | 218.7104 | FTS | 56646 | 259 | 7 | 6 | 19 | 0 | 0 | 3 | 804
23-0105926 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | Unknown Cause | 2023-08-18 08:04 | 8/15 - 8/21 | 2023-08-18 11:01 | 177 | FTS | 207621 | 1173 | 116 | 78 | 18 | 0 | 0 | 3 | 177
23-0106064 | Colusa | ELK CREEK 1101 | ELK CREEK 11012008 | Animal | 2023-08-18 10:56 | 8/15 - 8/21 | 2023-08-18 13:50 | 96.7289 | FTS | 32114 | 332 | 28 | 19 | 15 | 0 | 0 | 0 | 174
23-0106061 | Napa | NAPA 1112 | NAPA 11121302 | Unknown Cause | 2023-08-18 10:53 | 8/15 - 8/21 | 2023-08-18 14:13 | 86.9492 | FTS | 47909 | 551 | 31 | 21 | 9 | 0 | 0 | 11 | 200
23-0105878 | Amador | PINE GROVE 1101 | PINE GROVE 110152088 | Animal | 2023-08-18 07:16 | 8/15 - 8/21 | 2023-08-18 14:50 | 129.8802 | FTS | 144167 | 1110 | 95 | 67 | 15 | 0 | 0 | 15 | 454
23-0105855 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111349826 | Vegetation | 2023-08-18 05:30 | 8/15 - 8/21 | 2023-08-18 15:05 | 77.7469 | FTS | 183716 | 2363 | 81 | 54 | 40 | 4 | 0 | 14 | 575
23-0106223 | Amador | PINE GROVE 1101 | PINE GROVE 11013170 | Company Initiated | 2023-08-18 15:22 | 8/15 - 8/21 | 2023-08-18 15:44 | 22 | FTS | 15202 | 691 | 49 | 38 | 15 | 0 | 0 | 5 | 22
23-0106152 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown Cause | 2023-08-18 13:44 | 8/15 - 8/21 | 2023-08-18 15:59 | 74.9185 | FTS | 27570 | 368 | 13 | 10 | 20 | 3 | 0 | 0 | 135
23-0106231 | Santa Cruz | CAMP EVERS 2105 | BIG BASIN 110195690 | Company Initiated | 2023-08-18 15:42 | 8/15 - 8/21 | 2023-08-18 16:18 | 32.6685 | FTS | 131654 | 4030 | 318 | 251 | 68 | 4 | 0 | 2 | 36
23-0106150 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101806 | Unknown Cause | 2023-08-18 13:41 | 8/15 - 8/21 | 2023-08-18 17:17 | 216 | FTS | 17928 | 83 | 3 | 2 | 1 | 0 | 0 | 0 | 216
23-0105854 | Santa Clara | HICKS 2101 | HICKS 2101CB | Equipment Failure/Involved | 2023-08-18 05:02 | 8/15 - 8/21 | 2023-08-18 17:40 | 476.6036 | FTS | 1547532 | 3247 | 223 | 150 | 46 | 2 | 0 | 0 | 758
23-0105849 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Equipment Failure/Involved | 2023-08-18 02:00 | 8/15 - 8/21 | 2023-08-18 19:29 | 139.9712 | FTS | 116596 | 833 | 86 | 65 | 14 | 1 | 0 | 24 | 1049
23-0106276 | Kern | TEJON 1102 | TEJON 11024525 | Unknown Cause | 2023-08-18 19:33 | 8/15 - 8/21 | 2023-08-18 22:25 | 172 | FTS | 3784 | 22 | 0 | 0 | 4 | 0 | 0 | 0 | 172
23-0104267 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108CB | Equipment Failure/Involved | 2023-08-14 18:40 | 8/15 - 8/21 | 2023-08-19 01:18 | 422.8703 | FTS | 3337715 | 7893 | 360 | 238 | 129 | 26 | 0 | 0 | 6158
23-0106288 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Vegetation | 2023-08-18 21:33 | 8/15 - 8/21 | 2023-08-19 02:00 | 177.5731 | FTS | 106899 | 602 | 31 | 20 | 5 | 0 | 0 | 6 | 267
23-0085577 | Contra Costa | CLAYTON 2215 | CLAYTON 2215880066 | Company Initiated | 2023-08-19 10:14 | 8/15 - 8/21 | 2023-08-19 11:56 | 102 | FTS | 204 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 102
23-0106350 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | 3rd Party | 2023-08-19 11:12 | 8/15 - 8/21 | 2023-08-19 15:36 | 264 | FTS | 3432 | 13 | 0 | 0 | 1 | 0 | 0 | 0 | 264
23-0106415 | Nevada | NARROWS 2105 | NARROWS 21052426 | Vegetation | 2023-08-19 16:15 | 8/15 - 8/21 | 2023-08-19 17:01 | 38.3546 | FTS | 81120 | 2115 | 190 | 109 | 24 | 4 | 0 | 19 | 46
23-0106403 | Kern | KERN OIL 1106 | KERN OIL 11063301 | Unknown Cause | 2023-08-19 15:15 | 8/15 - 8/21 | 2023-08-19 17:35 | 73.281 | FTS | 17734 | 242 | 9 | 9 | 14 | 0 | 0 | 0 | 140
23-0106399 | Shasta | MC ARTHUR 1101 | MC ARTHUR 110138998 | Unknown Cause | 2023-08-19 15:05 | 8/15 - 8/21 | 2023-08-19 18:09 | 117.8762 | FTS | 74262 | 630 | 29 | 22 | 23 | 3 | 0 | 0 | 184
23-0106418 | Humboldt | BRIDGEVILLE 1102 | BRIDGEVILLE 110255612 | Environmental/External | 2023-08-19 16:28 | 8/15 - 8/21 | 2023-08-19 19:42 | 194 | FTS | 10670 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 194
23-0106316 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Vegetation | 2023-08-19 01:49 | 8/15 - 8/21 | 2023-08-19 20:09 | 1100 | FTS | 536800 | 488 | 9 | 7 | 13 | 3 | 0 | 0 | 1100
23-0106462 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101929360 | Vegetation | 2023-08-19 19:21 | 8/15 - 8/21 | 2023-08-19 20:31 | 69.0195 | FTS | 198155 | 2871 | 240 | 166 | 45 | 0 | 0 | 1 | 70
23-0106472 | Colusa | MAXWELL 1105 | MAXWELL 11053008 | Unknown Cause | 2023-08-19 19:53 | 8/15 - 8/21 | 2023-08-19 21:43 | 108.2857 | FTS | 5306 | 49 | 1 | 0 | 4 | 0 | 0 | 0 | 110
23-0106364 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106974130 | Vegetation | 2023-08-19 12:49 | 8/15 - 8/21 | 2023-08-19 22:04 | 129.7253 | FTS | 11805 | 91 | 11 | 11 | 1 | 0 | 0 | 0 | 555
23-0106493 | Tuolumne | CURTIS 1702 | CURTIS 170210940 | Environmental/External | 2023-08-19 20:41 | 8/15 - 8/21 | 2023-08-19 23:27 | 166 | FTS | 105410 | 635 | 67 | 45 | 3 | 1 | 0 | 0 | 166
23-0106390 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Animal | 2023-08-19 14:15 | 8/15 - 8/21 | 2023-08-19 23:37 | 117.1995 | FTS | 87548 | 747 | 76 | 58 | 10 | 1 | 0 | 20 | 562
23-0106513 | Placer | PENRYN 1103 | PENRYN 110351658 | Unknown Cause | 2023-08-19 22:16 | 8/15 - 8/21 | 2023-08-20 00:08 | 105.5404 | FTS | 71873 | 681 | 48 | 35 | 8 | 0 | 0 | 9 | 112
23-0106559 | Placer | PENRYN 1107 | PENRYN 1107CB | Vegetation | 2023-08-20 02:05 | 8/15 - 8/21 | 2023-08-20 03:10 | 65 | FTS | 185575 | 2855 | 213 | 135 | 44 | 7 | 0 | 11 | 65
23-0106485 | Kern | ANTELOPE 1101 | ANTELOPE 11013609 | Unknown Cause | 2023-08-19 20:55 | 8/15 - 8/21 | 2023-08-20 06:48 | 593 | FTS | 26685 | 45 | 3 | 0 | 7 | 0 | 0 | 0 | 593
23-0106484 | Tuolumne | CURTIS 1705 | CURTIS 170565908 | Environmental/External | 2023-08-19 20:38 | 8/15 - 8/21 | 2023-08-20 08:51 | 245.7577 | FTS | 168344 | 685 | 67 | 43 | 7 | 6 | 0 | 0 | 733
23-0106581 | Placer | PENRYN 1103 | PENRYN 110351658 | Unknown Cause | 2023-08-20 07:00 | 8/15 - 8/21 | 2023-08-20 09:07 | 90.2217 | FTS | 61441 | 681 | 48 | 35 | 8 | 0 | 0 | 9 | 127
23-0106401 | Kern | CAL WATER 1102 | CAL WATER 1102920714 | Equipment Failure/Involved | 2023-08-19 15:11 | 8/15 - 8/21 | 2023-08-20 09:28 | 588.5556 | FTS | 31782 | 54 | 0 | 0 | 11 | 0 | 0 | 0 | 1097
23-0106402 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Environmental/External | 2023-08-19 15:12 | 8/15 - 8/21 | 2023-08-20 09:35 | 1103 | FTS | 144493 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 1103
23-0106494 | Kings | AVENAL 2101 | AVENAL 21019810 | Animal | 2023-08-19 21:22 | 8/15 - 8/21 | 2023-08-20 09:35 | 528.7678 | FTS | 1555106 | 2941 | 124 | 78 | 24 | 16 | 0 | 0 | 733
23-0106585 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102429530 | Unknown Cause | 2023-08-20 07:22 | 8/15 - 8/21 | 2023-08-20 10:19 | 177 | FTS | 74871 | 423 | 10 | 3 | 8 | 1 | 0 | 1 | 177
23-0106467 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 210110000 | Environmental/External | 2023-08-19 19:36 | 8/15 - 8/21 | 2023-08-20 12:01 | 950.6047 | FTS | 245256 | 258 | 23 | 14 | 7 | 0 | 0 | 0 | 985
23-0106483 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Unknown Cause | 2023-08-19 20:37 | 8/15 - 8/21 | 2023-08-20 12:15 | 857.244 | FTS | 498916 | 582 | 58 | 44 | 3 | 4 | 0 | 2 | 938
23-0106556 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Vegetation | 2023-08-20 02:10 | 8/15 - 8/21 | 2023-08-20 12:23 | 140.6298 | FTS | 121926 | 867 | 74 | 54 | 7 | 0 | 0 | 6 | 613
23-0106454 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Environmental/External | 2023-08-19 18:46 | 8/15 - 8/21 | 2023-08-20 12:25 | 192.5823 | FTS | 286755 | 1489 | 179 | 136 | 39 | 2 | 0 | 0 | 1059
23-0106497 | Tuolumne | CURTIS 1705 | CURTIS 17058170 | Environmental/External | 2023-08-19 20:41 | 8/15 - 8/21 | 2023-08-20 12:49 | 255.2036 | FTS | 127857 | 501 | 58 | 45 | 4 | 0 | 0 | 0 | 968
23-0106487 | Calaveras | FROGTOWN 1702 | FROGTOWN 17027134 | 3rd Party | 2023-08-19 20:49 | 8/15 - 8/21 | 2023-08-20 12:56 | 948.7736 | FTS | 150855 | 159 | 4 | 3 | 1 | 0 | 0 | 0 | 967
23-0106488 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Equipment Failure/Involved | 2023-08-19 20:53 | 8/15 - 8/21 | 2023-08-20 13:11 | 977.4955 | FTS | 3010686 | 3080 | 214 | 160 | 43 | 1 | 0 | 5 | 978
23-0106520 | Tuolumne | RACETRACK 1703 | RACETRACK 170310870 | Equipment Failure/Involved | 2023-08-19 22:56 | 8/15 - 8/21 | 2023-08-20 13:32 | 203.0044 | FTS | 45676 | 225 | 13 | 10 | 9 | 0 | 1 | 0 | 876
23-0106625 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Unknown Cause | 2023-08-20 11:20 | 8/15 - 8/21 | 2023-08-20 13:46 | 146 | FTS | 19126 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 146
23-0106644 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | Animal | 2023-08-20 13:06 | 8/15 - 8/21 | 2023-08-20 14:24 | 78 | FTS | 7722 | 99 | 1 | 1 | 1 | 0 | 0 | 0 | 78
23-0106672 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207M501R | 3rd Party | 2023-08-20 14:18 | 8/15 - 8/21 | 2023-08-20 15:50 | 92 | FTS | 93104 | 1012 | 50 | 32 | 6 | 0 | 0 | 0 | 92
23-0106523 | Napa | SILVERADO 2105 | SILVERADO 2105131568 | Vegetation | 2023-08-19 23:19 | 8/15 - 8/21 | 2023-08-20 17:24 | 257.0167 | FTS | 107947 | 420 | 13 | 9 | 4 | 0 | 0 | 0 | 1085
23-0106473 | Kern | DEVILS DEN 1101 | DEVILS DEN 1101CB | Unknown Cause | 2023-08-19 20:07 | 8/15 - 8/21 | 2023-08-20 17:30 | 555.5522 | FTS | 37222 | 67 | 0 | 0 | 8 | 0 | 0 | 0 | 1283
23-0106708 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Animal | 2023-08-20 16:44 | 8/15 - 8/21 | 2023-08-20 17:48 | 64 | FTS | 6528 | 102 | 2 | 2 | 12 | 11 | 0 | 0 | 64
23-0106474 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210576694 | Environmental/External | 2023-08-19 20:08 | 8/15 - 8/21 | 2023-08-20 17:55 | 588.4545 | FTS | 19419 | 33 | 6 | 3 | 0 | 0 | 0 | 0 | 1307
23-0106677 | Tuolumne | CURTIS 1703 | CURTIS 17036064 | Animal | 2023-08-20 14:52 | 8/15 - 8/21 | 2023-08-20 17:56 | 184 | FTS | 70472 | 383 | 35 | 29 | 4 | 0 | 0 | 0 | 184
23-0106496 | Calaveras | SALT SPRINGS 2102 | SALT SPRINGS 21023118 | Environmental/External | 2023-08-19 21:11 | 8/15 - 8/21 | 2023-08-20 18:23 | 1047.1395 | FTS | 2108939 | 2014 | 56 | 40 | 36 | 0 | 0 | 0 | 1272
23-0106455 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Vegetation | 2023-08-19 18:56 | 8/15 - 8/21 | 2023-08-20 18:46 | 116.179 | FTS | 193438 | 1665 | 179 | 119 | 17 | 2 | 0 | 0 | 1430
23-0106710 | Contra Costa | LAKEWOOD 2109 | LAKEWOOD 2109432198 | Unknown Cause | 2023-08-20 16:55 | 8/15 - 8/21 | 2023-08-20 20:35 | 220 | FTS | 31240 | 142 | 11 | 7 | 4 | 0 | 1 | 0 | 220
23-0106734 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A46 | Unknown Cause | 2023-08-20 18:34 | 8/15 - 8/21 | 2023-08-20 20:36 | 54.9294 | FTS | 44328 | 807 | 23 | 17 | 11 | 1 | 0 | 0 | 122
23-0106738 | Tuolumne | RACETRACK 1703 | RACETRACK 17036014 | Equipment Failure/Involved | 2023-08-20 18:44 | 8/15 - 8/21 | 2023-08-20 20:44 | 118.2461 | FTS | 53329 | 451 | 45 | 29 | 8 | 0 | 0 | 0 | 120
23-0106712 | Amador | MARTELL 1101 | MARTELL 110111244 | Vegetation | 2023-08-20 17:02 | 8/15 - 8/21 | 2023-08-20 23:52 | 100.7793 | FTS | 67119 | 666 | 69 | 48 | 5 | 0 | 0 | 10 | 410
23-0106722 | Marin | SAN RAFAEL 1108 | SAN RAFAEL 11081262 | Vegetation | 2023-08-20 17:26 | 8/15 - 8/21 | 2023-08-21 01:13 | 108.1268 | FTS | 84447 | 781 | 25 | 13 | 6 | 3 | 0 | 1 | 467
23-0106783 | Monterey | DEL MONTE 2104 | DEL MONTE 21049096 | Unknown Cause | 2023-08-21 00:58 | 8/15 - 8/21 | 2023-08-21 02:42 | 58.9783 | FTS | 157590 | 2672 | 101 | 71 | 101 | 6 | 2 | 1 | 104
23-0106682 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 210542348 | 3rd Party | 2023-08-20 15:02 | 8/15 - 8/21 | 2023-08-21 02:56 | 90.7753 | FTS | 357927 | 3943 | 284 | 209 | 41 | 8 | 1 | 5 | 714
23-0106798 | Shasta | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Unknown Cause | 2023-08-21 02:23 | 8/15 - 8/21 | 2023-08-21 03:45 | 82 | FTS | 20008 | 244 | 16 | 13 | 3 | 0 | 0 | 0 | 82
23-0106826 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Unknown Cause | 2023-08-21 07:02 | 8/15 - 8/21 | 2023-08-21 07:59 | 57 | FTS | 7467 | 131 | 4 | 4 | 4 | 0 | 0 | 0 | 57
23-0106732 | Nevada | NARROWS 2105 | NARROWS 2105CB | Animal | 2023-08-20 18:23 | 8/15 - 8/21 | 2023-08-21 08:00 | 219.9236 | FTS | 831531 | 3781 | 314 | 188 | 41 | 4 | 0 | 31 | 817
23-0106762 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown Cause | 2023-08-20 21:55 | 8/15 - 8/21 | 2023-08-21 08:30 | 635 | FTS | 187325 | 295 | 25 | 20 | 2 | 0 | 0 | 0 | 635
23-0106827 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102776178 | Unknown Cause | 2023-08-21 07:04 | 8/15 - 8/21 | 2023-08-21 08:59 | 115 | FTS | 1035 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 115
23-0106803 | Placer | AUBURN 1102 | AUBURN 1102251946 | Equipment Failure/Involved | 2023-08-21 05:02 | 8/15 - 8/21 | 2023-08-21 09:10 | 196.8478 | FTS | 195273 | 992 | 49 | 29 | 11 | 2 | 0 | 0 | 248
23-0106757 | Alameda | CASTRO VALLEY 1108 | CASTRO VALLEY 1108343456 | Unknown Cause | 2023-08-20 20:52 | 8/15 - 8/21 | 2023-08-21 09:35 | 225.8715 | FTS | 418314 | 1852 | 151 | 115 | 29 | 3 | 0 | 1 | 763
23-0106490 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Environmental/External | 2023-08-19 21:05 | 8/15 - 8/21 | 2023-08-21 10:15 | 959.7077 | FTS | 1779298 | 1854 | 126 | 97 | 26 | 6 | 0 | 2 | 2230
23-0106639 | Kern | LAMONT 1104 | LAMONT 11043855 | Company Initiated | 2023-08-20 12:40 | 8/15 - 8/21 | 2023-08-21 10:30 | 130.7556 | HLT | 11768 | 90 | 1 | 0 | 0 | 0 | 0 | 0 | 1310
23-0106918 | Tuolumne | CURTIS 1705 | CURTIS 170565908 | Animal | 2023-08-21 09:23 | 8/15 - 8/21 | 2023-08-21 10:35 | 32.8528 | FTS | 22537 | 686 | 67 | 43 | 7 | 6 | 0 | 0 | 72
23-0106836 | Placer | PLACER 1103 | PLACER 1103CB | Equipment Failure/Involved | 2023-08-21 07:16 | 8/15 - 8/21 | 2023-08-21 10:52 | 168.3113 | FTS | 389304 | 2313 | 156 | 85 | 29 | 3 | 0 | 0 | 216
23-0106730 | Sonoma | MOLINO 1101 | MOLINO 1101322 | Vegetation | 2023-08-20 18:14 | 8/15 - 8/21 | 2023-08-21 10:54 | 1000 | FTS | 375000 | 375 | 17 | 14 | 6 | 0 | 0 | 4 | 1000
23-0106886 | Napa | SILVERADO 2104 | SILVERADO 2104722 | Unknown Cause | 2023-08-21 08:51 | 8/15 - 8/21 | 2023-08-21 11:18 | 147 | FTS | 77028 | 524 | 34 | 25 | 17 | 2 | 1 | 2 | 147
23-0106776 | Sonoma | COTATI 1105 | COTATI 1105616 | Unknown Cause | 2023-08-20 23:29 | 8/15 - 8/21 | 2023-08-21 11:31 | 182.9825 | FTS | 41903 | 229 | 4 | 3 | 6 | 0 | 0 | 0 | 722
23-0106935 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | Vegetation | 2023-08-21 09:46 | 8/15 - 8/21 | 2023-08-21 11:46 | 120 | FTS | 64440 | 537 | 17 | 8 | 9 | 1 | 0 | 2 | 120
23-0106888 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | Equipment Failure/Involved | 2023-08-21 08:49 | 8/15 - 8/21 | 2023-08-21 12:31 | 37.2326 | FTS | 19845 | 533 | 28 | 15 | 14 | 2 | 0 | 0 | 222
23-0106815 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR494 | Equipment Failure/Involved | 2023-08-21 06:28 | 8/15 - 8/21 | 2023-08-21 12:51 | 177.6432 | FTS | 700092 | 3941 | 284 | 209 | 41 | 8 | 1 | 5 | 383
23-0106973 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Unknown Cause | 2023-08-21 10:27 | 8/15 - 8/21 | 2023-08-21 13:11 | 164 | FTS | 11316 | 69 | 4 | 3 | 6 | 2 | 0 | 0 | 164
23-0107021 | Mendocino | GUALALA 1112 | GUALALA 1112CB | Unknown Cause | 2023-08-21 11:36 | 8/15 - 8/21 | 2023-08-21 13:43 | 125.5266 | FTS | 476750 | 3798 | 137 | 104 | 55 | 0 | 0 | 0 | 127
23-0107070 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Company Initiated | 2023-08-21 13:07 | 8/15 - 8/21 | 2023-08-21 13:48 | 41 | FTS | 8446 | 206 | 13 | 9 | 6 | 0 | 0 | 4 | 41
23-0106986 | Butte | BUTTE 1105 | BUTTE 1105612016 | 3rd Party | 2023-08-21 10:37 | 8/15 - 8/21 | 2023-08-21 15:13 | 183.901 | FTS | 37148 | 202 | 16 | 10 | 2 | 1 | 0 | 3 | 276
23-0107184 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Unknown Cause | 2023-08-21 15:18 | 8/15 - 8/21 | 2023-08-21 15:37 | 18.8389 | FTS | 16258 | 863 | 70 | 42 | 11 | 0 | 0 | 3 | 19
23-0107094 | Marin | ALTO 1124 | ALTO 1124432 | Vegetation | 2023-08-21 13:42 | 8/15 - 8/21 | 2023-08-21 16:00 | 138 | FTS | 94530 | 685 | 22 | 14 | 7 | 0 | 0 | 0 | 138
23-0107149 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 11071276 | Vegetation | 2023-08-21 14:27 | 8/15 - 8/21 | 2023-08-21 16:12 | 105 | FTS | 31395 | 299 | 15 | 9 | 3 | 0 | 0 | 0 | 105
23-0106953 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101829164 | Company Initiated | 2023-08-21 09:52 | 8/22 - 8/28 | 2023-08-21 17:11 | 177.3039 | FTS | 369856 | 2086 | 94 | 66 | 37 | 7 | 0 | 5 | 439
23-0107195 | Shasta | GIRVAN 1101 | GIRVAN 11011636 | Animal | 2023-08-21 15:35 | 8/22 - 8/28 | 2023-08-21 17:11 | 55.0548 | FTS | 64249 | 1167 | 98 | 68 | 30 | 6 | 0 | 0 | 96
23-0106735 | Humboldt | WILLOW CREEK 1102 | WILLOW CREEK 110347966 | Unknown Cause | 2023-08-20 18:36 | 8/22 - 8/28 | 2023-08-21 17:15 | 831.8013 | FTS | 1377463 | 1656 | 99 | 75 | 19 | 5 | 0 | 0 | 1359
23-0107224 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Animal | 2023-08-21 16:36 | 8/22 - 8/28 | 2023-08-21 17:41 | 32.8694 | FTS | 19130 | 582 | 58 | 44 | 3 | 4 | 0 | 2 | 65
23-0107214 | Placer | PENRYN 1107 | PENRYN 1107CB | Vegetation | 2023-08-21 15:59 | 8/22 - 8/28 | 2023-08-21 17:58 | 119 | FTS | 343672 | 2888 | 214 | 135 | 44 | 7 | 0 | 11 | 119
23-0107209 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Vegetation | 2023-08-21 15:38 | 8/22 - 8/28 | 2023-08-21 19:27 | 62.6031 | FTS | 76814 | 1227 | 99 | 63 | 13 | 0 | 0 | 3 | 229
23-0107069 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052210 | 3rd Party | 2023-08-21 13:07 | 8/22 - 8/28 | 2023-08-21 20:07 | 420 | FTS | 370440 | 882 | 62 | 42 | 16 | 0 | 0 | 2 | 420
23-0106875 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Equipment Failure/Involved | 2023-08-21 08:38 | 8/22 - 8/28 | 2023-08-21 21:39 | 771.7869 | FTS | 376632 | 488 | 9 | 7 | 13 | 3 | 0 | 0 | 781
23-0106828 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Equipment Failure/Involved | 2023-08-21 07:03 | 8/22 - 8/28 | 2023-08-21 23:58 | 258.738 | FTS | 59251 | 229 | 3 | 1 | 9 | 0 | 0 | 0 | 1015
23-0107311 | Sonoma | IGNACIO 1104 | IGNACIO 1104469764 | Animal | 2023-08-21 22:44 | 8/22 - 8/28 | 2023-08-22 00:41 | 117 | FTS | 34281 | 293 | 2 | 2 | 15 | 0 | 0 | 0 | 117
23-0107326 | Fresno | SHEPHERD 2111 | SHEPHERD 2111537008 | Vegetation | 2023-08-22 00:53 | 8/22 - 8/28 | 2023-08-22 05:33 | 101.6 | FTS | 56896 | 560 | 44 | 26 | 12 | 0 | 0 | 1 | 280
23-0107212 | Placer | DRUM 1101 | DRUM 1101CB | Unknown Cause | 2023-08-21 15:46 | 8/22 - 8/28 | 2023-08-22 09:20 | 844.7129 | FTS | 170632 | 202 | 8 | 4 | 19 | 1 | 0 | 1 | 1054
23-0107296 | Fresno | DUNLAP 1103 | DUNLAP 1103CB | Environmental/External | 2023-08-21 21:51 | 8/22 - 8/28 | 2023-08-22 09:22 | 690.0306 | FTS | 67623 | 98 | 1 | 1 | 5 | 0 | 0 | 0 | 691
23-0107295 | Fresno | DUNLAP 1103 | DUNLAP 11037220 | Environmental/External | 2023-08-21 21:51 | 8/22 - 8/28 | 2023-08-22 10:06 | 735 | FTS | 409395 | 557 | 36 | 26 | 5 | 3 | 0 | 0 | 735
23-0107431 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Animal | 2023-08-22 08:45 | 8/22 - 8/28 | 2023-08-22 10:11 | 86 | FTS | 26402 | 307 | 19 | 17 | 10 | 5 | 0 | 0 | 86
23-0107498 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102851902 | Equipment Failure/Involved | 2023-08-22 10:17 | 8/22 - 8/28 | 2023-08-22 10:50 | 31.7194 | FTS | 84564 | 2666 | 195 | 141 | 40 | 6 | 0 | 2 | 33
23-0107291 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | Environmental/External | 2023-08-21 21:40 | 8/22 - 8/28 | 2023-08-22 11:14 | 814 | FTS | 227920 | 280 | 15 | 14 | 2 | 0 | 0 | 0 | 814
23-0107354 | Contra Costa | CLAYTON 2212 | CLAYTON 2212681608 | Company Initiated | 2023-08-22 06:27 | 8/22 - 8/28 | 2023-08-22 12:05 | 265.5074 | FTS | 142843 | 538 | 42 | 27 | 45 | 0 | 0 | 5 | 338
23-0107528 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052100 | Company Initiated | 2023-08-22 11:01 | 8/22 - 8/28 | 2023-08-22 12:07 | 66 | FTS | 132132 | 2002 | 127 | 85 | 32 | 0 | 0 | 13 | 66
23-0107466 | Napa | NAPA 1112 | NAPA 11121302 | Unknown Cause | 2023-08-22 09:39 | 8/22 - 8/28 | 2023-08-22 12:14 | 55.1978 | FTS | 30414 | 551 | 31 | 21 | 9 | 0 | 0 | 11 | 155
23-0107437 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown Cause | 2023-08-22 08:53 | 8/22 - 8/28 | 2023-08-22 12:16 | 90.9538 | FTS | 155440 | 1709 | 96 | 76 | 19 | 2 | 0 | 12 | 203
23-0107693 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110170 | Unknown Cause | 2023-08-22 14:55 | 8/22 - 8/28 | 2023-08-22 17:11 | 136 | FTS | 28288 | 208 | 14 | 6 | 7 | 0 | 0 | 0 | 136
23-0107385 | Solano | VACAVILLE 1111 | VACAVILLE 1111CB | 3rd Party | 2023-08-22 07:16 | 8/22 - 8/28 | 2023-08-22 20:04 | 123.2925 | FTS | 267668 | 2171 | 237 | 177 | 26 | 2 | 0 | 1 | 768
23-0107777 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown Cause | 2023-08-22 18:03 | 8/22 - 8/28 | 2023-08-22 20:41 | 158 | FTS | 8690 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 158
23-0107330 | Monterey | LAURELES 1111 | LAURELES 1111432 | Unknown Cause | 2023-08-22 01:37 | 8/22 - 8/28 | 2023-08-23 01:50 | 719.2377 | FTS | 233033 | 324 | 6 | 5 | 7 | 0 | 0 | 0 | 1453
23-0107835 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Equipment Failure/Involved | 2023-08-22 23:32 | 8/22 - 8/28 | 2023-08-23 04:17 | 108.7265 | FTS | 24246 | 223 | 11 | 9 | 3 | 0 | 0 | 0 | 285
23-0107784 | Placer | HALSEY 1101 | HALSEY 1101CB | 3rd Party | 2023-08-22 20:43 | 8/22 - 8/28 | 2023-08-23 05:12 | 91.3119 | FTS | 221888 | 2430 | 191 | 135 | 28 | 5 | 0 | 4 | 509
23-0107875 | Napa | PUEBLO 2103 | PUEBLO 210378504 | Animal | 2023-08-23 07:33 | 8/22 - 8/28 | 2023-08-23 09:10 | 79.6113 | FTS | 21097 | 265 | 20 | 11 | 2 | 0 | 0 | 4 | 97
23-0107894 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207M501R | Animal | 2023-08-23 08:14 | 8/22 - 8/28 | 2023-08-23 09:27 | 73 | FTS | 73876 | 1012 | 50 | 32 | 6 | 0 | 0 | 0 | 73
23-0107851 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018522 | Animal | 2023-08-23 06:40 | 8/22 - 8/28 | 2023-08-23 09:28 | 162.698 | FTS | 141710 | 871 | 35 | 18 | 36 | 17 | 0 | 0 | 168
23-0107786 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062392 | Unknown Cause | 2023-08-22 21:02 | 8/22 - 8/28 | 2023-08-23 09:41 | 154.1972 | FTS | 328440 | 2130 | 161 | 123 | 19 | 3 | 0 | 14 | 759
23-0107844 | San Luis Obispo | ATASCADERO 1101 | ATASCADERO 1101A50 | Unknown Cause | 2023-08-23 06:09 | 8/22 - 8/28 | 2023-08-23 10:29 | 249.2882 | FTS | 169516 | 680 | 174 | 107 | 35 | 7 | 0 | 4 | 260
23-0107880 | Madera | OAKHURST 1101 | OAKHURST 11015490 | Animal | 2023-08-23 07:42 | 8/22 - 8/28 | 2023-08-23 12:18 | 93.0636 | FTS | 144900 | 1557 | 174 | 127 | 31 | 2 | 0 | 0 | 276
23-0108016 | Alameda | OAKLAND X 1104 | OAKLAND X 1104CR101 | Unknown Cause | 2023-08-23 10:57 | 8/22 - 8/28 | 2023-08-23 12:38 | 101 | FTS | 61509 | 609 | 26 | 21 | 7 | 0 | 0 | 0 | 101
23-0107964 | Glenn | ELK CREEK 1101 | ELK CREEK 110137334 | Animal | 2023-08-23 10:01 | 8/22 - 8/28 | 2023-08-23 12:38 | 150.5234 | FTS | 48318 | 321 | 18 | 17 | 11 | 5 | 0 | 0 | 157
23-0108102 | Sonoma | MOLINO 1101 | MOLINO 1101322 | Unknown Cause | 2023-08-23 12:41 | 8/22 - 8/28 | 2023-08-23 14:38 | 117 | FTS | 43992 | 376 | 17 | 14 | 6 | 0 | 0 | 4 | 117
23-0108226 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | Animal | 2023-08-23 14:54 | 8/22 - 8/28 | 2023-08-23 15:51 | 57 | FTS | 6498 | 114 | 3 | 2 | 9 | 2 | 0 | 0 | 57
23-0108212 | Shasta | COTTONWOOD 1101 | COTTONWOOD 1101384360 | 3rd Party | 2023-08-23 14:21 | 8/22 - 8/28 | 2023-08-23 16:02 | 101 | FTS | 1919 | 19 | 1 | 0 | 0 | 0 | 0 | 0 | 101
23-0108236 | Sonoma | SANTA ROSA A 1104 | SANTA ROSA A 1104210 | Unknown Cause | 2023-08-23 14:59 | 8/22 - 8/28 | 2023-08-23 17:37 | 153.5493 | FTS | 252128 | 1642 | 125 | 99 | 24 | 1 | 0 | 14 | 158
23-0108290 | Butte | WYANDOTTE 1109 | WYANDOTTE 1109759354 | Vegetation | 2023-08-23 16:43 | 8/22 - 8/28 | 2023-08-23 18:15 | 66.9745 | FTS | 123568 | 1845 | 212 | 156 | 24 | 7 | 0 | 2 | 92
23-0108310 | Plumas | CRESCENT MILLS SUB | CRESCENT MILLS 21012056 | Vegetation | 2023-08-23 18:47 | 8/22 - 8/28 | 2023-08-23 20:43 | 100.31 | FTS | 153374 | 1529 | 71 | 54 | 24 | 2 | 4 | 0 | 116
23-0108344 | Monterey | JOLON 1103 | JOLON 1103CB | Unknown Cause | 2023-08-23 21:23 | 8/22 - 8/28 | 2023-08-24 00:51 | 173.35 | FTS | 3467 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 208
23-0108305 | Lake | KONOCTI 1102 | KONOCTI 110275382 | Vegetation | 2023-08-23 17:52 | 8/22 - 8/28 | 2023-08-24 01:40 | 87.0133 | FTS | 32804 | 377 | 15 | 10 | 7 | 0 | 0 | 0 | 468
23-0107923 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041634 | Equipment Failure/Involved | 2023-08-23 09:23 | 8/22 - 8/28 | 2023-08-24 02:42 | 149.3339 | FTS | 165462 | 1108 | 52 | 35 | 6 | 0 | 0 | 2 | 1039
23-0108324 | Santa Clara | MILPITAS 1105 | MILPITAS 1105CB | Equipment Failure/Involved | 2023-08-23 19:49 | 8/22 - 8/28 | 2023-08-24 07:29 | 104.0366 | FTS | 428839 | 4122 | 151 | 95 | 28 | 7 | 0 | 0 | 700
23-0108338 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21061104 | Company Initiated | 2023-08-23 20:40 | 8/22 - 8/28 | 2023-08-24 09:25 | 765 | FTS | 507195 | 663 | 49 | 39 | 27 | 5 | 0 | 1 | 765
23-0108503 | Amador | WEST POINT 1101 | WEST POINT 110112256 | Company Initiated | 2023-08-24 09:22 | 8/22 - 8/28 | 2023-08-24 09:50 | 26.7345 | FTS | 47534 | 1778 | 0 | 0 | 0 | 0 | 0 | 0 | 28
23-0108450 | Plumas | CHALLENGE 1101 | CHALLENGE 1101CB | Vegetation | 2023-08-24 08:03 | 8/22 - 8/28 | 2023-08-24 13:02 | 262.6766 | FTS | 185187 | 705 | 48 | 32 | 10 | 0 | 0 | 0 | 299
23-0108633 | Lake | HARTLEY 1101 | HARTLEY 1101738 | Animal | 2023-08-24 12:17 | 8/22 - 8/28 | 2023-08-24 13:58 | 101 | FTS | 95647 | 947 | 82 | 56 | 9 | 5 | 0 | 0 | 101
23-0108563 | Napa | NAPA 1112 | NAPA 11121302 | Unknown Cause | 2023-08-24 10:44 | 8/22 - 8/28 | 2023-08-24 14:36 | 73.2595 | FTS | 40366 | 551 | 31 | 21 | 9 | 0 | 0 | 11 | 232
23-0108418 | Tehama | VOLTA 1101 | VOLTA 110165764 | Vegetation | 2023-08-24 06:39 | 8/22 - 8/28 | 2023-08-24 15:00 | 178.7534 | FTS | 26098 | 146 | 10 | 8 | 15 | 2 | 0 | 0 | 501
23-0108662 | Santa Cruz | LOS GATOS 1107 | LOS GATOS 1107781232 | Unknown Cause | 2023-08-24 12:15 | 8/22 - 8/28 | 2023-08-24 15:01 | 155.3902 | FTS | 31855 | 205 | 16 | 14 | 2 | 0 | 0 | 2 | 166
23-0108620 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018912 | Unknown Cause | 2023-08-24 11:50 | 8/22 - 8/28 | 2023-08-24 15:20 | 210 | FTS | 17850 | 85 | 5 | 3 | 1 | 0 | 0 | 0 | 210
23-0108309 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 040116010 | Equipment Failure/Involved | 2023-08-23 18:46 | 8/22 - 8/28 | 2023-08-24 16:01 | 707.3925 | FTS | 187459 | 265 | 20 | 17 | 7 | 1 | 0 | 0 | 1275
23-0108400 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11021510 | Vegetation | 2023-08-24 02:31 | 8/22 - 8/28 | 2023-08-24 17:47 | 797.6084 | FTS | 666003 | 835 | 18 | 14 | 29 | 6 | 0 | 0 | 916
23-0108772 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Unknown Cause | 2023-08-24 16:11 | 8/22 - 8/28 | 2023-08-24 19:10 | 138.5025 | FTS | 300689 | 2171 | 96 | 64 | 44 | 2 | 0 | 4 | 179
23-0108799 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown Cause | 2023-08-24 18:05 | 8/22 - 8/28 | 2023-08-24 19:41 | 96 | FTS | 12960 | 135 | 9 | 7 | 5 | 2 | 0 | 0 | 96
23-0108604 | Kings | DEVILS DEN 1101 | DEVILS DEN 1101CB | Equipment Failure/Involved | 2023-08-24 11:32 | 8/22 - 8/28 | 2023-08-24 23:20 | 115.7612 | FTS | 7756 | 67 | 0 | 0 | 8 | 0 | 0 | 0 | 708
23-0108886 | Nevada | BRUNSWICK 1105 | BRUNSWICK 110532536 | Vegetation | 2023-08-25 02:03 | 8/22 - 8/28 | 2023-08-25 05:10 | 187 | FTS | 85646 | 458 | 36 | 18 | 13 | 0 | 0 | 3 | 187
23-0108883 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V58 | Equipment Failure/Involved | 2023-08-25 01:39 | 8/22 - 8/28 | 2023-08-25 08:25 | 95.4084 | FTS | 268670 | 2816 | 78 | 59 | 58 | 5 | 2 | 25 | 406
23-0108983 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110170 | Unknown Cause | 2023-08-25 08:54 | 8/22 - 8/28 | 2023-08-25 10:41 | 39.2796 | FTS | 112968 | 2876 | 240 | 166 | 45 | 0 | 0 | 1 | 107
23-0108794 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 110347966 | Environmental/External | 2023-08-24 17:30 | 8/22 - 8/28 | 2023-08-25 12:07 | 565.8337 | FTS | 551122 | 974 | 65 | 49 | 10 | 1 | 0 | 0 | 1117
23-0108884 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106LB44 | Unknown Cause | 2023-08-25 01:46 | 8/22 - 8/28 | 2023-08-25 12:23 | 327.8929 | FTS | 36724 | 112 | 7 | 7 | 0 | 0 | 0 | 1 | 637
23-0109152 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102CB | Company Initiated | 2023-08-25 12:07 | 8/22 - 8/28 | 2023-08-25 12:29 | 22 | FTS | 9790 | 445 | 26 | 13 | 13 | 2 | 0 | 0 | 22
23-0109202 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121204 | Company Initiated | 2023-08-25 11:49 | 8/22 - 8/28 | 2023-08-25 13:28 | 99 | FTS | 2376 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 99
23-0108800 | Humboldt | HOOPA 1101 | HOOPA 1101405280 | Vegetation | 2023-08-24 18:00 | 8/22 - 8/28 | 2023-08-25 13:37 | 466.4971 | FTS | 977778 | 2096 | 99 | 72 | 61 | 17 | 1 | 0 | 1177
23-0108955 | Amador | ELECTRA 1101 | ELECTRA 110161816 | Vegetation | 2023-08-25 08:16 | 8/22 - 8/28 | 2023-08-25 14:37 | 293.5829 | FTS | 109800 | 374 | 35 | 25 | 3 | 0 | 0 | 12 | 381
23-0109262 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 110582622 | Vegetation | 2023-08-25 15:03 | 8/22 - 8/28 | 2023-08-25 15:23 | 20 | FTS | 4060 | 203 | 13 | 12 | 2 | 0 | 0 | 4 | 20
23-0109188 | Napa | NAPA 1112 | NAPA 11121302 | Unknown Cause | 2023-08-25 12:55 | 8/22 - 8/28 | 2023-08-25 15:30 | 51.2686 | FTS | 28249 | 551 | 31 | 21 | 9 | 0 | 0 | 11 | 155
23-0109254 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104350030 | Unknown Cause | 2023-08-25 15:03 | 8/22 - 8/28 | 2023-08-25 16:46 | 103 | FTS | 412 | 4 | 0 | 0 | 2 | 0 | 0 | 0 | 103
23-0108887 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101135762 | Equipment Failure/Involved | 2023-08-25 02:27 | 8/22 - 8/28 | 2023-08-25 17:06 | 242.5556 | FTS | 8732 | 36 | 1 | 1 | 0 | 0 | 0 | 0 | 879
23-0108892 | Napa | SILVERADO 2103 | SILVERADO 2103507513 | Vegetation | 2023-08-25 04:36 | 8/22 - 8/28 | 2023-08-25 21:25 | 259.3896 | FTS | 39946 | 154 | 1 | 0 | 1 | 0 | 0 | 0 | 1009
23-0109349 | Monterey | SAN BENITO 2104 | SAN BENITO 2104785888 | Animal | 2023-08-26 03:26 | 8/22 - 8/28 | 2023-08-26 05:48 | 135.7657 | FTS | 175545 | 1293 | 97 | 81 | 23 | 3 | 0 | 3 | 142
23-0109353 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108636 | Unknown Cause | 2023-08-26 06:34 | 8/22 - 8/28 | 2023-08-26 07:57 | 83 | FTS | 11786 | 142 | 5 | 4 | 2 | 0 | 0 | 1 | 83
23-0109334 | Lake | REDBUD 1101 | REDBUD 1101323962 | Unknown Cause | 2023-08-25 23:08 | 8/22 - 8/28 | 2023-08-26 09:10 | 153.6792 | FTS | 77608 | 505 | 54 | 39 | 3 | 0 | 0 | 0 | 602
23-0109352 | Mendocino | POINT ARENA 1101 | POINT ARENA 1101476 | Equipment Failure/Involved | 2023-08-26 06:05 | 8/22 - 8/28 | 2023-08-26 12:18 | 120.9883 | FTS | 30973 | 256 | 12 | 8 | 9 | 1 | 0 | 0 | 373
23-0109372 | Napa | NAPA 1112 | NAPA 1112850068 | Unknown Cause | 2023-08-26 08:59 | 8/22 - 8/28 | 2023-08-26 12:26 | 59.2613 | FTS | 32653 | 551 | 31 | 21 | 9 | 0 | 0 | 11 | 207
23-0109362 | Placer | PENRYN 1107 | PENRYN 11072706 | Animal | 2023-08-26 07:37 | 8/22 - 8/28 | 2023-08-26 12:58 | 85.333 | FTS | 92501 | 1084 | 87 | 57 | 13 | 1 | 0 | 7 | 321
23-0109357 | Humboldt | EEL RIVER 1102 | EEL RIVER 11021902 | Unknown Cause | 2023-08-26 07:06 | 8/22 - 8/28 | 2023-08-26 13:48 | 351.3868 | FTS | 37247 | 106 | 3 | 2 | 12 | 0 | 0 | 0 | 402
23-0109307 | Lake | HARTLEY 1101 | HARTLEY 1101738 | Equipment Failure/Involved | 2023-08-25 19:39 | 8/22 - 8/28 | 2023-08-26 17:10 | 88.3833 | FTS | 83699 | 947 | 82 | 56 | 9 | 5 | 0 | 0 | 1291
23-0109295 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Equipment Failure/Involved | 2023-08-25 16:52 | 8/22 - 8/28 | 2023-08-26 17:24 | 1451.0073 | FTS | 399027 | 275 | 2 | 2 | 5 | 0 | 0 | 0 | 1472
23-0109418 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702CB | Unknown Cause | 2023-08-26 13:24 | 8/22 - 8/28 | 2023-08-26 17:38 | 242.4907 | FTS | 942804 | 3888 | 274 | 193 | 103 | 14 | 1 | 3 | 254
23-0109387 | Butte | CLARK ROAD 1102 | CLARK ROAD 110281296 | Animal | 2023-08-26 10:24 | 8/22 - 8/28 | 2023-08-26 18:43 | 291.2554 | FTS | 285139 | 979 | 84 | 60 | 19 | 3 | 0 | 1 | 499
23-0109385 | San Mateo | HALF MOON BAY 1101 | HALF MOON BAY 11012500 | Vegetation | 2023-08-26 10:05 | 8/22 - 8/28 | 2023-08-27 00:41 | 379.1974 | FTS | 115276 | 304 | 10 | 7 | 23 | 0 | 0 | 1 | 876
23-0109461 | Marin | BOLINAS 1101 | BOLINAS 1101528 | Unknown Cause | 2023-08-26 21:24 | 8/22 - 8/28 | 2023-08-27 02:29 | 305 | FTS | 235460 | 772 | 15 | 9 | 5 | 0 | 0 | 0 | 305
23-0109484 | Sonoma | COTATI 1105 | COTATI 110536536 | Unknown Cause | 2023-08-27 04:30 | 8/22 - 8/28 | 2023-08-27 08:15 | 161.2416 | FTS | 130122 | 807 | 24 | 18 | 23 | 2 | 2 | 1 | 225
23-0109494 | Mendocino | WILLITS 1104 | WILLITS 1104627552 | Unknown Cause | 2023-08-27 08:24 | 8/22 - 8/28 | 2023-08-27 10:58 | 154 | FTS | 25102 | 163 | 13 | 12 | 6 | 0 | 0 | 0 | 154
23-0109453 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 110287432 | Unknown Cause | 2023-08-26 19:48 | 8/22 - 8/28 | 2023-08-27 11:05 | 917 | FTS | 64190 | 70 | 5 | 5 | 5 | 0 | 0 | 0 | 917
23-0109495 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062392 | Animal | 2023-08-27 08:56 | 8/22 - 8/28 | 2023-08-27 11:05 | 104.0871 | FTS | 57352 | 551 | 37 | 28 | 9 | 2 | 0 | 2 | 129
23-0109487 | Sonoma | DUNBAR 1102 | DUNBAR 1102386158 | Unknown Cause | 2023-08-27 06:27 | 8/22 - 8/28 | 2023-08-27 11:18 | 291 | FTS | 10185 | 35 | 1 | 0 | 0 | 0 | 0 | 0 | 291
23-0109489 | Santa Cruz | CAMP EVERS 2106 | BURNS 210139126 | Vegetation | 2023-08-27 07:47 | 8/22 - 8/28 | 2023-08-27 12:09 | 225.7079 | FTS | 1625097 | 7200 | 546 | 423 | 150 | 23 | 0 | 24 | 262
23-0109499 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown Cause | 2023-08-27 09:23 | 8/22 - 8/28 | 2023-08-27 12:15 | 70.6897 | FTS | 86100 | 1218 | 116 | 93 | 17 | 3 | 0 | 4 | 172
23-0109446 | Yuba | BANGOR 1101 | BANGOR 11017446 | Animal | 2023-08-26 18:57 | 8/22 - 8/28 | 2023-08-27 12:41 | 778.9434 | FTS | 412840 | 530 | 59 | 39 | 4 | 0 | 0 | 3 | 1064
23-0109457 | Marin | WOODACRE 1101 | WOODACRE 110196844 | Animal | 2023-08-26 20:22 | 8/22 - 8/28 | 2023-08-27 13:02 | 320.0556 | FTS | 86415 | 270 | 12 | 7 | 4 | 2 | 0 | 0 | 1000
23-0109509 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Unknown Cause | 2023-08-27 11:15 | 8/22 - 8/28 | 2023-08-27 13:44 | 46.1075 | FTS | 48044 | 1042 | 83 | 61 | 18 | 5 | 0 | 2 | 149
23-0109552 | Marin | PETALUMA C 1109 | PETALUMA C 110948000 | Unknown Cause | 2023-08-27 16:21 | 8/22 - 8/28 | 2023-08-27 18:57 | 156 | FTS | 5772 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 156
23-0109550 | Sonoma | PETALUMA C 1109 | PETALUMA C 110948000 | Unknown Cause | 2023-08-27 16:16 | 8/22 - 8/28 | 2023-08-27 18:57 | 161 | FTS | 22218 | 138 | 4 | 4 | 13 | 0 | 0 | 0 | 161
23-0109541 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Environmental/External | 2023-08-27 15:39 | 8/22 - 8/28 | 2023-08-27 19:16 | 160.771 | FTS | 21061 | 131 | 2 | 2 | 7 | 0 | 0 | 1 | 217
23-0109555 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown Cause | 2023-08-27 18:02 | 8/22 - 8/28 | 2023-08-27 20:08 | 126 | FTS | 6930 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 126
23-0109562 | Placer | LINCOLN 1101 | LINCOLN 110195756 | Animal | 2023-08-27 20:16 | 8/22 - 8/28 | 2023-08-27 21:44 | 88 | FTS | 23936 | 272 | 28 | 22 | 0 | 0 | 0 | 6 | 88
23-0109486 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | 3rd Party | 2023-08-27 05:36 | 8/22 - 8/28 | 2023-08-28 04:41 | 156.3936 | FTS | 172033 | 1100 | 67 | 50 | 16 | 3 | 0 | 3 | 1385
23-0109598 | Fresno | AUBERRY 1101 | AUBERRY 110137536 | Unknown Cause | 2023-08-28 06:05 | 8/22 - 8/28 | 2023-08-28 09:18 | 193 | FTS | 119274 | 618 | 30 | 24 | 19 | 3 | 0 | 1 | 193
23-0109590 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102672 | Unknown Cause | 2023-08-28 01:49 | 8/22 - 8/28 | 2023-08-28 09:32 | 93.9404 | FTS | 55143 | 587 | 36 | 22 | 18 | 0 | 0 | 0 | 463
23-0109591 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Equipment Failure/Involved | 2023-08-28 03:06 | 8/22 - 8/28 | 2023-08-28 09:45 | 254.2874 | FTS | 219450 | 863 | 70 | 42 | 11 | 0 | 0 | 3 | 399
23-0109678 | Contra Costa | CLAYTON 2215 | CLAYTON 2215W573R | Unknown Cause | 2023-08-28 09:11 | 8/22 - 8/28 | 2023-08-28 10:25 | 73.4734 | FTS | 100732 | 1371 | 108 | 76 | 20 | 2 | 0 | 0 | 74
23-0109637 | Calaveras | Valley Springs 1101 | Valley Springs 1101207256 | Unknown Cause | 2023-08-28 08:04 | 8/22 - 8/28 | 2023-08-28 10:57 | 139.8646 | FTS | 207699 | 1485 | 117 | 82 | 37 | 5 | 0 | 0 | 173
23-0109741 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612760 | Company Initiated | 2023-08-28 11:00 | 8/22 - 8/28 | 2023-08-28 11:11 | 11 | FTS | 4532 | 412 | 36 | 30 | 7 | 0 | 0 | 6 | 11
23-0109780 | Lake | HARTLEY 1101 | HARTLEY 1101871312 | Company Initiated | 2023-08-28 11:21 | 8/22 - 8/28 | 2023-08-28 11:59 | 38 | FTS | 1140 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 38
23-0109859 | Marin | OLEMA 1101 | OLEMA 11011200 | Company Initiated | 2023-08-28 14:18 | 8/22 - 8/28 | 2023-08-28 14:41 | 23 | FTS | 3036 | 132 | 4 | 3 | 5 | 1 | 0 | 0 | 23
23-0109628 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062392 | Animal | 2023-08-28 07:41 | 8/22 - 8/28 | 2023-08-28 14:51 | 83.5336 | FTS | 46027 | 551 | 37 | 28 | 9 | 2 | 0 | 2 | 430
23-0109935 | Monterey | DEL MONTE 2104 | DEL MONTE 21042762 | Animal | 2023-08-28 17:19 | 8/29 - 9/4 | 2023-08-28 18:38 | 79 | FTS | 33180 | 420 | 22 | 15 | 5 | 1 | 0 | 0 | 79
23-0109936 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101978 | Company Initiated | 2023-08-28 17:25 | 8/29 - 9/4 | 2023-08-28 18:42 | 77 | FTS | 9317 | 121 | 2 | 1 | 1 | 0 | 0 | 0 | 77
23-0109848 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | Unknown Cause | 2023-08-28 13:54 | 8/29 - 9/4 | 2023-08-28 18:50 | 189.4613 | FTS | 176199 | 930 | 22 | 17 | 10 | 0 | 0 | 6 | 296
23-0110008 | Humboldt | FRUITLAND 1142 | FRUITLAND 1142899734 | Vegetation | 2023-08-29 02:00 | 8/29 - 9/4 | 2023-08-29 04:14 | 134 | FTS | 68876 | 514 | 13 | 8 | 13 | 4 | 0 | 0 | 134
23-0110073 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | Company Initiated | 2023-08-29 08:26 | 8/29 - 9/4 | 2023-08-29 08:51 | 25 | FTS | 71525 | 2861 | 276 | 202 | 49 | 4 | 0 | 4 | 25
23-0109957 | Monterey | OILFIELDS 1103 | OILFIELDS 11037006 | Unknown Cause | 2023-08-28 20:06 | 8/29 - 9/4 | 2023-08-29 09:16 | 184.2093 | FTS | 47526 | 258 | 11 | 6 | 6 | 0 | 0 | 0 | 790
23-0100246 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Company Initiated | 2023-08-29 09:16 | 8/29 - 9/4 | 2023-08-29 09:37 | 21 | FTS | 34398 | 1638 | 127 | 96 | 26 | 5 | 0 | 2 | 21
23-0110063 | Lake | LUCERNE 1103 | LUCERNE 110327932 | Unknown Cause | 2023-08-29 08:07 | 8/29 - 9/4 | 2023-08-29 09:40 | 93 | FTS | 1488 | 16 | 0 | 0 | 6 | 0 | 0 | 0 | 93
23-0110020 | Yolo | MADISON 2101 | MADISON 2101760730 | Unknown Cause | 2023-08-29 06:21 | 8/29 - 9/4 | 2023-08-29 10:11 | 230 | FTS | 4140 | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 230
23-0110014 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 2104CB | Equipment Failure/Involved | 2023-08-29 04:49 | 8/29 - 9/4 | 2023-08-29 10:21 | 188.9492 | FTS | 770535 | 4078 | 326 | 233 | 55 | 5 | 0 | 30 | 332
23-0110281 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 110564118 | Company Initiated | 2023-08-29 13:01 | 8/29 - 9/4 | 2023-08-29 13:20 | 19 | FTS | 12654 | 666 | 32 | 24 | 13 | 7 | 0 | 0 | 19
23-0110340 | Amador | PINE GROVE 1101 | PINE GROVE 11013170 | Company Initiated | 2023-08-29 14:05 | 8/29 - 9/4 | 2023-08-29 14:27 | 22 | FTS | 15224 | 692 | 49 | 38 | 15 | 0 | 0 | 5 | 22
23-0110384 | Amador | PINE GROVE 1101 | PINE GROVE 11013170 | Company Initiated | 2023-08-29 14:57 | 8/29 - 9/4 | 2023-08-29 15:13 | 16 | FTS | 11072 | 692 | 49 | 38 | 15 | 0 | 0 | 5 | 16
23-0110310 | San Luis Obispo | MORRO BAY 1102 | MORRO BAY 1102V84 | Unknown Cause | 2023-08-29 13:37 | 8/29 - 9/4 | 2023-08-29 16:07 | 44.5164 | FTS | 108620 | 2440 | 84 | 68 | 17 | 4 | 0 | 0 | 150
23-0110381 | Tehama | VOLTA 1101 | VOLTA 110165764 | Vegetation | 2023-08-29 14:58 | 8/29 - 9/4 | 2023-08-29 16:40 | 96.4514 | FTS | 13889 | 144 | 10 | 8 | 15 | 2 | 0 | 0 | 102
23-0110093 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Unknown Cause | 2023-08-29 08:51 | 8/29 - 9/4 | 2023-08-29 17:10 | 144.0443 | FTS | 91036 | 632 | 30 | 25 | 11 | 0 | 0 | 0 | 499
23-0111737 | Shasta | JESSUP 1101 | JESSUP 11011496 | Company Initiated | 2023-08-30 02:04 | 8/29 - 9/4 | 2023-08-30 02:19 | 15 | FTS | 10605 | 707 | 79 | 59 | 6 | 2 | 0 | 0 | 15
23-0110465 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N48 | Animal | 2023-08-29 19:37 | 8/29 - 9/4 | 2023-08-30 08:08 | 553.427 | FTS | 155513 | 281 | 12 | 6 | 4 | 0 | 0 | 3 | 751
23-0110459 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 11071166 | Unknown Cause | 2023-08-29 19:01 | 8/29 - 9/4 | 2023-08-30 08:50 | 301.1695 | FTS | 859839 | 2855 | 109 | 61 | 46 | 10 | 0 | 1 | 829
23-0110551 | Napa | PUEBLO 2104 | PUEBLO 2102618 | Unknown Cause | 2023-08-30 05:57 | 8/29 - 9/4 | 2023-08-30 09:22 | 150.5703 | FTS | 56765 | 377 | 4 | 2 | 7 | 1 | 0 | 3 | 205
23-0110626 | Santa Clara | HICKS 2101 | HICKS 2101XR250 | Animal | 2023-08-30 08:54 | 8/29 - 9/4 | 2023-08-30 10:55 | 121 | FTS | 25773 | 213 | 11 | 6 | 3 | 0 | 0 | 0 | 121
23-0110637 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2104CB | Animal | 2023-08-30 07:19 | 8/29 - 9/4 | 2023-08-30 11:43 | 241.3333 | FTS | 33304 | 138 | 11 | 3 | 4 | 0 | 0 | 5 | 264
23-0110748 | Lassen | HAMILTON BRANCH 1101 | HAMILTON BRANCH 11012046 | 3rd Party | 2023-08-30 11:39 | 8/29 - 9/4 | 2023-08-30 13:05 | 86 | FTS | 17716 | 206 | 15 | 11 | 6 | 0 | 0 | 0 | 86
23-0110716 | Santa Clara | MORGAN HILL 2109 | MORGAN HILL 2109XR246 | Unknown Cause | 2023-08-30 10:53 | 8/29 - 9/4 | 2023-08-30 13:20 | 90.779 | FTS | 380364 | 4190 | 236 | 158 | 44 | 5 | 0 | 0 | 147
23-0110860 | Monterey | OILFIELDS 1103 | OILFIELDS 11037006 | Animal | 2023-08-30 13:55 | 8/29 - 9/4 | 2023-08-30 15:32 | 97 | FTS | 25026 | 258 | 11 | 6 | 6 | 0 | 0 | 0 | 97
23-0110642 | Placer | PLACER 1103 | PLACER 1103284874 | Equipment Failure/Involved | 2023-08-30 09:24 | 8/29 - 9/4 | 2023-08-30 16:31 | 91.1152 | FTS | 15034 | 165 | 11 | 5 | 3 | 0 | 0 | 0 | 427
23-0110942 | Sonoma | FULTON 1107 | FULTON 1107126742 | Unknown Cause | 2023-08-30 15:35 | 8/29 - 9/4 | 2023-08-30 16:56 | 73.7569 | FTS | 69184 | 938 | 62 | 48 | 22 | 2 | 0 | 5 | 81
23-0110955 | Monterey | OILFIELDS 1103 | OILFIELDS 11037006 | Unknown Cause | 2023-08-30 15:54 | 8/29 - 9/4 | 2023-08-30 18:06 | 132 | FTS | 34056 | 258 | 11 | 6 | 6 | 0 | 0 | 0 | 132
23-0110669 | Contra Costa | SAN RAMON 2108 | SAN RAMON 210853732 | Equipment Failure/Involved | 2023-08-30 10:09 | 8/29 - 9/4 | 2023-08-30 21:07 | 541.0638 | FTS | 50860 | 94 | 1 | 0 | 5 | 3 | 0 | 0 | 658
23-0111033 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 11071166 | Equipment Failure/Involved | 2023-08-30 22:01 | 8/29 - 9/4 | 2023-08-31 03:52 | 248.1856 | FTS | 537570 | 2166 | 87 | 52 | 41 | 10 | 0 | 1 | 351
23-0110998 | Humboldt | RIO DELL 1101 | RIO DELL 11018768 | Vegetation | 2023-08-30 19:13 | 8/29 - 9/4 | 2023-08-31 07:31 | 571.9871 | FTS | 176744 | 309 | 11 | 8 | 3 | 0 | 0 | 0 | 738
23-0103615 | El Dorado | SHINGLE SPRINGS 1103 | SHINGLE SPRINGS 1103CB | Company Initiated | 2023-08-31 03:52 | 8/29 - 9/4 | 2023-08-31 09:23 | 10.8256 | FTS | 12850 | 1187 | 59 | 38 | 6 | 2 | 0 | 4 | 331
23-0111094 | Amador | OLETA 1102 | OLETA 1102186326 | Company Initiated | 2023-08-31 08:00 | 8/29 - 9/4 | 2023-08-31 09:52 | 112 | FTS | 108976 | 973 | 39 | 26 | 19 | 1 | 0 | 6 | 112
23-0111042 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V40 | Unknown Cause | 2023-08-31 02:02 | 8/29 - 9/4 | 2023-08-31 10:02 | 245.574 | FTS | 134329 | 547 | 20 | 16 | 12 | 0 | 0 | 1 | 480
23-0111165 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101483444 | Animal | 2023-08-31 09:09 | 8/29 - 9/4 | 2023-08-31 10:03 | 54 | FTS | 159570 | 2955 | 23 | 14 | 73 | 6 | 0 | 1 | 54
23-0111145 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Animal | 2023-08-31 09:00 | 8/29 - 9/4 | 2023-08-31 10:05 | 65 | FTS | 4420 | 68 | 4 | 3 | 6 | 2 | 0 | 0 | 65
23-0110886 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022428 | Equipment Failure/Involved | 2023-08-30 14:34 | 8/29 - 9/4 | 2023-08-31 10:17 | 110.2483 | FTS | 16427 | 149 | 4 | 4 | 0 | 0 | 0 | 0 | 1183
23-0111076 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Company Initiated | 2023-08-31 07:22 | 8/29 - 9/4 | 2023-08-31 11:03 | 221 | FTS | 380562 | 1722 | 128 | 80 | 29 | 7 | 0 | 4 | 221
23-0111173 | Monterey | JOLON 1103 | JOLON 1103549180 | 3rd Party | 2023-08-31 09:41 | 8/29 - 9/4 | 2023-08-31 11:13 | 92 | FTS | 828 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 92
23-0111261 | Monterey | JOLON 1103 | JOLON 1103CB | 3rd Party | 2023-08-31 11:23 | 8/29 - 9/4 | 2023-08-31 11:40 | 16.45 | FTS | 329 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 17
23-0111055 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111236 | Unknown Cause | 2023-08-31 06:22 | 8/29 - 9/4 | 2023-08-31 11:53 | 65.2624 | FTS | 229854 | 3522 | 258 | 182 | 97 | 15 | 5 | 1 | 331
23-0111151 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X16 | Unknown Cause | 2023-08-31 09:02 | 8/29 - 9/4 | 2023-08-31 12:04 | 72.7852 | FTS | 20671 | 284 | 8 | 4 | 14 | 2 | 0 | 0 | 182
23-0111239 | Amador | IONE 1101 | IONE 1101510200 | Unknown Cause | 2023-08-31 10:38 | 8/29 - 9/4 | 2023-08-31 12:37 | 119 | FTS | 12138 | 102 | 4 | 2 | 2 | 0 | 0 | 1 | 119
23-0111041 | Monterey | HATTON 1102 | HATTON 1102CB | Unknown Cause | 2023-08-31 00:14 | 8/29 - 9/4 | 2023-08-31 13:39 | 224.0373 | FTS | 480784 | 2146 | 86 | 63 | 46 | 3 | 0 | 0 | 805
23-0111335 | Merced | ORO LOMA 1106 | ORO LOMA 11069790 | Equipment Failure/Involved | 2023-08-31 13:19 | 8/29 - 9/4 | 2023-08-31 13:58 | 39 | FTS | 8151 | 209 | 0 | 0 | 7 | 0 | 0 | 0 | 39
23-0111064 | Sonoma | MOLINO 1104 | MOLINO 1104368158 | 3rd Party | 2023-08-31 06:35 | 8/29 - 9/4 | 2023-08-31 17:15 | 337.1545 | FTS | 78557 | 233 | 17 | 10 | 4 | 0 | 0 | 1 | 640
23-0111044 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106CB | Vegetation | 2023-08-31 03:21 | 8/29 - 9/4 | 2023-08-31 18:01 | 320.462 | FTS | 1710626 | 5338 | 409 | 289 | 92 | 18 | 1 | 15 | 880
23-0111518 | Fresno | SAND CREEK 1103 | SAND CREEK 11037140 | Unknown Cause | 2023-08-31 17:56 | 8/29 - 9/4 | 2023-08-31 21:58 | 201.4537 | FTS | 91460 | 454 | 55 | 32 | 3 | 0 | 0 | 0 | 242
23-0111548 | San Joaquin | TEMPORARY CARBONA 1101 | TEMPORARY CARBONA 110145186 | 3rd Party | 2023-08-31 21:56 | 8/29 - 9/4 | 2023-08-31 22:54 | 58 | FTS | 7598 | 131 | 6 | 4 | 7 | 0 | 0 | 0 | 58
23-0111532 | Kern | TEMBLOR 1104 | TEMBLOR 1104CB | Unknown Cause | 2023-08-31 19:48 | 8/29 - 9/4 | 2023-08-31 23:55 | 126.7925 | FTS | 6720 | 53 | 1 | 1 | 1 | 0 | 0 | 0 | 247
23-0111535 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113524 | Vegetation | 2023-08-31 20:17 | 8/29 - 9/4 | 2023-09-01 01:35 | 91.198 | FTS | 92566 | 1015 | 55 | 36 | 15 | 0 | 0 | 0 | 318
23-0111253 | Marin | WOODACRE 1101 | WOODACRE 1101404 | Vegetation | 2023-08-31 11:02 | 8/29 - 9/4 | 2023-09-01 02:08 | 85.9743 | FTS | 63535 | 739 | 44 | 27 | 17 | 1 | 0 | 1 | 906
23-0111595 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108233646 | Unknown Cause | 2023-09-01 06:42 | 8/29 - 9/4 | 2023-09-01 08:00 | 78 | FTS | 21060 | 270 | 8 | 8 | 4 | 0 | 0 | 3 | 78
23-0111667 | Shasta | GIRVAN 1102 | GIRVAN 1102296428 | Environmental/External | 2023-09-01 09:00 | 8/29 - 9/4 | 2023-09-01 09:26 | 24.8284 | FTS | 15046 | 606 | 48 | 36 | 7 | 0 | 0 | 0 | 26
23-0111725 | Sonoma | MONTE RIO 1112 | MONTE RIO 1112938174 | Company Initiated | 2023-09-01 10:05 | 8/29 - 9/4 | 2023-09-01 10:37 | 32 | FTS | 1440 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 32
23-0111670 | Mendocino | COVELO 1101 | COVELO 1101562360 | 3rd Party | 2023-09-01 08:57 | 8/29 - 9/4 | 2023-09-01 11:27 | 137.1255 | FTS | 71031 | 518 | 21 | 17 | 2 | 3 | 0 | 0 | 150
23-0111740 | Shasta | GIRVAN 1101 | GIRVAN 1101409530 | 3rd Party | 2023-09-01 10:36 | 8/29 - 9/4 | 2023-09-01 12:00 | 65.6262 | FTS | 74092 | 1129 | 98 | 67 | 29 | 6 | 0 | 0 | 84
23-0111983 | Shasta | KESWICK 1101 | KESWICK 1101417066 | Unknown Cause | 2023-09-01 16:03 | 8/29 - 9/4 | 2023-09-01 18:04 | 121 | FTS | 2299 | 19 | 0 | 0 | 9 | 0 | 0 | 0 | 121
23-0111993 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 1101CB | Environmental/External | 2023-09-01 18:14 | 8/29 - 9/4 | 2023-09-01 18:37 | 23 | FTS | 17710 | 770 | 58 | 44 | 15 | 3 | 0 | 1 | 23
23-0111951 | Shasta | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Unknown Cause | 2023-09-01 15:55 | 8/29 - 9/4 | 2023-09-01 18:42 | 142.5 | FTS | 34770 | 244 | 15 | 13 | 3 | 0 | 0 | 0 | 167
23-0112004 | Tuolumne | CURTIS 1702 | CURTIS 1702278740 | Unknown Cause | 2023-09-01 19:10 | 8/29 - 9/4 | 2023-09-01 20:19 | 67.4441 | FTS | 127267 | 1887 | 195 | 145 | 22 | 5 | 0 | 2 | 69
23-0111977 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 110347966 | Equipment Failure/Involved | 2023-09-01 16:59 | 8/29 - 9/4 | 2023-09-01 20:42 | 216.7864 | FTS | 211150 | 974 | 64 | 48 | 10 | 1 | 0 | 0 | 223
23-0112011 | Glenn | ELK CREEK 1101 | ELK CREEK 11012004 | Unknown Cause | 2023-09-01 19:48 | 8/29 - 9/4 | 2023-09-01 21:22 | 79.7072 | FTS | 25586 | 321 | 19 | 17 | 11 | 5 | 0 | 0 | 94
23-0112006 | Kern | TEMBLOR 1104 | TEMBLOR 1104CB | Unknown Cause | 2023-09-01 19:26 | 8/29 - 9/4 | 2023-09-02 01:10 | 254.3396 | FTS | 13480 | 53 | 1 | 1 | 1 | 0 | 0 | 0 | 344
23-0112041 | Santa Cruz | ROB ROY 2104 | ROB ROY 210412596 | Vegetation | 2023-09-02 04:12 | 8/29 - 9/4 | 2023-09-02 06:11 | 119 | FTS | 48314 | 406 | 36 | 29 | 4 | 0 | 0 | 0 | 119
23-0112055 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | Unknown Cause | 2023-09-02 07:22 | 8/29 - 9/4 | 2023-09-02 07:44 | 22 | FTS | 14146 | 643 | 66 | 44 | 4 | 0 | 0 | 14 | 22
23-0112047 | Santa Cruz | ROB ROY 2104 | ROB ROY 210412596 | Unknown Cause | 2023-09-02 06:58 | 8/29 - 9/4 | 2023-09-02 08:15 | 67.3202 | FTS | 27332 | 406 | 36 | 29 | 4 | 0 | 0 | 0 | 77
23-0112043 | Yolo | MADISON 2101 | MADISON 2101760730 | Unknown Cause | 2023-09-02 06:23 | 8/29 - 9/4 | 2023-09-02 08:57 | 154 | FTS | 2772 | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 154
23-0112037 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Unknown Cause | 2023-09-02 02:12 | 8/29 - 9/4 | 2023-09-02 09:07 | 413.3151 | FTS | 369917 | 895 | 65 | 44 | 16 | 0 | 0 | 0 | 415
23-0112063 | Napa | SILVERADO 2104 | SILVERADO 2104722 | Company Initiated | 2023-09-02 07:43 | 8/29 - 9/4 | 2023-09-02 10:07 | 100.7774 | FTS | 52505 | 521 | 36 | 27 | 18 | 2 | 2 | 2 | 144
23-0112096 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Company Initiated | 2023-09-02 09:56 | 8/29 - 9/4 | 2023-09-02 10:09 | 13 | FTS | 11635 | 895 | 65 | 44 | 16 | 0 | 0 | 0 | 13
23-0112009 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107584840 | Unknown Cause | 2023-09-01 19:36 | 8/29 - 9/4 | 2023-09-02 10:30 | 863.7231 | FTS | 449136 | 520 | 50 | 32 | 3 | 0 | 0 | 1 | 894
23-0112086 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | 3rd Party | 2023-09-02 09:06 | 8/29 - 9/4 | 2023-09-02 12:47 | 217.2095 | FTS | 533032 | 2454 | 99 | 78 | 27 | 3 | 2 | 0 | 221
23-0112036 | Alameda | OAKLAND X 1106 | OAKLAND X 1106CR008 | 3rd Party | 2023-09-02 00:37 | 8/29 - 9/4 | 2023-09-02 13:08 | 142.9925 | FTS | 190180 | 1330 | 90 | 55 | 32 | 4 | 0 | 0 | 751
23-0112098 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown Cause | 2023-09-02 10:05 | 8/29 - 9/4 | 2023-09-02 16:24 | 76.7857 | FTS | 93525 | 1218 | 115 | 92 | 17 | 3 | 0 | 4 | 379
23-0112146 | Monterey | DEL MONTE 2104 | DEL MONTE 21042762 | Animal | 2023-09-02 15:32 | 8/29 - 9/4 | 2023-09-02 17:43 | 92.6 | FTS | 38892 | 420 | 21 | 15 | 5 | 1 | 0 | 0 | 131
23-0112144 | Monterey | OILFIELDS 1103 | OILFIELDS 110383158 | Unknown Cause | 2023-09-02 15:22 | 8/29 - 9/4 | 2023-09-02 18:07 | 165 | FTS | 32340 | 196 | 10 | 6 | 6 | 0 | 0 | 0 | 165
23-0112124 | El Dorado | SHINGLE SPRINGS 1103 | SHINGLE SPRINGS 1103CB | Equipment Failure/Involved | 2023-09-02 13:38 | 8/29 - 9/4 | 2023-09-02 19:57 | 130.1613 | FTS | 150857 | 1159 | 59 | 38 | 6 | 2 | 0 | 4 | 379
23-0112157 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | 3rd Party | 2023-09-02 16:29 | 8/29 - 9/4 | 2023-09-02 23:47 | 145.5705 | FTS | 136254 | 936 | 71 | 44 | 11 | 0 | 0 | 1 | 438
23-0112170 | Amador | ELECTRA 1101 | ELECTRA 110161816 | Vegetation | 2023-09-02 18:09 | 8/29 - 9/4 | 2023-09-03 04:10 | 311.0695 | FTS | 116340 | 374 | 35 | 25 | 3 | 0 | 0 | 12 | 601
23-0112201 | Shasta | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Unknown Cause | 2023-09-03 03:48 | 8/29 - 9/4 | 2023-09-03 04:49 | 61 | FTS | 14884 | 244 | 15 | 13 | 3 | 0 | 0 | 0 | 61
23-0112202 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 110192870 | Vegetation | 2023-09-03 04:40 | 8/29 - 9/4 | 2023-09-03 06:16 | 96 | FTS | 64512 | 672 | 36 | 27 | 10 | 0 | 0 | 0 | 96
23-0112203 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Animal | 2023-09-03 05:04 | 8/29 - 9/4 | 2023-09-03 06:25 | 81 | FTS | 151713 | 1873 | 146 | 104 | 19 | 1 | 0 | 4 | 81
23-0112179 | Calaveras | PEORIA 1704 | PEORIA 170459596 | 3rd Party | 2023-09-02 21:51 | 8/29 - 9/4 | 2023-09-03 10:15 | 732.4015 | FTS | 576400 | 787 | 66 | 53 | 30 | 1 | 0 | 1 | 744
23-0112210 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Unknown Cause | 2023-09-03 08:04 | 8/29 - 9/4 | 2023-09-03 10:17 | 85.0576 | FTS | 70853 | 833 | 84 | 65 | 14 | 1 | 0 | 23 | 133
23-0111637 | Shasta | FRENCH GULCH 1102 | FRENCH GULCH 11022902 | Equipment Failure/Involved | 2023-09-01 08:12 | 8/29 - 9/4 | 2023-09-03 10:57 | 2521.2857 | FTS | 17649 | 7 | 0 | 0 | 4 | 0 | 0 | 0 | 3045
23-0112209 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113154 | Vegetation | 2023-09-03 07:55 | 8/29 - 9/4 | 2023-09-03 14:43 | 86.757 | FTS | 34269 | 395 | 16 | 12 | 11 | 0 | 0 | 4 | 408
23-0112261 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 21012232 | Equipment Failure/Involved | 2023-09-03 16:45 | 8/29 - 9/4 | 2023-09-03 18:10 | 85 | FTS | 12070 | 142 | 7 | 6 | 2 | 0 | 0 | 0 | 85
23-0112294 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102914918 | Animal | 2023-09-04 07:51 | 8/29 - 9/4 | 2023-09-04 09:13 | 82 | FTS | 19598 | 239 | 44 | 26 | 3 | 1 | 0 | 0 | 82
23-0112314 | Mendocino | CALPELLA 1101 | CALPELLA 1101CB | Unknown Cause | 2023-09-04 09:26 | 8/29 - 9/4 | 2023-09-04 11:48 | 142 | FTS | 241116 | 1698 | 90 | 63 | 38 | 2 | 0 | 0 | 142
23-0112345 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311046 | Vegetation | 2023-09-04 13:33 | 8/29 - 9/4 | 2023-09-04 14:29 | 55 | FTS | 19305 | 351 | 64 | 55 | 17 | 2 | 0 | 10 | 56
23-0112334 | Sonoma | FULTON 1107 | FULTON 1107126742 | Unknown Cause | 2023-09-04 11:55 | 8/29 - 9/4 | 2023-09-04 14:35 | 150.5698 | FTS | 141385 | 939 | 61 | 48 | 22 | 2 | 0 | 5 | 160
23-0112354 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | Unknown Cause | 2023-09-04 14:44 | 8/29 - 9/4 | 2023-09-04 16:43 | 119 | FTS | 111384 | 936 | 71 | 44 | 11 | 0 | 0 | 1 | 119
23-0112366 | Monterey | DEL MONTE 2104 | DEL MONTE 21042762 | Animal | 2023-09-04 16:24 | 9/5 - 9/11 | 2023-09-04 17:16 | 35.5429 | FTS | 14928 | 420 | 21 | 15 | 5 | 1 | 0 | 0 | 52
23-0112281 | Lassen | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Equipment Failure/Involved | 2023-09-04 02:56 | 9/5 - 9/11 | 2023-09-04 17:47 | 335.2336 | FTS | 81797 | 244 | 15 | 13 | 3 | 0 | 0 | 0 | 891
23-0112368 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105502672 | Animal | 2023-09-04 16:55 | 9/5 - 9/11 | 2023-09-04 18:24 | 89 | FTS | 8811 | 99 | 5 | 1 | 8 | 0 | 0 | 0 | 89
23-0112340 | Nevada | NARROWS 2102 | NARROWS 210276952 | Animal | 2023-09-04 12:58 | 9/5 - 9/11 | 2023-09-04 20:46 | 146.6921 | FTS | 223412 | 1523 | 125 | 87 | 30 | 5 | 0 | 12 | 468
23-0112381 | Humboldt | RIO DELL 1101 | RIO DELL 11018768 | Vegetation | 2023-09-04 19:12 | 9/5 - 9/11 | 2023-09-04 21:23 | 111.0777 | FTS | 34323 | 309 | 11 | 8 | 3 | 0 | 0 | 0 | 131
23-0112416 | Sonoma | DUNBAR 1101 | DUNBAR 1101440 | Animal | 2023-09-05 00:57 | 9/5 - 9/11 | 2023-09-05 02:59 | 113.7854 | FTS | 212096 | 1864 | 103 | 63 | 30 | 5 | 0 | 8 | 122
23-0112415 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Equipment Failure/Involved | 2023-09-05 00:55 | 9/5 - 9/11 | 2023-09-05 05:58 | 143.0563 | FTS | 391545 | 2737 | 181 | 146 | 41 | 7 | 0 | 0 | 303
23-0112344 | Sonoma | MOLINO 1102 | MOLINO 1102104 | 3rd Party | 2023-09-04 13:08 | 9/5 - 9/11 | 2023-09-05 09:25 | 30.3399 | FTS | 46511 | 1533 | 91 | 60 | 21 | 1 | 0 | 15 | 1217
23-0112436 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111236 | Unknown Cause | 2023-09-05 06:52 | 9/5 - 9/11 | 2023-09-05 10:21 | 126.235 | FTS | 23101 | 183 | 11 | 9 | 6 | 0 | 0 | 0 | 209
23-0112475 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Unknown Cause | 2023-09-05 08:03 | 9/5 - 9/11 | 2023-09-05 14:05 | 276.4334 | FTS | 575258 | 2081 | 174 | 135 | 32 | 3 | 0 | 2 | 362
23-0112573 | Napa | SILVERADO 2104 | SILVERADO 210437632 | 3rd Party | 2023-09-05 11:03 | 9/5 - 9/11 | 2023-09-05 14:27 | 129.2696 | FTS | 281420 | 2177 | 114 | 75 | 57 | 8 | 16 | 4 | 204
23-0112768 | Napa | SILVERADO 2104 | SILVERADO 2104209359 | Company Initiated | 2023-09-05 15:08 | 9/5 - 9/11 | 2023-09-05 16:11 | 63 | FTS | 126 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 63
23-0112756 | Monterey | JOLON 1103 | JOLON 1103549180 | 3rd Party | 2023-09-05 15:39 | 9/5 - 9/11 | 2023-09-05 16:41 | 62 | FTS | 558 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 62
23-0112774 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 211051800 | Vegetation | 2023-09-05 16:27 | 9/5 - 9/11 | 2023-09-05 23:36 | 216.9653 | FTS | 218918 | 1009 | 94 | 63 | 12 | 7 | 0 | 9 | 429
23-0112778 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R12 | Vegetation | 2023-09-05 16:29 | 9/5 - 9/11 | 2023-09-06 02:20 | 136.7759 | FTS | 31732 | 232 | 3 | 3 | 2 | 0 | 0 | 0 | 591
23-0112882 | Humboldt | ARCATA 1121 | ARCATA 1121716954 | Vegetation | 2023-09-06 02:30 | 9/5 - 9/11 | 2023-09-06 04:25 | 115 | FTS | 18745 | 163 | 13 | 9 | 6 | 1 | 0 | 0 | 115
23-0112958 | Madera | SAN JOAQUIN #3 1101 | SAN JOAQUIN #3 1101CB | Company Initiated | 2023-09-06 08:00 | 9/5 - 9/11 | 2023-09-06 08:20 | 19.5543 | FTS | 10794 | 552 | 30 | 25 | 19 | 0 | 0 | 1 | 20
23-0112842 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Company Initiated | 2023-09-05 21:05 | 9/5 - 9/11 | 2023-09-06 08:39 | 445.2715 | FTS | 259148 | 582 | 59 | 45 | 3 | 4 | 0 | 2 | 694
23-0112925 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106974130 | Unknown Cause | 2023-09-06 07:25 | 9/5 - 9/11 | 2023-09-06 09:26 | 90.3407 | FTS | 8221 | 91 | 11 | 11 | 1 | 0 | 0 | 0 | 121
23-0112794 | Tehama | COTTONWOOD 1101 | COTTONWOOD 110168190 | Unknown Cause | 2023-09-05 17:26 | 9/5 - 9/11 | 2023-09-06 10:22 | 336.6574 | FTS | 158229 | 470 | 49 | 30 | 5 | 1 | 0 | 0 | 1016
23-0112885 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X08 | Unknown Cause | 2023-09-06 05:02 | 9/5 - 9/11 | 2023-09-06 10:30 | 328 | FTS | 23944 | 73 | 4 | 0 | 1 | 0 | 0 | 0 | 328
23-0112854 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR586 | Unknown Cause | 2023-09-05 22:57 | 9/5 - 9/11 | 2023-09-06 10:55 | 718 | FTS | 41644 | 58 | 1 | 1 | 3 | 0 | 0 | 1 | 718
23-0112924 | Placer | LINCOLN 1104 | LINCOLN 1104693294 | Unknown Cause | 2023-09-06 07:25 | 9/5 - 9/11 | 2023-09-06 11:16 | 171.2997 | FTS | 61154 | 357 | 18 | 7 | 1 | 0 | 0 | 0 | 231
23-0112881 | Napa | CALISTOGA 1101 | CALISTOGA 1101257964 | 3rd Party | 2023-09-06 01:50 | 9/5 - 9/11 | 2023-09-06 12:49 | 502.1 | FTS | 180756 | 360 | 10 | 8 | 3 | 0 | 0 | 1 | 659
23-0113072 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110307832 | Animal | 2023-09-06 10:49 | 9/5 - 9/11 | 2023-09-06 13:43 | 96.4584 | FTS | 127518 | 1322 | 41 | 30 | 18 | 0 | 0 | 13 | 174
23-0113263 | Yolo | MADISON 2101 | MADISON 2101274974 | Unknown Cause | 2023-09-06 14:27 | 9/5 - 9/11 | 2023-09-06 14:37 | 10 | FTS | 300 | 30 | 4 | 4 | 2 | 0 | 0 | 0 | 10
23-0113232 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | 3rd Party | 2023-09-06 13:19 | 9/5 - 9/11 | 2023-09-06 15:14 | 115 | FTS | 2990 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 115
23-0113184 | Nevada | SPAULDING 1101 | SPAULDING 1101578852 | Unknown Cause | 2023-09-06 12:49 | 9/5 - 9/11 | 2023-09-06 15:42 | 126.6047 | FTS | 21776 | 172 | 3 | 1 | 13 | 3 | 0 | 0 | 173
23-0113374 | Yolo | MADISON 2101 | MADISON 2101274974 | Unknown Cause | 2023-09-06 16:23 | 9/5 - 9/11 | 2023-09-06 16:34 | 11 | FTS | 341 | 31 | 4 | 4 | 2 | 0 | 0 | 0 | 11
23-0113310 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown Cause | 2023-09-06 15:43 | 9/5 - 9/11 | 2023-09-06 16:34 | 51 | FTS | 1326 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 51
23-0113352 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown Cause | 2023-09-06 17:03 | 9/5 - 9/11 | 2023-09-06 18:19 | 76 | FTS | 1976 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 76
23-0113353 | Lake | REDBUD 1102 | REDBUD 1102432 | Unknown Cause | 2023-09-06 17:08 | 9/5 - 9/11 | 2023-09-06 18:35 | 36.5618 | FTS | 74586 | 2040 | 182 | 110 | 22 | 1 | 0 | 0 | 87
23-0113330 | Monterey | OILFIELDS 1103 | OILFIELDS 11037006 | Unknown Cause | 2023-09-06 16:18 | 9/5 - 9/11 | 2023-09-06 21:01 | 283 | FTS | 73014 | 258 | 11 | 6 | 6 | 0 | 0 | 0 | 283
23-0113417 | Monterey | DOLAN ROAD 1101 | DOLAN ROAD 1101CB | Unknown Cause | 2023-09-06 23:38 | 9/5 - 9/11 | 2023-09-07 02:14 | 128.373 | FTS | 103597 | 807 | 41 | 33 | 3 | 0 | 0 | 0 | 156
23-0113419 | Calaveras | SALT SPRINGS 2101 | SALT SPRINGS 21011232 | Equipment Failure/Involved | 2023-09-07 01:04 | 9/5 - 9/11 | 2023-09-07 08:06 | 422 | FTS | 388240 | 920 | 16 | 13 | 9 | 2 | 0 | 0 | 422
23-0113485 | Placer | FORESTHILL 1101 | FORESTHILL 1101CB | Company Initiated | 2023-09-07 08:02 | 9/5 - 9/11 | 2023-09-07 09:06 | 64 | FTS | 142592 | 2228 | 213 | 143 | 35 | 6 | 0 | 0 | 64
23-0113560 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104721823 | Unknown Cause | 2023-09-07 10:00 | 9/5 - 9/11 | 2023-09-07 11:43 | 103 | FTS | 126896 | 1232 | 46 | 36 | 23 | 3 | 0 | 0 | 103
23-0113823 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 210110000 | Animal | 2023-09-07 16:17 | 9/5 - 9/11 | 2023-09-07 19:18 | 138.9961 | FTS | 36000 | 259 | 23 | 14 | 7 | 0 | 0 | 0 | 181
23-0113935 | Monterey | SOLEDAD 2104 | SOLEDAD 21027008 | Unknown Cause | 2023-09-08 05:13 | 9/5 - 9/11 | 2023-09-08 08:23 | 190 | FTS | 18050 | 95 | 0 | 0 | 3 | 0 | 0 | 0 | 190
23-0113946 | Santa Cruz | ROB ROY 2105 | ROB ROY 21055090 | Unknown Cause | 2023-09-08 06:25 | 9/5 - 9/11 | 2023-09-08 08:39 | 66.2456 | FTS | 41006 | 619 | 41 | 33 | 7 | 2 | 0 | 4 | 134
23-0113420 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103520 | Equipment Failure/Involved | 2023-09-07 01:09 | 9/5 - 9/11 | 2023-09-08 09:28 | 494.2466 | FTS | 440868 | 892 | 83 | 47 | 7 | 0 | 0 | 2 | 1939
23-0114012 | Lake | LUCERNE 1103 | LUCERNE 110327932 | 3rd Party | 2023-09-08 08:29 | 9/5 - 9/11 | 2023-09-08 09:57 | 88 | FTS | 1408 | 16 | 0 | 0 | 6 | 0 | 0 | 0 | 88
23-0113929 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-09-08 03:30 | 9/5 - 9/11 | 2023-09-08 11:56 | 455.8947 | FTS | 25986 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 506
23-0114094 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Unknown Cause | 2023-09-08 10:14 | 9/5 - 9/11 | 2023-09-08 12:08 | 114 | FTS | 83106 | 729 | 21 | 13 | 14 | 1 | 0 | 0 | 114
23-0114223 | Amador | OLETA 1102 | OLETA 1102186326 | Company Initiated | 2023-09-08 08:34 | 9/5 - 9/11 | 2023-09-08 12:17 | 221.0952 | FTS | 4643 | 21 | 1 | 1 | 0 | 0 | 0 | 0 | 223
23-0114018 | Amador | OLETA 1102 | OLETA 1102186326 | Company Initiated | 2023-09-08 08:34 | 9/5 - 9/11 | 2023-09-08 12:17 | 209.5541 | FTS | 203477 | 971 | 40 | 27 | 19 | 1 | 0 | 6 | 223
23-0114304 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105370732 | Company Initiated | 2023-09-08 16:36 | 9/5 - 9/11 | 2023-09-08 16:43 | 7 | FTS | 3010 | 430 | 23 | 21 | 3 | 1 | 0 | 0 | 7
23-0114294 | Sonoma | MOLINO 1102 | MOLINO 1102495692 | Unknown Cause | 2023-09-08 16:04 | 9/5 - 9/11 | 2023-09-08 17:43 | 78.9942 | FTS | 27411 | 347 | 32 | 20 | 4 | 0 | 0 | 2 | 99
23-0114277 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210985766 | Company Initiated | 2023-09-08 15:16 | 9/5 - 9/11 | 2023-09-08 18:54 | 218 | FTS | 56680 | 260 | 13 | 10 | 2 | 0 | 0 | 10 | 218
23-0113957 | Yuba | BANGOR 1101 | BANGOR 11011958 | Equipment Failure/Involved | 2023-09-08 07:00 | 9/5 - 9/11 | 2023-09-08 19:09 | 78.0973 | FTS | 49748 | 637 | 71 | 48 | 2 | 0 | 0 | 5 | 729
23-0114017 | Monterey | GONZALES 1104 | GONZALES 110422418 | Equipment Failure/Involved | 2023-09-08 08:29 | 9/5 - 9/11 | 2023-09-09 02:43 | 1094 | FTS | 102836 | 94 | 1 | 1 | 2 | 0 | 0 | 0 | 1094
23-0114380 | Monterey | SOLEDAD 2104 | SOLEDAD 21027008 | Unknown Cause | 2023-09-09 05:57 | 9/5 - 9/11 | 2023-09-09 08:15 | 138 | FTS | 13110 | 95 | 0 | 0 | 3 | 0 | 0 | 0 | 138
23-0114374 | Monterey | SOLEDAD 2104 | SOLEDAD 2104413916 | Environmental/External | 2023-09-09 04:59 | 9/5 - 9/11 | 2023-09-09 09:05 | 246 | FTS | 8118 | 33 | 1 | 1 | 0 | 0 | 0 | 0 | 246
23-0114392 | Solano | JAMESON 1105 | JAMESON 1105466348 | Animal | 2023-09-09 07:45 | 9/5 - 9/11 | 2023-09-09 09:35 | 110 | FTS | 38500 | 350 | 14 | 7 | 7 | 2 | 0 | 2 | 110
23-0114388 | Solano | VACAVILLE 1104 | VACAVILLE 1104CB | Unknown Cause | 2023-09-09 07:27 | 9/5 - 9/11 | 2023-09-09 10:07 | 154.6882 | FTS | 325000 | 2101 | 142 | 98 | 30 | 2 | 0 | 1 | 160
23-0114329 | Marin | WOODACRE 1101 | WOODACRE 110196844 | Unknown Cause | 2023-09-08 18:38 | 9/5 - 9/11 | 2023-09-09 11:02 | 232.8593 | FTS | 62872 | 270 | 12 | 7 | 4 | 2 | 0 | 0 | 984
23-0114414 | San Benito | HOLLISTER 2106 | HOLLISTER 21064004 | Unknown Cause | 2023-09-09 09:23 | 9/5 - 9/11 | 2023-09-09 11:12 | 109 | FTS | 5995 | 55 | 16 | 11 | 3 | 1 | 0 | 0 | 109
23-0114433 | Madera | OAKHURST 1101 | OAKHURST 1101352740 | Company Initiated | 2023-09-09 10:55 | 9/5 - 9/11 | 2023-09-09 11:42 | 47 | FTS | 61194 | 1302 | 143 | 103 | 30 | 3 | 0 | 0 | 47
23-0114439 | Sonoma | DUNBAR 1103 | DUNBAR 1103234 | Unknown Cause | 2023-09-09 11:11 | 9/5 - 9/11 | 2023-09-09 13:52 | 161 | FTS | 399602 | 2482 | 278 | 216 | 20 | 0 | 0 | 14 | 161
23-0114432 | Madera | OAKHURST 1101 | OAKHURST 1101618380 | Unknown Cause | 2023-09-09 10:36 | 9/5 - 9/11 | 2023-09-09 14:28 | 232 | FTS | 60784 | 262 | 34 | 26 | 4 | 0 | 0 | 0 | 232
23-0114389 | Madera | SAN JOAQUIN #3 1102 | SAN JOAQUIN #3 1102CB | Environmental/External | 2023-09-09 07:31 | 9/5 - 9/11 | 2023-09-09 15:00 | 148.9237 | FTS | 39018 | 262 | 24 | 20 | 4 | 0 | 0 | 0 | 449
23-0114332 | San Benito | SAN BENITO 2104 | SAN BENITO 2104785888 | Vegetation | 2023-09-08 18:57 | 9/5 - 9/11 | 2023-09-09 15:17 | 121.9218 | FTS | 157523 | 1292 | 97 | 82 | 23 | 3 | 0 | 3 | 1220
23-0114469 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210513430 | Environmental/External | 2023-09-09 13:14 | 9/5 - 9/11 | 2023-09-09 16:05 | 171 | FTS | 22059 | 129 | 6 | 5 | 0 | 0 | 0 | 0 | 171
23-0114464 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 2105916436 | Environmental/External | 2023-09-09 12:58 | 9/5 - 9/11 | 2023-09-09 16:24 | 150.5961 | FTS | 68973 | 458 | 49 | 36 | 5 | 0 | 0 | 0 | 206
23-0114413 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Equipment Failure/Involved | 2023-09-09 09:17 | 9/5 - 9/11 | 2023-09-09 16:26 | 135.4 | FTS | 23018 | 170 | 11 | 7 | 13 | 0 | 0 | 1 | 429
23-0114454 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110180930 | Unknown Cause | 2023-09-09 12:28 | 9/5 - 9/11 | 2023-09-09 16:34 | 246 | FTS | 171954 | 699 | 43 | 32 | 18 | 0 | 0 | 0 | 246
23-0114463 | Santa Cruz | LOS GATOS 1107 | LOS GATOS 110760114 | Unknown Cause | 2023-09-09 13:03 | 9/5 - 9/11 | 2023-09-09 16:41 | 218 | FTS | 63002 | 289 | 19 | 13 | 16 | 0 | 0 | 4 | 218
23-0114528 | Merced | GUSTINE 1102 | GUSTINE 1102999258 | Unknown Cause | 2023-09-09 13:28 | 9/5 - 9/11 | 2023-09-09 18:26 | 298 | FTS | 7450 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 298
23-0114485 | Santa Clara | LOS GATOS 1101 | LOS GATOS 1101LB40 | Company Initiated | 2023-09-09 15:22 | 9/5 - 9/11 | 2023-09-09 18:35 | 193 | FTS | 128538 | 666 | 32 | 28 | 9 | 3 | 0 | 0 | 193
23-0114523 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | Environmental/External | 2023-09-09 17:12 | 9/5 - 9/11 | 2023-09-10 00:37 | 445 | FTS | 313725 | 705 | 94 | 71 | 3 | 0 | 0 | 1 | 445
23-0114468 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210521160 | Environmental/External | 2023-09-09 13:10 | 9/5 - 9/11 | 2023-09-10 01:00 | 188.5939 | FTS | 43188 | 229 | 13 | 8 | 1 | 0 | 0 | 0 | 710
23-0114479 | Calaveras | PEORIA 1704 | PEORIA 170459596 | Unknown Cause | 2023-09-09 14:35 | 9/5 - 9/11 | 2023-09-10 05:26 | 891 | FTS | 585387 | 657 | 59 | 47 | 23 | 0 | 0 | 1 | 891
23-0114548 | Tuolumne | CURTIS 1701 | CURTIS 17019230 | Environmental/External | 2023-09-09 19:08 | 9/5 - 9/11 | 2023-09-10 09:05 | 755.345 | FTS | 1381526 | 1829 | 135 | 101 | 29 | 5 | 6 | 0 | 837
23-0114562 | Tuolumne | MIWUK 1701 | MIWUK 1701767890 | Environmental/External | 2023-09-09 19:24 | 9/5 - 9/11 | 2023-09-10 09:40 | 856 | FTS | 1058872 | 1237 | 76 | 59 | 10 | 2 | 0 | 0 | 856
23-0114559 | Tuolumne | MIWUK 1701 | MIWUK 1701953336 | Environmental/External | 2023-09-09 19:25 | 9/5 - 9/11 | 2023-09-10 09:49 | 864 | FTS | 796608 | 922 | 48 | 35 | 11 | 1 | 0 | 0 | 864
23-0114520 | Tuolumne | TAR FLAT 0402 | TAR FLAT 04023144 | Environmental/External | 2023-09-09 17:07 | 9/5 - 9/11 | 2023-09-10 10:27 | 1040 | FTS | 263120 | 253 | 16 | 10 | 1 | 0 | 0 | 0 | 1040
23-0114593 | Contra Costa | NORTH TOWER 2101 | NORTH TOWER 2101CB | Unknown Cause | 2023-09-09 23:39 | 9/5 - 9/11 | 2023-09-10 10:39 | 613.6504 | FTS | 1144458 | 1865 | 93 | 59 | 29 | 3 | 0 | 0 | 660
23-0114632 | Amador | PINE GROVE 1101 | PINE GROVE 11013166 | Unknown Cause | 2023-09-10 08:09 | 9/5 - 9/11 | 2023-09-10 11:06 | 177 | FTS | 60003 | 339 | 29 | 21 | 2 | 0 | 0 | 1 | 177
23-0114620 | Santa Barbara | SISQUOC 1103 | SISQUOC 1103858898 | Unknown Cause | 2023-09-10 06:29 | 9/5 - 9/11 | 2023-09-10 11:57 | 252.95 | FTS | 40472 | 160 | 6 | 4 | 5 | 0 | 0 | 1 | 328
23-0114482 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Environmental/External | 2023-09-09 15:08 | 9/5 - 9/11 | 2023-09-10 15:20 | 1425.2136 | FTS | 4389658 | 3080 | 211 | 158 | 43 | 1 | 0 | 5 | 1452
23-0114602 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR494 | 3rd Party | 2023-09-10 01:39 | 9/5 - 9/11 | 2023-09-10 16:05 | 227.8947 | FTS | 783274 | 3437 | 243 | 181 | 30 | 6 | 1 | 5 | 866
23-0114555 | Tuolumne | CURTIS 1702 | CURTIS 1702295684 | Unknown Cause | 2023-09-09 19:24 | 9/5 - 9/11 | 2023-09-10 16:10 | 1231.0407 | FTS | 907277 | 737 | 54 | 39 | 13 | 2 | 0 | 1 | 1246
23-0114492 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029280 | Company Initiated | 2023-09-09 15:16 | 9/5 - 9/11 | 2023-09-10 17:38 | 226.0939 | FTS | 645272 | 2854 | 38 | 26 | 18 | 2 | 0 | 0 | 1582
23-0114493 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Environmental/External | 2023-09-09 15:06 | 9/5 - 9/11 | 2023-09-10 17:45 | 1599 | FTS | 930618 | 582 | 59 | 45 | 3 | 4 | 0 | 2 | 1599
23-0114543 | Tuolumne | PEORIA 1705 | PEORIA 1705CB | Environmental/External | 2023-09-09 18:59 | 9/5 - 9/11 | 2023-09-10 17:49 | 549.4059 | FTS | 1410325 | 2567 | 269 | 198 | 28 | 12 | 0 | 4 | 1370
23-0114483 | Tuolumne | CURTIS 1702 | CURTIS 170247488 | Environmental/External | 2023-09-09 15:12 | 9/5 - 9/11 | 2023-09-10 18:48 | 1437.3712 | FTS | 848049 | 590 | 61 | 48 | 7 | 8 | 0 | 1 | 1656
23-0114494 | Tuolumne | CURTIS 1702 | CURTIS 170210940 | Environmental/External | 2023-09-09 15:05 | 9/5 - 9/11 | 2023-09-10 19:50 | 1364.1402 | FTS | 866229 | 635 | 66 | 44 | 3 | 1 | 0 | 0 | 1725
23-0114711 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102851902 | Unknown Cause | 2023-09-10 17:19 | 9/5 - 9/11 | 2023-09-10 20:18 | 94.1553 | FTS | 251677 | 2673 | 191 | 137 | 40 | 6 | 0 | 2 | 179
23-0114553 | Tuolumne | CURTIS 1702 | CURTIS 17028000 | Unknown Cause | 2023-09-09 19:24 | 9/5 - 9/11 | 2023-09-10 21:16 | 1489.242 | FTS | 1717096 | 1153 | 117 | 84 | 16 | 1 | 0 | 0 | 1552
23-0114524 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Environmental/External | 2023-09-09 17:16 | 9/5 - 9/11 | 2023-09-10 21:54 | 1651.567 | FTS | 4771377 | 2889 | 234 | 172 | 26 | 1 | 0 | 1 | 1718
23-0114521 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Environmental/External | 2023-09-09 17:08 | 9/5 - 9/11 | 2023-09-10 22:08 | 851.7338 | FTS | 1116623 | 1311 | 126 | 91 | 20 | 2 | 0 | 2 | 1740
23-0114615 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107869946 | Environmental/External | 2023-09-10 05:27 | 9/5 - 9/11 | 2023-09-10 23:20 | 159.1951 | FTS | 45689 | 287 | 38 | 29 | 3 | 0 | 0 | 0 | 1073
23-0114421 | Monterey | LOS COCHES 1101 | LOS COCHES 1101625902 | Environmental/External | 2023-09-09 07:55 | 9/5 - 9/11 | 2023-09-11 02:02 | 586.2778 | FTS | 10553 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 2527
23-0114725 | Madera | OAKHURST 1101 | OAKHURST 1101352740 | Environmental/External | 2023-09-10 18:47 | 9/5 - 9/11 | 2023-09-11 09:38 | 145.4565 | FTS | 227494 | 1564 | 177 | 129 | 34 | 3 | 0 | 0 | 891
23-0114728 | Monterey | SAN ARDO 1102 | SAN ARDO 11027030 | Unknown Cause | 2023-09-10 19:26 | 9/5 - 9/11 | 2023-09-11 11:43 | 977 | FTS | 103562 | 106 | 2 | 1 | 8 | 0 | 0 | 0 | 977
23-0114721 | Yuba | NARROWS 2101 | NARROWS 21011202 | 3rd Party | 2023-09-10 18:42 | 9/5 - 9/11 | 2023-09-11 12:50 | 850.9082 | FTS | 426305 | 501 | 41 | 26 | 2 | 0 | 0 | 4 | 1088
23-0114610 | Tuolumne | PEORIA 1705 | PEORIA 170570198 | Environmental/External | 2023-09-10 03:34 | 9/5 - 9/11 | 2023-09-11 14:00 | 851.3315 | FTS | 950086 | 1116 | 123 | 91 | 11 | 12 | 0 | 1 | 2066
23-0114995 | Placer | LINCOLN 1101 | LINCOLN 1101881364 | Unknown Cause | 2023-09-11 10:42 | 9/5 - 9/11 | 2023-09-11 14:39 | 237 | FTS | 13983 | 59 | 8 | 7 | 0 | 0 | 0 | 3 | 237
23-0114547 | Tuolumne | CURTIS 1703 | CURTIS 17036064 | Environmental/External | 2023-09-09 19:06 | 9/5 - 9/11 | 2023-09-11 15:00 | 1269.0783 | FTS | 486057 | 383 | 35 | 29 | 4 | 0 | 0 | 0 | 2634
23-0115075 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101730862 | 3rd Party | 2023-09-11 14:00 | 9/5 - 9/11 | 2023-09-11 15:39 | 99 | FTS | 3168 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 99
23-0114613 | Tuolumne | CURTIS 1704 | CURTIS 170411290 | Environmental/External | 2023-09-10 04:44 | 9/5 - 9/11 | 2023-09-11 16:17 | 943.5971 | FTS | 131160 | 139 | 14 | 12 | 2 | 0 | 0 | 1 | 2133
23-0115187 | Humboldt | FORT SEWARD 1121 | FORT SEWARD 1121CB | Company Initiated | 2023-09-11 16:04 | 9/5 - 9/11 | 2023-09-11 16:40 | 36 | FTS | 324 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 36
23-0115072 | Napa | CALISTOGA 1101 | CALISTOGA 11015934 | Unknown Cause | 2023-09-11 13:49 | 9/5 - 9/11 | 2023-09-11 16:55 | 163.4697 | FTS | 61955 | 379 | 13 | 10 | 1 | 0 | 0 | 1 | 186
23-0115209 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062796 | Company Initiated | 2023-09-11 18:06 | 9/12 - 9/18 | 2023-09-11 18:39 | 16.5907 | FTS | 59826 | 3606 | 292 | 212 | 34 | 3 | 0 | 21 | 33
23-0115213 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X06 | Unknown Cause | 2023-09-11 18:24 | 9/12 - 9/18 | 2023-09-11 21:36 | 192 | FTS | 33024 | 172 | 4 | 4 | 7 | 2 | 0 | 0 | 192
23-0115212 | Alameda | NORTH DUBLIN 2101 | NORTH DUBLIN 2101CB | Equipment Failure/Involved | 2023-09-11 18:22 | 9/12 - 9/18 | 2023-09-12 04:23 | 150.9097 | FTS | 837549 | 5550 | 98 | 74 | 23 | 1 | 0 | 0 | 601
23-0115267 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 1101CB | Vegetation | 2023-09-11 22:50 | 9/12 - 9/18 | 2023-09-12 05:52 | 77.2684 | FTS | 77732 | 1006 | 22 | 13 | 35 | 4 | 0 | 0 | 422
23-0115302 | Monterey | GABILAN 1101 | GABILAN 11013034 | Animal | 2023-09-12 06:57 | 9/12 - 9/18 | 2023-09-12 07:25 | 28 | FTS | 15232 | 544 | 33 | 23 | 12 | 0 | 0 | 0 | 28
23-0115303 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | 3rd Party | 2023-09-12 07:01 | 9/12 - 9/18 | 2023-09-12 07:26 | 25 | FTS | 22375 | 895 | 65 | 44 | 16 | 0 | 0 | 0 | 25
23-0115299 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Unknown Cause | 2023-09-12 06:33 | 9/12 - 9/18 | 2023-09-12 07:50 | 61.4706 | FTS | 10450 | 170 | 11 | 7 | 13 | 0 | 0 | 1 | 77
23-0115265 | Contra Costa | ROSSMOOR 1101 | ROSSMOOR 110181770 | Vegetation | 2023-09-11 22:40 | 9/12 - 9/18 | 2023-09-12 08:04 | 414.1392 | FTS | 145777 | 352 | 30 | 21 | 5 | 0 | 0 | 0 | 564
23-0115271 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102230414 | 3rd Party | 2023-09-11 23:18 | 9/12 - 9/18 | 2023-09-12 08:20 | 308.9027 | FTS | 104718 | 339 | 54 | 35 | 7 | 1 | 0 | 0 | 542
23-0114489 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | Environmental/External | 2023-09-09 15:13 | 9/12 - 9/18 | 2023-09-12 08:34 | 1076.1396 | FTS | 562821 | 523 | 66 | 47 | 4 | 0 | 0 | 0 | 3921
23-0114513 | Tuolumne | RACETRACK 1703 | RACETRACK 1703CB | Environmental/External | 2023-09-09 16:25 | 9/12 - 9/18 | 2023-09-12 08:55 | 475.0103 | FTS | 1476332 | 3108 | 277 | 211 | 62 | 16 | 1 | 0 | 3870
23-0115413 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Company Initiated | 2023-09-12 09:59 | 9/12 - 9/18 | 2023-09-12 10:51 | 52 | FTS | 172692 | 3321 | 172 | 121 | 62 | 2 | 0 | 4 | 52
23-0115321 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210611132 | Unknown Cause | 2023-09-12 07:41 | 9/12 - 9/18 | 2023-09-12 11:22 | 150.9069 | FTS | 457097 | 3029 | 231 | 178 | 66 | 15 | 0 | 4 | 221
23-0115280 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 110287432 | Unknown Cause | 2023-09-12 01:51 | 9/12 - 9/18 | 2023-09-12 11:47 | 596 | FTS | 41720 | 70 | 5 | 5 | 5 | 0 | 0 | 0 | 596
23-0114916 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029690 | Unknown Cause | 2023-09-11 10:32 | 9/12 - 9/18 | 2023-09-12 12:29 | 282.7241 | FTS | 193666 | 685 | 19 | 12 | 8 | 0 | 0 | 0 | 1557
23-0115508 | Sonoma | DUNBAR 1101 | DUNBAR 1101872066 | Unknown Cause | 2023-09-12 12:03 | 9/12 - 9/18 | 2023-09-12 13:17 | 74 | FTS | 2738 | 37 | 1 | 1 | 1 | 0 | 0 | 1 | 74
23-0089421 | Placer | HORSESHOE 1104 | HORSESHOE 110450142 | Equipment Failure/Involved | 2023-09-12 07:09 | 9/12 - 9/18 | 2023-09-12 14:57 | 193.6418 | FTS | 75133 | 388 | 37 | 22 | 5 | 0 | 0 | 0 | 468
23-0114758 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Environmental/External | 2023-09-09 17:16 | 9/12 - 9/18 | 2023-09-12 15:37 | 802.7343 | FTS | 2317494 | 2887 | 234 | 172 | 26 | 1 | 0 | 1 | 4221
23-0115503 | Contra Costa | NORTH TOWER 2101 | NORTH TOWER 2101CB | Unknown Cause | 2023-09-12 12:32 | 9/12 - 9/18 | 2023-09-12 18:29 | 192.8499 | FTS | 359665 | 1865 | 93 | 59 | 29 | 3 | 0 | 0 | 357
23-0115712 | Tuolumne | CURTIS 1702 | CURTIS 1702278740 | Unknown Cause | 2023-09-12 18:01 | 9/12 - 9/18 | 2023-09-12 20:50 | 148.6831 | FTS | 280565 | 1887 | 195 | 145 | 22 | 5 | 0 | 2 | 169
23-0115606 | Sonoma | MONTE RIO 1111 | MONTE RIO 1111969182 | 3rd Party | 2023-09-12 14:24 | 9/12 - 9/18 | 2023-09-13 01:18 | 125.7287 | FTS | 70911 | 564 | 31 | 21 | 16 | 1 | 0 | 0 | 654
23-0115800 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651484 | Vegetation | 2023-09-12 22:34 | 9/12 - 9/18 | 2023-09-13 04:08 | 57.9716 | FTS | 57218 | 987 | 68 | 53 | 11 | 2 | 0 | 5 | 334
23-0115703 | Nevada | NARROWS 2105 | NARROWS 21052748 | Vegetation | 2023-09-12 17:39 | 9/12 - 9/18 | 2023-09-13 05:17 | 67.9866 | FTS | 131486 | 1934 | 164 | 109 | 16 | 0 | 0 | 20 | 698
23-0115747 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2023-09-12 21:46 | 9/12 - 9/18 | 2023-09-13 05:40 | 474 | FTS | 4266 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 474
23-0115857 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Unknown Cause | 2023-09-13 06:39 | 9/12 - 9/18 | 2023-09-13 08:30 | 33.6627 | FTS | 50494 | 1500 | 68 | 58 | 15 | 3 | 0 | 13 | 111
23-0115890 | Lake | LUCERNE 1103 | LUCERNE 11034200 | 3rd Party | 2023-09-13 07:44 | 9/12 - 9/18 | 2023-09-13 09:58 | 133.4103 | FTS | 5203 | 39 | 2 | 2 | 7 | 0 | 0 | 0 | 134
23-0115965 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 1103N40 | Company Initiated | 2023-09-13 09:46 | 9/12 - 9/18 | 2023-09-13 10:25 | 39 | FTS | 35061 | 899 | 57 | 44 | 14 | 1 | 0 | 0 | 39
23-0115941 | Fresno | AUBERRY 1102 | AUBERRY 1102R2850 | Equipment Failure/Involved | 2023-09-13 09:16 | 9/12 - 9/18 | 2023-09-13 13:17 | 241 | FTS | 53984 | 224 | 29 | 20 | 7 | 4 | 0 | 1 | 241
23-0116047 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-09-13 11:32 | 9/12 - 9/18 | 2023-09-13 14:02 | 150 | FTS | 8100 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 150
23-0115938 | Contra Costa | CLAYTON 2212 | CLAYTON 221296224 | Animal | 2023-09-13 08:59 | 9/12 - 9/18 | 2023-09-13 14:05 | 187.0329 | FTS | 45449 | 243 | 19 | 11 | 3 | 0 | 0 | 1 | 306
23-0116129 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Company Initiated | 2023-09-13 13:07 | 9/12 - 9/18 | 2023-09-13 14:16 | 69 | FTS | 40158 | 582 | 59 | 45 | 3 | 4 | 0 | 2 | 69
23-0116053 | Shasta | COTTONWOOD 1102 | COTTONWOOD 11021578 | Unknown Cause | 2023-09-13 11:38 | 9/12 - 9/18 | 2023-09-13 15:07 | 201.1521 | FTS | 52903 | 263 | 38 | 30 | 2 | 0 | 0 | 1 | 209
23-0115839 | Tuolumne | CURTIS 1703 | CURTIS 17036064 | Equipment Failure/Involved | 2023-09-13 03:33 | 9/12 - 9/18 | 2023-09-13 15:47 | 278.9713 | FTS | 106846 | 383 | 35 | 29 | 4 | 0 | 0 | 0 | 734
23-0116127 | Tuolumne | CURTIS 1703 | CURTIS 1703CB | Unknown Cause | 2023-09-13 13:07 | 9/12 - 9/18 | 2023-09-13 15:48 | 160.5785 | FTS | 622884 | 3879 | 286 | 216 | 52 | 1 | 0 | 5 | 161
23-0116254 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062104 | Company Initiated | 2023-09-13 15:39 | 9/12 - 9/18 | 2023-09-13 16:56 | 23.243 | FTS | 52227 | 2247 | 160 | 121 | 19 | 3 | 0 | 14 | 77
23-0116279 | Santa Barbara | ZACA 1101 | ZACA 1101CB | Unknown Cause | 2023-09-13 16:47 | 9/12 - 9/18 | 2023-09-13 18:45 | 118 | FTS | 120596 | 1022 | 20 | 14 | 19 | 13 | 0 | 0 | 118
23-0116299 | Santa Clara | LOYOLA 1102 | LOYOLA 1102CB | Animal | 2023-09-13 18:09 | 9/12 - 9/18 | 2023-09-13 19:30 | 81 | FTS | 3240 | 40 | 3 | 3 | 1 | 0 | 0 | 0 | 81
23-0116307 | Napa | SILVERADO 2104 | SILVERADO 210437632 | Animal | 2023-09-13 19:12 | 9/12 - 9/18 | 2023-09-13 21:02 | 110 | FTS | 243210 | 2211 | 114 | 75 | 57 | 8 | 16 | 4 | 110
23-0115842 | Contra Costa | MORAGA 1103 | MORAGA 110381146 | Equipment Failure/Involved | 2023-09-13 05:26 | 9/12 - 9/18 | 2023-09-13 21:21 | 140.1775 | FTS | 331660 | 2366 | 125 | 101 | 30 | 7 | 0 | 0 | 955
23-0115295 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Equipment Failure/Involved | 2023-09-12 05:52 | 9/12 - 9/18 | 2023-09-14 02:22 | 69.9014 | FTS | 191320 | 2737 | 181 | 146 | 41 | 7 | 0 | 0 | 2670
23-0116392 | Butte | NOTRE DAME 1103 | NOTRE DAME 1103317782 | Animal | 2023-09-14 01:26 | 9/12 - 9/18 | 2023-09-14 04:07 | 161 | FTS | 18193 | 113 | 7 | 4 | 9 | 0 | 0 | 0 | 161
23-0116434 | Santa Cruz | CAMP EVERS 2104 | CAMP EVERS 2104CB | Animal | 2023-09-14 07:55 | 9/12 - 9/18 | 2023-09-14 09:00 | 38.0966 | FTS | 116728 | 3064 | 157 | 128 | 55 | 6 | 2 | 3 | 65
23-0116468 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Unknown Cause | 2023-09-14 08:44 | 9/12 - 9/18 | 2023-09-14 11:55 | 176.137 | FTS | 482087 | 2737 | 181 | 146 | 41 | 7 | 0 | 0 | 191
23-0116743 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121204 | Company Initiated | 2023-09-14 12:59 | 9/12 - 9/18 | 2023-09-14 14:33 | 94 | FTS | 1598 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 94
23-0116648 | Contra Costa | NORTH TOWER 2101 | NORTH TOWER 2101CB | Unknown Cause | 2023-09-14 12:24 | 9/12 - 9/18 | 2023-09-14 16:03 | 175.3474 | FTS | 323516 | 1845 | 93 | 59 | 26 | 3 | 0 | 0 | 219
23-0116314 | Contra Costa | NORTH TOWER 2101 | NORTH TOWER 2101CB | Equipment Failure/Involved | 2023-09-13 19:28 | 9/12 - 9/18 | 2023-09-14 16:51 | 150.4384 | FTS | 281019 | 1868 | 93 | 59 | 29 | 3 | 0 | 0 | 1283
23-0116845 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Unknown Cause | 2023-09-14 17:08 | 9/12 - 9/18 | 2023-09-14 19:12 | 74.7626 | FTS | 38428 | 514 | 55 | 32 | 4 | 0 | 0 | 3 | 124
23-0116413 | Colusa | ELK CREEK 1101 | ELK CREEK 11012008 | Animal | 2023-09-14 06:48 | 9/12 - 9/18 | 2023-09-14 19:57 | 263.9238 | FTS | 135129 | 512 | 37 | 25 | 22 | 3 | 0 | 0 | 789
23-0116906 | Placer | LINCOLN 1101 | LINCOLN 1101881364 | Unknown Cause | 2023-09-14 21:51 | 9/12 - 9/18 | 2023-09-15 00:14 | 143 | FTS | 8437 | 59 | 8 | 7 | 0 | 0 | 0 | 3 | 143
23-0116885 | Tuolumne | RACETRACK 1703 | RACETRACK 170311270 | Vegetation | 2023-09-14 19:30 | 9/12 - 9/18 | 2023-09-15 01:48 | 121.4911 | FTS | 41064 | 338 | 36 | 24 | 6 | 0 | 0 | 0 | 378
23-0116925 | Mendocino | UKIAH 1114 | UKIAH 1114408 | Vegetation | 2023-09-14 23:27 | 9/12 - 9/18 | 2023-09-15 06:30 | 115.8882 | FTS | 37316 | 322 | 17 | 9 | 8 | 1 | 0 | 0 | 423
23-0117027 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 1103540954 | Company Initiated | 2023-09-15 08:37 | 9/12 - 9/18 | 2023-09-15 09:12 | 33.1623 | FTS | 59659 | 1799 | 101 | 76 | 29 | 0 | 0 | 6 | 35
23-0108977 | Calaveras | WEST POINT 1102 | WEST POINT 11024790 | Company Initiated | 2023-09-15 09:06 | 9/12 - 9/18 | 2023-09-15 09:40 | 34 | FTS | 75174 | 2211 | 170 | 121 | 28 | 0 | 0 | 3 | 34
23-0117108 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Company Initiated | 2023-09-15 10:08 | 9/12 - 9/18 | 2023-09-15 10:37 | 29 | FTS | 30972 | 1068 | 85 | 58 | 14 | 0 | 0 | 6 | 29
23-0116965 | Fresno | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-09-15 06:52 | 9/12 - 9/18 | 2023-09-15 10:38 | 226 | FTS | 69834 | 309 | 10 | 6 | 7 | 0 | 0 | 0 | 226
23-0117273 | Placer | PENRYN 1105 | PENRYN 110551676 | 3rd Party | 2023-09-15 13:56 | 9/12 - 9/18 | 2023-09-15 14:36 | 35.9284 | FTS | 37150 | 1034 | 63 | 42 | 22 | 8 | 0 | 14 | 40
23-0117295 | Humboldt | EEL RIVER 1102 | EEL RIVER 110249130 | Company Initiated | 2023-09-15 13:55 | 9/12 - 9/18 | 2023-09-15 14:56 | 61 | FTS | 549 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 61
23-0117286 | Santa Clara | LOS GATOS 1106 | LOS GATOS 110660116 | Vegetation | 2023-09-15 14:20 | 9/12 - 9/18 | 2023-09-15 16:19 | 118.4972 | FTS | 188766 | 1593 | 154 | 123 | 27 | 3 | 0 | 8 | 119
23-0117310 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2023-09-15 15:10 | 9/12 - 9/18 | 2023-09-15 16:35 | 85 | FTS | 765 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 85
23-0117319 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101191544 | Unknown Cause | 2023-09-15 15:20 | 9/12 - 9/18 | 2023-09-15 17:36 | 136 | FTS | 104448 | 768 | 59 | 41 | 18 | 1 | 0 | 0 | 136
23-0117109 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401944178 | Vegetation | 2023-09-15 10:16 | 9/12 - 9/18 | 2023-09-15 18:38 | 91.5797 | FTS | 81048 | 885 | 81 | 65 | 16 | 3 | 0 | 1 | 502
23-0117359 | Placer | LINCOLN 1101 | LINCOLN 1101210168 | 3rd Party | 2023-09-15 18:19 | 9/12 - 9/18 | 2023-09-15 18:41 | 22 | FTS | 2486 | 113 | 6 | 4 | 0 | 0 | 0 | 4 | 22
23-0117356 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y36 | Unknown Cause | 2023-09-15 18:09 | 9/12 - 9/18 | 2023-09-15 19:13 | 64 | FTS | 17408 | 272 | 3 | 1 | 14 | 1 | 0 | 0 | 64
23-0117212 | Sonoma | MOLINO 1102 | MOLINO 1102178 | Unknown Cause | 2023-09-15 12:16 | 9/12 - 9/18 | 2023-09-15 21:32 | 214.8006 | FTS | 452370 | 2106 | 127 | 87 | 25 | 1 | 0 | 20 | 556
23-0117385 | Yuba | BANGOR 1101 | BANGOR 1101870548 | Animal | 2023-09-15 23:35 | 9/12 - 9/18 | 2023-09-16 08:28 | 233 | FTS | 14213 | 61 | 8 | 6 | 0 | 0 | 0 | 0 | 533
23-0117400 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Company Initiated | 2023-09-16 08:08 | 9/12 - 9/18 | 2023-09-16 09:07 | 59 | FTS | 55401 | 939 | 75 | 50 | 13 | 0 | 0 | 5 | 59
23-0117401 | Yuba | DOBBINS 1101 | DOBBINS 11015202 | Unknown Cause | 2023-09-16 08:31 | 9/12 - 9/18 | 2023-09-16 12:16 | 225 | FTS | 46575 | 207 | 9 | 7 | 4 | 0 | 0 | 0 | 225
23-0117387 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Vegetation | 2023-09-16 01:13 | 9/12 - 9/18 | 2023-09-16 12:38 | 489.3073 | FTS | 902772 | 1845 | 127 | 96 | 26 | 5 | 0 | 2 | 685
23-0117444 | Calaveras | FROGTOWN 1702 | FROGTOWN 170236870 | Unknown Cause | 2023-09-16 11:47 | 9/12 - 9/18 | 2023-09-16 13:40 | 113 | FTS | 41923 | 371 | 14 | 10 | 14 | 0 | 1 | 0 | 113
23-0117397 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029280 | Equipment Failure/Involved | 2023-09-16 07:57 | 9/12 - 9/18 | 2023-09-16 16:26 | 122.5961 | FTS | 188185 | 1535 | 41 | 27 | 18 | 2 | 0 | 0 | 509
23-0117416 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Equipment Failure/Involved | 2023-09-16 09:17 | 9/12 - 9/18 | 2023-09-16 17:46 | 171.984 | FTS | 268811 | 1563 | 99 | 74 | 24 | 5 | 0 | 1 | 509
23-0117508 | Lake | KONOCTI 1108 | KONOCTI 1108950 | 3rd Party | 2023-09-16 22:02 | 9/12 - 9/18 | 2023-09-17 04:58 | 98.623 | FTS | 102272 | 1037 | 133 | 91 | 12 | 1 | 0 | 0 | 416
23-0117520 | Monterey | HATTON 1101 | HATTON 110137088 | Unknown Cause | 2023-09-17 06:34 | 9/12 - 9/18 | 2023-09-17 08:28 | 111.5817 | FTS | 338539 | 3034 | 89 | 60 | 80 | 8 | 0 | 0 | 114
23-0117525 | Placer | WISE 1102 | WISE 1102307494 | Unknown Cause | 2023-09-17 07:34 | 9/12 - 9/18 | 2023-09-17 09:52 | 138 | FTS | 38088 | 276 | 26 | 19 | 3 | 0 | 0 | 4 | 138
23-0117526 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102CB | Unknown Cause | 2023-09-17 08:09 | 9/12 - 9/18 | 2023-09-17 10:00 | 103.0916 | FTS | 261028 | 2532 | 171 | 115 | 43 | 1 | 0 | 6 | 111
23-0117491 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR152 | Unknown Cause | 2023-09-16 18:04 | 9/12 - 9/18 | 2023-09-17 10:13 | 603.958 | FTS | 201118 | 333 | 27 | 23 | 1 | 0 | 1 | 1 | 969
23-0117517 | Santa Clara | HOLLISTER 2102 | HOLLISTER 2102113634 | 3rd Party | 2023-09-17 06:06 | 9/12 - 9/18 | 2023-09-17 11:21 | 160.0549 | FTS | 14565 | 91 | 2 | 0 | 3 | 0 | 0 | 0 | 315
23-0117538 | Napa | MONTICELLO 1101 | MONTICELLO 110152910 | Unknown Cause | 2023-09-17 09:07 | 9/12 - 9/18 | 2023-09-17 11:55 | 168 | FTS | 34608 | 206 | 10 | 5 | 4 | 1 | 0 | 0 | 168
23-0117521 | Sonoma | SONOMA 1104 | SONOMA 1104914376 | Unknown Cause | 2023-09-17 06:45 | 9/12 - 9/18 | 2023-09-17 12:05 | 101.2574 | FTS | 78272 | 773 | 39 | 28 | 11 | 1 | 0 | 5 | 320
23-0117559 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | 3rd Party | 2023-09-17 15:30 | 9/12 - 9/18 | 2023-09-17 17:10 | 100 | FTS | 4700 | 47 | 3 | 3 | 0 | 0 | 0 | 0 | 100
23-0117523 | Butte | WYANDOTTE 1103 | WYANDOTTE 11031508 | Animal | 2023-09-17 07:21 | 9/12 - 9/18 | 2023-09-17 17:12 | 201.4836 | FTS | 178313 | 885 | 36 | 24 | 15 | 0 | 0 | 2 | 591
23-0117560 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Animal | 2023-09-17 15:40 | 9/12 - 9/18 | 2023-09-17 17:59 | 93.5615 | FTS | 161300 | 1724 | 127 | 80 | 29 | 7 | 0 | 4 | 139
23-0117577 | Napa | PUEBLO 2104 | PUEBLO 2102279478 | Unknown Cause | 2023-09-17 19:32 | 9/12 - 9/18 | 2023-09-17 22:43 | 191 | FTS | 2674 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 191
23-0117593 | Sonoma | PETALUMA C 1109 | PETALUMA C 1109820458 | Unknown Cause | 2023-09-18 | 9/12 - 9/18 | 2023-09-18 01:28 | 88 | FTS | 4752 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 88
23-0117562 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 1101CB | 3rd Party | 2023-09-17 15:48 | 9/12 - 9/18 | 2023-09-18 02:02 | 182.3333 | FTS | 8205 | 45 | 6 | 5 | 0 | 0 | 0 | 0 | 614
23-0117646 | Shasta | GIRVAN 1101 | GIRVAN 1101323094 | Company Initiated | 2023-09-18 07:37 | 9/12 - 9/18 | 2023-09-18 08:10 | 33 | FTS | 2244 | 68 | 1 | 1 | 4 | 0 | 0 | 0 | 33
23-0117613 | Alameda | CAYETANO 2109 | CAYETANO 2109MR186 | Unknown Cause | 2023-09-18 06:31 | 9/12 - 9/18 | 2023-09-18 08:41 | 107.0964 | FTS | 306617 | 2863 | 165 | 114 | 30 | 8 | 0 | 0 | 130
23-0117651 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Vegetation | 2023-09-18 07:50 | 9/12 - 9/18 | 2023-09-18 10:28 | 119.7379 | FTS | 69448 | 580 | 35 | 26 | 13 | 2 | 0 | 0 | 158
23-0117664 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | Unknown Cause | 2023-09-18 08:16 | 9/12 - 9/18 | 2023-09-18 11:03 | 167 | FTS | 38076 | 228 | 14 | 10 | 1 | 0 | 0 | 0 | 167
23-0117740 | Shasta | BURNEY 1101 | BURNEY 1101519432 | Unknown Cause | 2023-09-18 10:43 | 9/12 - 9/18 | 2023-09-18 12:23 | 100 | FTS | 2100 | 21 | 0 | 0 | 9 | 0 | 0 | 0 | 100
23-0117561 | Sonoma | WINDSOR 1103 | WINDSOR 1103701650 | Animal | 2023-09-17 15:36 | 9/12 - 9/18 | 2023-09-18 13:47 | 101.2099 | FTS | 8198 | 81 | 8 | 3 | 0 | 0 | 0 | 1 | 1331
23-0117817 | Monterey | DOLAN ROAD 1101 | DOLAN ROAD 1101CB | Company Initiated | 2023-09-18 12:48 | 9/12 - 9/18 | 2023-09-18 13:55 | 67 | FTS | 54069 | 807 | 41 | 33 | 3 | 0 | 0 | 0 | 67
23-0117852 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121204 | Unknown Cause | 2023-09-18 13:08 | 9/12 - 9/18 | 2023-09-18 15:53 | 165 | FTS | 4125 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 165
23-0117821 | Shasta | KESWICK 1101 | KESWICK 11011590 | Equipment Failure/Involved | 2023-09-18 12:54 | 9/12 - 9/18 | 2023-09-18 16:57 | 203 | FTS | 10962 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 243
23-0117917 | Mendocino | GUALALA 1112 | GUALALA 1112CB | Vegetation | 2023-09-18 15:03 | 9/19 - 9/25 | 2023-09-18 17:13 | 47.1311 | FTS | 179051 | 3799 | 136 | 102 | 55 | 0 | 0 | 0 | 130
23-0117994 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210151584 | Animal | 2023-09-18 18:50 | 9/19 - 9/25 | 2023-09-18 19:40 | 50 | FTS | 33200 | 664 | 82 | 55 | 9 | 0 | 0 | 13 | 50
23-0117987 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102851902 | Animal | 2023-09-18 18:05 | 9/19 - 9/25 | 2023-09-18 20:24 | 81.7541 | FTS | 218447 | 2672 | 191 | 137 | 40 | 6 | 0 | 2 | 139
23-0118016 | Placer | LINCOLN 1101 | LINCOLN 1101881364 | Unknown Cause | 2023-09-19 01:28 | 9/19 - 9/25 | 2023-09-19 03:16 | 108 | FTS | 6372 | 59 | 8 | 7 | 0 | 0 | 0 | 3 | 108
23-0118027 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102347280 | Unknown Cause | 2023-09-19 06:49 | 9/19 - 9/25 | 2023-09-19 08:36 | 107 | FTS | 10700 | 100 | 4 | 3 | 1 | 0 | 0 | 2 | 107
23-0118102 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 1103N44 | Unknown Cause | 2023-09-19 08:53 | 9/19 - 9/25 | 2023-09-19 11:17 | 53.8873 | FTS | 64072 | 1189 | 37 | 21 | 25 | 1 | 0 | 3 | 144
23-0118245 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101518 | Company Initiated | 2023-09-19 12:49 | 9/19 - 9/25 | 2023-09-19 12:59 | 10 | FTS | 880 | 88 | 6 | 5 | 6 | 1 | 0 | 0 | 10
23-0118089 | Sonoma | MONTE RIO 1113 | MONTE RIO 11133970 | Unknown Cause | 2023-09-19 08:38 | 9/19 - 9/25 | 2023-09-19 13:04 | 181.3191 | FTS | 466534 | 2573 | 157 | 101 | 45 | 6 | 0 | 0 | 266
23-0117999 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | Unknown Cause | 2023-09-18 19:31 | 9/19 - 9/25 | 2023-09-19 13:40 | 972.3376 | FTS | 904274 | 930 | 22 | 17 | 10 | 0 | 0 | 6 | 1089
23-0118198 | Shasta | KESWICK 1101 | KESWICK 11011590 | Company Initiated | 2023-09-19 11:55 | 9/19 - 9/25 | 2023-09-19 13:53 | 118 | FTS | 6372 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 118
23-0118395 | Mendocino | WILLITS 1103 | WILLITS 1103409216 | Company Initiated | 2023-09-19 15:48 | 9/19 - 9/25 | 2023-09-19 16:38 | 50 | FTS | 2100 | 42 | 2 | 1 | 2 | 0 | 0 | 0 | 50
23-0118337 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110676088 | 3rd Party | 2023-09-19 15:00 | 9/19 - 9/25 | 2023-09-19 17:32 | 152 | FTS | 61712 | 406 | 39 | 33 | 1 | 0 | 0 | 14 | 152
23-0118327 | Butte | SYCAMORE CREEK 1111 | SYCAMORE CREEK 11112014 | Unknown Cause | 2023-09-19 14:48 | 9/19 - 9/25 | 2023-09-19 18:24 | 116.7135 | FTS | 62325 | 534 | 27 | 21 | 12 | 1 | 0 | 3 | 216
23-0118430 | Plumas | BIG MEADOWS 2101 | CRESCENT MILLS 21012230 | Company Initiated | 2023-09-19 18:07 | 9/19 - 9/25 | 2023-09-19 23:06 | 231.5613 | FTS | 84983 | 367 | 17 | 15 | 9 | 1 | 0 | 0 | 299
23-0118426 | Calaveras | PEORIA 1704 | PEORIA 170459596 | Animal | 2023-09-19 17:59 | 9/19 - 9/25 | 2023-09-20 01:44 | 241.0916 | FTS | 189498 | 786 | 66 | 53 | 30 | 1 | 0 | 1 | 465
23-0118415 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N48 | Equipment Failure/Involved | 2023-09-19 17:21 | 9/19 - 9/25 | 2023-09-20 02:55 | 120.1177 | FTS | 142820 | 1189 | 37 | 21 | 25 | 1 | 0 | 3 | 574
23-0118555 | Plumas | BIG MEADOWS 2101 | CRESCENT MILLS 21012230 | Company Initiated | 2023-09-20 07:34 | 9/19 - 9/25 | 2023-09-20 07:49 | 15 | FTS | 5505 | 367 | 17 | 15 | 9 | 1 | 0 | 0 | 15
23-0118550 | Placer | LINCOLN 1101 | LINCOLN 110195756 | Unknown Cause | 2023-09-20 07:24 | 9/19 - 9/25 | 2023-09-20 09:16 | 112 | FTS | 30464 | 272 | 28 | 22 | 0 | 0 | 0 | 6 | 112
23-0118631 | Shasta | VOLTA 1102 | VOLTA 11021502 | Company Initiated | 2023-09-20 09:04 | 9/19 - 9/25 | 2023-09-20 09:17 | 13 | FTS | 18408 | 1416 | 152 | 124 | 14 | 0 | 0 | 0 | 13
23-0118688 | Monterey | LAURELES 1111 | LAURELES 11112028 | Company Initiated | 2023-09-20 10:18 | 9/19 - 9/25 | 2023-09-20 10:28 | 10 | FTS | 3940 | 394 | 26 | 19 | 7 | 0 | 0 | 0 | 10
23-0118559 | Sonoma | PENNGROVE 1101 | PENNGROVE 1101950828 | Unknown Cause | 2023-09-20 07:43 | 9/19 - 9/25 | 2023-09-20 10:29 | 119.8473 | FTS | 31400 | 262 | 14 | 9 | 3 | 0 | 0 | 5 | 166
23-0089227 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101136050 | Equipment Failure/Involved | 2023-09-20 10:26 | 9/19 - 9/25 | 2023-09-20 11:05 | 39 | FTS | 8970 | 230 | 20 | 15 | 2 | 0 | 0 | 0 | 39
23-0118002 | Contra Costa | TASSAJARA 2103 | TASSAJARA 2103CB | Equipment Failure/Involved | 2023-09-18 21:00 | 9/19 - 9/25 | 2023-09-20 12:01 | 430.9277 | FTS | 1316484 | 3055 | 222 | 146 | 46 | 6 | 0 | 0 | 2341
23-0118727 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-09-20 11:26 | 9/19 - 9/25 | 2023-09-20 12:06 | 40 | FTS | 2160 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 40
23-0118587 | Calaveras | CORRAL 1101 | CORRAL 110175204 | Unknown Cause | 2023-09-20 08:04 | 9/19 - 9/25 | 2023-09-20 12:12 | 248 | FTS | 45136 | 182 | 3 | 2 | 4 | 0 | 0 | 0 | 248
23-0118924 | San Mateo | MENLO 1102 | MENLO 1102628458 | Company Initiated | 2023-09-20 16:04 | 9/19 - 9/25 | 2023-09-20 16:17 | 13 | FTS | 169 | 13 | 1 | 1 | 1 | 0 | 0 | 0 | 13
23-0118876 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113R82 | Animal | 2023-09-20 15:00 | 9/19 - 9/25 | 2023-09-20 17:25 | 43.7186 | FTS | 39303 | 899 | 41 | 29 | 12 | 2 | 0 | 7 | 145
23-0118747 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | 3rd Party | 2023-09-20 11:58 | 9/19 - 9/25 | 2023-09-20 20:30 | 208.494 | FTS | 173884 | 834 | 75 | 54 | 13 | 0 | 0 | 0 | 512
23-0119011 | Amador | SALT SPRINGS 2101 | SALT SPRINGS 210110416 | Environmental/External | 2023-09-21 04:46 | 9/19 - 9/25 | 2023-09-21 09:37 | 261.9474 | FTS | 14931 | 57 | 1 | 0 | 3 | 0 | 0 | 0 | 291
23-0119114 | Contra Costa | ROSSMOOR 1109 | ROSSMOOR 1109724062 | Unknown Cause | 2023-09-21 08:46 | 9/19 - 9/25 | 2023-09-21 10:03 | 73.7112 | FTS | 27052 | 367 | 72 | 49 | 5 | 1 | 0 | 1 | 77
23-0118983 | Monterey | LAURELES 1111 | LAURELES 1111432 | Unknown Cause | 2023-09-20 21:51 | 9/19 - 9/25 | 2023-09-21 11:23 | 622.9598 | FTS | 201216 | 323 | 6 | 5 | 7 | 0 | 0 | 0 | 812
23-0119095 | Tuolumne | CURTIS 1703 | CURTIS 1703258550 | Animal | 2023-09-21 08:21 | 9/19 - 9/25 | 2023-09-21 11:47 | 111.1046 | FTS | 284650 | 2562 | 171 | 134 | 43 | 1 | 0 | 1 | 206
23-0119184 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | 3rd Party | 2023-09-21 10:21 | 9/19 - 9/25 | 2023-09-21 12:08 | 105.9292 | FTS | 109213 | 1031 | 69 | 56 | 42 | 10 | 0 | 1 | 107
23-0119334 | Mendocino | WILLITS 1103 | WILLITS 1103409216 | Company Initiated | 2023-09-21 13:47 | 9/19 - 9/25 | 2023-09-21 14:49 | 62 | FTS | 14508 | 234 | 17 | 9 | 8 | 0 | 0 | 0 | 62
23-0119200 | Contra Costa | TIDEWATER 2106 | TIDEWATER 210657926 | Unknown Cause | 2023-09-21 10:34 | 9/19 - 9/25 | 2023-09-21 15:11 | 176.4105 | FTS | 393219 | 2229 | 174 | 116 | 74 | 5 | 0 | 0 | 277
23-0119256 | Humboldt | HOOPA 1101 | HOOPA 11013304 | 3rd Party | 2023-09-21 11:33 | 9/19 - 9/25 | 2023-09-21 15:14 | 221 | FTS | 148733 | 673 | 21 | 19 | 24 | 5 | 0 | 0 | 221
23-0119269 | Sonoma | MONTE RIO 1111 | MONTE RIO 1111969182 | Unknown Cause | 2023-09-21 12:11 | 9/19 - 9/25 | 2023-09-21 16:14 | 191.8617 | FTS | 108210 | 564 | 31 | 21 | 16 | 1 | 0 | 0 | 243
23-0119405 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210151584 | Animal | 2023-09-21 15:46 | 9/19 - 9/25 | 2023-09-21 16:40 | 54 | FTS | 35856 | 664 | 82 | 55 | 9 | 0 | 0 | 13 | 54
23-0119304 | Santa Barbara | ZACA 1101 | ZACA 1101CB | Unknown Cause | 2023-09-21 13:15 | 9/19 - 9/25 | 2023-09-21 16:50 | 117.8914 | FTS | 120485 | 1022 | 20 | 14 | 19 | 13 | 0 | 0 | 215
23-0119306 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V46 | Unknown Cause | 2023-09-21 13:22 | 9/19 - 9/25 | 2023-09-21 16:56 | 214 | FTS | 48150 | 225 | 3 | 3 | 10 | 0 | 0 | 0 | 214
23-0119484 | Shasta | DESCHUTES 1101 | DESCHUTES 11011380 | Equipment Failure/Involved | 2023-09-21 21:36 | 9/19 - 9/25 | 2023-09-22 02:59 | 263.3997 | FTS | 154879 | 588 | 47 | 31 | 8 | 1 | 0 | 2 | 323
23-0119577 | Santa Clara | LOS GATOS 1108 | LOS GATOS 1108590544 | Animal | 2023-09-22 08:02 | 9/19 - 9/25 | 2023-09-22 09:26 | 84 | FTS | 66276 | 789 | 24 | 16 | 4 | 1 | 0 | 0 | 84
23-0119581 | Napa | MONTICELLO 1101 | MONTICELLO 1101718 | Equipment Failure/Involved | 2023-09-22 07:56 | 9/19 - 9/25 | 2023-09-22 15:15 | 265.0952 | FTS | 55670 | 210 | 11 | 8 | 3 | 0 | 0 | 1 | 439
23-0119701 | Mariposa | OAKHURST 1103 | OAKHURST 11035480 | Vegetation | 2023-09-22 10:27 | 9/19 - 9/25 | 2023-09-22 17:12 | 158.5122 | FTS | 182289 | 1150 | 39 | 29 | 28 | 10 | 0 | 0 | 405
23-0119951 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113CB | Animal | 2023-09-22 18:43 | 9/19 - 9/25 | 2023-09-22 20:56 | 69.3028 | FTS | 386987 | 5584 | 302 | 217 | 84 | 10 | 1 | 20 | 133
23-0119968 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2023-09-22 20:55 | 9/19 - 9/25 | 2023-09-22 22:13 | 78 | FTS | 702 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 78
23-0119988 | Humboldt | ARCATA 1121 | ARCATA 1121716954 | Unknown Cause | 2023-09-23 04:32 | 9/19 - 9/25 | 2023-09-23 07:03 | 80.9877 | FTS | 13201 | 163 | 13 | 9 | 6 | 1 | 0 | 0 | 151
23-0119993 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Animal | 2023-09-23 06:51 | 9/19 - 9/25 | 2023-09-23 07:47 | 34.6471 | FTS | 5890 | 170 | 11 | 7 | 13 | 0 | 0 | 1 | 56
23-0119987 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 1101528344 | Vegetation | 2023-09-23 03:42 | 9/19 - 9/25 | 2023-09-23 08:12 | 169.3355 | FTS | 25739 | 152 | 6 | 5 | 5 | 5 | 0 | 2 | 270
23-0120001 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2023-09-23 07:35 | 9/19 - 9/25 | 2023-09-23 09:19 | 104 | FTS | 936 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 104
23-0120012 | Calaveras | PEORIA 1704 | PEORIA 1704CB | Equipment Failure/Involved | 2023-09-23 08:38 | 9/19 - 9/25 | 2023-09-23 11:09 | 151 | FTS | 485616 | 3216 | 284 | 207 | 78 | 1 | 1 | 2 | 151
23-0120025 | Contra Costa | MEADOW LANE 2106 | MEADOW LANE 2106C558R | Company Initiated | 2023-09-23 09:48 | 9/19 - 9/25 | 2023-09-23 12:00 | 60.7068 | FTS | 189648 | 3124 | 227 | 163 | 36 | 6 | 0 | 0 | 132
23-0120023 | Plumas | BIG MEADOWS 2101 | CRESCENT MILLS 21012230 | Company Initiated | 2023-09-23 09:39 | 9/19 - 9/25 | 2023-09-23 12:32 | 121.5014 | FTS | 44591 | 367 | 17 | 15 | 9 | 1 | 0 | 0 | 173
23-0120026 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103248212 | 3rd Party | 2023-09-23 10:09 | 9/19 - 9/25 | 2023-09-23 13:05 | 154.9674 | FTS | 28514 | 184 | 9 | 6 | 8 | 0 | 0 | 0 | 176
23-0119994 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210151584 | Unknown Cause | 2023-09-23 06:59 | 9/19 - 9/25 | 2023-09-23 13:14 | 375 | FTS | 249000 | 664 | 82 | 55 | 9 | 0 | 0 | 13 | 375
23-0120043 | Nevada | NARROWS 2102 | NARROWS 210276952 | Animal | 2023-09-23 12:11 | 9/19 - 9/25 | 2023-09-23 13:35 | 61.2478 | FTS | 55368 | 904 | 86 | 61 | 13 | 0 | 0 | 2 | 84
23-0120037 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Unknown Cause | 2023-09-23 09:01 | 9/19 - 9/25 | 2023-09-23 13:36 | 265.9804 | FTS | 27130 | 102 | 2 | 2 | 12 | 11 | 0 | 0 | 275
23-0119980 | Marin | PETALUMA C 1108 | PETALUMA C 1108296 | 3rd Party | 2023-09-23 00:09 | 9/19 - 9/25 | 2023-09-23 14:06 | 369.4228 | FTS | 45439 | 123 | 8 | 2 | 1 | 1 | 0 | 0 | 837
23-0120016 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Unknown Cause | 2023-09-23 09:08 | 9/19 - 9/25 | 2023-09-23 14:41 | 333 | FTS | 162504 | 488 | 9 | 7 | 13 | 3 | 0 | 0 | 333
23-0120085 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Animal | 2023-09-23 17:13 | 9/19 - 9/25 | 2023-09-23 19:34 | 141 | FTS | 80511 | 571 | 37 | 25 | 26 | 3 | 0 | 0 | 141
23-0120120 | Napa | PUEBLO 2104 | PUEBLO 2102391312 | Unknown Cause | 2023-09-23 23:22 | 9/19 - 9/25 | 2023-09-24 06:46 | 444 | FTS | 7548 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 444
23-0120124 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 110582622 | Vegetation | 2023-09-24 02:25 | 9/19 - 9/25 | 2023-09-24 09:41 | 255.1439 | FTS | 104609 | 410 | 37 | 22 | 10 | 0 | 0 | 4 | 436
23-0120095 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Unknown Cause | 2023-09-23 19:44 | 9/19 - 9/25 | 2023-09-24 09:42 | 380.1134 | FTS | 221226 | 582 | 59 | 45 | 3 | 4 | 0 | 2 | 838
23-0120130 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106CB | Unknown Cause | 2023-09-24 06:59 | 9/19 - 9/25 | 2023-09-24 10:14 | 195 | FTS | 67470 | 346 | 40 | 35 | 5 | 1 | 0 | 5 | 195
23-0120149 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Animal | 2023-09-24 13:16 | 9/19 - 9/25 | 2023-09-24 15:29 | 66.5727 | FTS | 99859 | 1500 | 68 | 58 | 15 | 3 | 0 | 13 | 133
23-0120137 | Solano | PUTAH CREEK 1102 | PUTAH CREEK 110264044 | Unknown Cause | 2023-09-24 09:59 | 9/19 - 9/25 | 2023-09-24 16:49 | 81.3511 | FTS | 21314 | 262 | 12 | 8 | 5 | 0 | 0 | 3 | 410
23-0120156 | Contra Costa | SOBRANTE 1101 | SOBRANTE 1101CB | Unknown Cause | 2023-09-24 16:00 | 9/19 - 9/25 | 2023-09-24 19:05 | 98.4979 | FTS | 209702 | 2129 | 93 | 71 | 22 | 4 | 0 | 1 | 185
23-0120131 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106697500 | Equipment Failure/Involved | 2023-09-24 07:19 | 9/19 - 9/25 | 2023-09-24 19:26 | 496.4572 | FTS | 1066390 | 2148 | 188 | 148 | 54 | 8 | 0 | 10 | 727
23-0120161 | Placer | BELL 1107 | BELL 110750172 | Animal | 2023-09-24 16:31 | 9/19 - 9/25 | 2023-09-24 21:36 | 88.6364 | FTS | 30225 | 341 | 28 | 18 | 4 | 0 | 0 | 2 | 305
23-0120191 | Humboldt | TRINIDAD SUB | N/A | Vegetation | 2023-09-25 01:15 | 9/19 - 9/25 | 2023-09-25 04:11 | 176 | T-EPSS | 276144 | 1569 | 98 | 81 | 45 | 4 | 0 | 4 | 176
23-0120192 | Humboldt | ORICK SUB | N/A | Vegetation | 2023-09-25 01:15 | 9/19 - 9/25 | 2023-09-25 06:56 | 340.4943 | T-EPSS | 118492 | 348 | 13 | 10 | 8 | 1 | 0 | 0 | 341
23-0120198 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 2102767046 | Unknown Cause | 2023-09-25 04:34 | 9/19 - 9/25 | 2023-09-25 07:42 | 188 | FTS | 8272 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 188
23-0120213 | Humboldt | HOOPA 1101 | HOOPA 1101405280 | Vegetation | 2023-09-25 06:46 | 9/19 - 9/25 | 2023-09-25 08:32 | 57.7186 | FTS | 106664 | 1848 | 84 | 63 | 53 | 17 | 1 | 0 | 106
23-0120347 | Humboldt | CARLOTTA 1121 | CARLOTTA 112144150 | Unknown Cause | 2023-09-25 10:29 | 9/19 - 9/25 | 2023-09-25 11:17 | 48 | FTS | 432 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 48
23-0120340 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | Animal | 2023-09-25 10:12 | 9/19 - 9/25 | 2023-09-25 12:11 | 119 | FTS | 46053 | 387 | 27 | 18 | 10 | 0 | 0 | 0 | 119
23-0120204 | Humboldt | HUMBOLDT BAY 1102 | HUMBOLDT BAY 1102104220 | Vegetation | 2023-09-25 05:44 | 9/19 - 9/25 | 2023-09-25 14:09 | 121.8455 | FTS | 26806 | 220 | 17 | 10 | 2 | 0 | 0 | 0 | 505
23-0120475 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102262 | Unknown Cause | 2023-09-25 13:33 | 9/19 - 9/25 | 2023-09-25 15:52 | 123.2507 | FTS | 44740 | 363 | 20 | 15 | 11 | 0 | 0 | 5 | 139
23-0120541 | Sonoma | PETALUMA C 1109 | PETALUMA C 1109259100 | Unknown Cause | 2023-09-25 15:07 | 9/19 - 9/25 | 2023-09-25 16:03 | 56 | FTS | 728 | 13 | 0 | 0 | 2 | 0 | 0 | 0 | 56
23-0120555 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Unknown Cause | 2023-09-25 15:23 | 9/19 - 9/25 | 2023-09-25 16:40 | 77 | FTS | 44814 | 582 | 59 | 45 | 3 | 4 | 0 | 2 | 77
23-0120524 | Shasta | MC ARTHUR 1101 | MC ARTHUR 11011488 | Unknown Cause | 2023-09-25 14:40 | 9/26 - 10/2 | 2023-09-25 17:17 | 72.8447 | FTS | 22509 | 309 | 15 | 10 | 1 | 0 | 0 | 0 | 157
23-0120451 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11021510 | Vegetation | 2023-09-25 12:52 | 9/26 - 10/2 | 2023-09-25 17:28 | 274.9258 | FTS | 229838 | 836 | 18 | 14 | 29 | 6 | 0 | 0 | 276
23-0120499 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V46 | Unknown Cause | 2023-09-25 14:11 | 9/26 - 10/2 | 2023-09-25 17:41 | 201.28 | FTS | 45288 | 225 | 3 | 3 | 10 | 0 | 0 | 0 | 210
23-0120615 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11022124 | 3rd Party | 2023-09-25 18:32 | 9/26 - 10/2 | 2023-09-25 19:17 | 45 | FTS | 180 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 45
23-0120600 | Placer | PLACER 1104 | AUBURN 1102251946 | Unknown Cause | 2023-09-25 17:00 | 9/26 - 10/2 | 2023-09-25 19:51 | 169.3034 | FTS | 167949 | 992 | 50 | 30 | 11 | 2 | 0 | 0 | 171
23-0120604 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 1105640888 | Unknown Cause | 2023-09-25 17:06 | 9/26 - 10/2 | 2023-09-25 20:41 | 215 | FTS | 21285 | 99 | 6 | 6 | 0 | 0 | 0 | 0 | 215
23-0120453 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | 3rd Party | 2023-09-25 13:07 | 9/26 - 10/2 | 2023-09-25 21:58 | 108.2685 | FTS | 296331 | 2737 | 181 | 146 | 41 | 7 | 0 | 0 | 531
23-0120609 | Humboldt | RIO DELL 1101 | RIO DELL 11018768 | Vegetation | 2023-09-25 17:33 | 9/26 - 10/2 | 2023-09-25 23:57 | 241.7078 | FTS | 74446 | 308 | 11 | 8 | 3 | 0 | 0 | 0 | 384
23-0120685 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410960 | Unknown Cause | 2023-09-26 00:34 | 9/26 - 10/2 | 2023-09-26 01:57 | 35.328 | FTS | 84540 | 2393 | 186 | 155 | 34 | 6 | 0 | 2 | 83
23-0120677 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 1105640888 | Unknown Cause | 2023-09-25 22:50 | 9/26 - 10/2 | 2023-09-26 02:30 | 220 | FTS | 21780 | 99 | 6 | 6 | 0 | 0 | 0 | 0 | 220
23-0120689 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Equipment Failure/Involved | 2023-09-26 01:19 | 9/26 - 10/2 | 2023-09-26 06:30 | 169.3582 | FTS | 11347 | 67 | 4 | 3 | 4 | 1 | 0 | 0 | 311
23-0120691 | Napa | SILVERADO 2104 | SILVERADO 2104722 | Unknown Cause | 2023-09-26 01:56 | 9/26 - 10/2 | 2023-09-26 08:24 | 324.8107 | FTS | 169876 | 523 | 36 | 27 | 17 | 2 | 1 | 2 | 388
23-0120752 | Amador | ELECTRA 1102 | ELECTRA 11026014 | Unknown Cause | 2023-09-26 06:49 | 9/26 - 10/2 | 2023-09-26 08:37 | 108 | FTS | 3996 | 37 | 1 | 1 | 0 | 0 | 0 | 0 | 108
23-0120706 | Napa | SILVERADO 2102 | SILVERADO 2102285782 | Animal | 2023-09-26 05:11 | 9/26 - 10/2 | 2023-09-26 08:56 | 225 | FTS | 23625 | 105 | 1 | 1 | 1 | 0 | 0 | 0 | 225
23-0120768 | Placer | WEIMAR 1101 | WEIMAR 11012058 | Animal | 2023-09-26 07:57 | 9/26 - 10/2 | 2023-09-26 09:15 | 78 | FTS | 46332 | 594 | 41 | 30 | 9 | 0 | 0 | 3 | 78
23-0120778 | Marin | PETALUMA C 1108 | PETALUMA C 1108618 | Unknown Cause | 2023-09-26 08:33 | 9/26 - 10/2 | 2023-09-26 09:19 | 37.7907 | FTS | 26907 | 712 | 32 | 24 | 10 | 3 | 0 | 1 | 46
23-0120758 | Colusa | CORTINA 1101 | CORTINA 110130262 | Unknown Cause | 2023-09-26 07:49 | 9/26 - 10/2 | 2023-09-26 09:37 | 108 | FTS | 2592 | 24 | 2 | 2 | 0 | 0 | 0 | 0 | 108
23-0120790 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101502 | Company Initiated | 2023-09-26 08:59 | 9/26 - 10/2 | 2023-09-26 09:42 | 43 | FTS | 39216 | 912 | 48 | 38 | 23 | 0 | 0 | 0 | 43
23-0120687 | Sonoma | MIRABEL 1101 | MIRABEL 1101228 | Unknown Cause | 2023-09-26 00:59 | 9/26 - 10/2 | 2023-09-26 09:52 | 455.5102 | FTS | 111600 | 245 | 14 | 12 | 4 | 0 | 0 | 3 | 533
23-0120613 | Sonoma | DUNBAR 1102 | DUNBAR 1102246 | Unknown Cause | 2023-09-25 18:40 | 9/26 - 10/2 | 2023-09-26 10:46 | 291.2212 | FTS | 156677 | 538 | 25 | 15 | 8 | 0 | 0 | 6 | 966
23-0120785 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102CB | 3rd Party | 2023-09-26 08:46 | 9/26 - 10/2 | 2023-09-26 10:59 | 133 | FTS | 70889 | 533 | 29 | 16 | 14 | 2 | 0 | 0 | 133
23-0120796 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 11029460 | Animal | 2023-09-26 09:10 | 9/26 - 10/2 | 2023-09-26 11:14 | 93.0184 | FTS | 121575 | 1307 | 116 | 77 | 25 | 5 | 0 | 0 | 124
23-0120193 | Humboldt | HOOPA 1101 | HOOPA 110182542 | Vegetation | 2023-09-25 02:35 | 9/26 - 10/2 | 2023-09-26 13:11 | 565.1169 | FTS | 140149 | 248 | 16 | 10 | 8 | 0 | 0 | 0 | 2076
23-0120943 | Lake | UPPER LAKE 1101 | UPPER LAKE 1101CB | Unknown Cause | 2023-09-26 11:49 | 9/26 - 10/2 | 2023-09-26 13:54 | 125 | FTS | 130250 | 1042 | 70 | 45 | 14 | 5 | 0 | 1 | 125
23-0121015 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102156 | Company Initiated | 2023-09-26 13:31 | 9/26 - 10/2 | 2023-09-26 14:02 | 31 | FTS | 16740 | 540 | 35 | 21 | 10 | 0 | 0 | 0 | 31
23-0121022 | Santa Barbara | SISQUOC 1103 | SISQUOC 1103M98 | Animal | 2023-09-26 13:33 | 9/26 - 10/2 | 2023-09-26 14:55 | 75.2 | FTS | 2632 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 82
23-0121054 | Santa Cruz | SAN BENITO 2104 | SAN BENITO 210488772 | Vegetation | 2023-09-26 14:14 | 9/26 - 10/2 | 2023-09-26 16:27 | 125.4701 | FTS | 157465 | 1255 | 95 | 81 | 21 | 2 | 0 | 3 | 133
23-0121183 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A88 | Animal | 2023-09-26 19:22 | 9/26 - 10/2 | 2023-09-26 20:33 | 70.6724 | FTS | 126857 | 1795 | 67 | 40 | 9 | 2 | 0 | 0 | 71
23-0121115 | Tehama | RED BLUFF 1105 | RED BLUFF 110585632 | 3rd Party | 2023-09-26 15:50 | 9/26 - 10/2 | 2023-09-27 00:47 | 171.5384 | FTS | 172053 | 1003 | 109 | 77 | 20 | 1 | 0 | 7 | 537
23-0121246 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 110192870 | Unknown Cause | 2023-09-27 01:30 | 9/26 - 10/2 | 2023-09-27 03:25 | 115 | FTS | 77280 | 672 | 36 | 27 | 10 | 0 | 0 | 0 | 115
23-0121276 | Calaveras | CORRAL 1103 | CORRAL 1103CB | Animal | 2023-09-27 06:34 | 9/26 - 10/2 | 2023-09-27 07:14 | 40 | FTS | 5560 | 139 | 11 | 5 | 2 | 0 | 0 | 0 | 40
23-0121252 | Mendocino | FORT BRAGG A 1102 | FORT BRAGG A 110233064 | Unknown Cause | 2023-09-27 02:53 | 9/26 - 10/2 | 2023-09-27 07:54 | 294.0584 | FTS | 75573 | 257 | 9 | 7 | 4 | 2 | 0 | 0 | 301
23-0121309 | Solano | JAMESON 1105 | JAMESON 1105466348 | Vegetation | 2023-09-27 07:48 | 9/26 - 10/2 | 2023-09-27 09:17 | 89 | FTS | 31150 | 350 | 14 | 7 | 7 | 2 | 0 | 2 | 89
23-0121188 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113320 | Unknown Cause | 2023-09-26 20:01 | 9/26 - 10/2 | 2023-09-27 09:48 | 65.0751 | FTS | 26876 | 413 | 27 | 20 | 4 | 0 | 0 | 0 | 827
23-0121374 | Sonoma | PETALUMA C 1109 | PETALUMA C 1109259100 | Unknown Cause | 2023-09-27 09:17 | 9/26 - 10/2 | 2023-09-27 10:53 | 96 | FTS | 1248 | 13 | 0 | 0 | 2 | 0 | 0 | 0 | 96
23-0121273 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown Cause | 2023-09-27 06:43 | 9/26 - 10/2 | 2023-09-27 11:54 | 253.8931 | FTS | 128216 | 505 | 29 | 21 | 11 | 0 | 0 | 2 | 311
23-0121454 | Santa Clara | EDENVALE 2105 | EDENVALE 2105CB | Equipment Failure/Involved | 2023-09-27 10:36 | 9/26 - 10/2 | 2023-09-27 13:14 | 158 | FTS | 972174 | 6153 | 171 | 105 | 87 | 4 | 1 | 0 | 158
23-0121348 | Marin | PETALUMA C 1108 | PETALUMA C 1108618 | Equipment Failure/Involved | 2023-09-27 08:36 | 9/26 - 10/2 | 2023-09-27 16:25 | 222.1742 | FTS | 158188 | 712 | 32 | 24 | 10 | 3 | 0 | 1 | 469
23-0121647 | San Luis Obispo | MESA 1101 | MESA 1101M86 | Unknown Cause | 2023-09-27 14:37 | 9/26 - 10/2 | 2023-09-27 17:25 | 168 | FTS | 127008 | 756 | 38 | 27 | 14 | 3 | 0 | 8 | 168
23-0121371 | Humboldt | MAPLE CREEK 1101 | MAPLE CREEK 11016906 | Equipment Failure/Involved | 2023-09-27 09:03 | 9/26 - 10/2 | 2023-09-27 17:34 | 511 | FTS | 55699 | 109 | 7 | 5 | 16 | 2 | 0 | 2 | 511
23-0121753 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Company Initiated | 2023-09-27 16:31 | 9/26 - 10/2 | 2023-09-27 19:06 | 155 | FTS | 380370 | 2454 | 99 | 78 | 27 | 3 | 2 | 0 | 155
23-0120842 | Humboldt | HOOPA 1101 | HOOPA 11013304 | Equipment Failure/Involved | 2023-09-26 09:53 | 9/26 - 10/2 | 2023-09-27 19:21 | 1639.0951 | FTS | 1103111 | 673 | 21 | 19 | 24 | 5 | 0 | 0 | 2008
23-0121256 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102280 | Equipment Failure/Involved | 2023-09-27 04:50 | 9/26 - 10/2 | 2023-09-27 21:22 | 194.36 | FTS | 9718 | 50 | 5 | 2 | 0 | 0 | 0 | 0 | 992
23-0121763 | San Luis Obispo | SAN LUIS OBISPO 1103 | SAN LUIS OBISPO 1103V82 | Equipment Failure/Involved | 2023-09-27 18:18 | 9/26 - 10/2 | 2023-09-28 00:39 | 261.5907 | FTS | 337452 | 1290 | 43 | 35 | 35 | 3 | 2 | 3 | 381
23-0121807 | San Luis Obispo | SAN LUIS OBISPO 1103 | SAN LUIS OBISPO 1103V82 | Company Initiated | 2023-09-28 00:47 | 9/26 - 10/2 | 2023-09-28 00:54 | 7 | FTS | 9037 | 1291 | 43 | 35 | 35 | 3 | 2 | 3 | 7
23-0121845 | Sonoma | COTATI 1103 | COTATI 110379140 | Unknown Cause | 2023-09-28 07:06 | 9/26 - 10/2 | 2023-09-28 07:22 | 16 | FTS | 5648 | 353 | 27 | 21 | 6 | 0 | 0 | 5 | 16
23-0121819 | Marin | PETALUMA C 1108 | PETALUMA C 1108618 | Company Initiated | 2023-09-28 05:29 | 9/26 - 10/2 | 2023-09-28 07:55 | 116.6489 | FTS | 83054 | 712 | 32 | 24 | 10 | 3 | 0 | 1 | 146
23-0121802 | Butte | OROVILLE 1104 | OROVILLE 11042588 | 3rd Party | 2023-09-27 23:31 | 9/26 - 10/2 | 2023-09-28 08:21 | 122.4746 | FTS | 202818 | 1656 | 178 | 126 | 19 | 5 | 1 | 0 | 530
23-0121833 | Lake | UPPER LAKE 1101 | UPPER LAKE 1101412 | 3rd Party | 2023-09-28 06:45 | 9/26 - 10/2 | 2023-09-28 09:59 | 187.5901 | FTS | 30202 | 161 | 19 | 10 | 0 | 0 | 0 | 0 | 194
23-0121950 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 21059480 | Unknown Cause | 2023-09-28 09:25 | 9/26 - 10/2 | 2023-09-28 10:55 | 90 | FTS | 81360 | 904 | 75 | 53 | 18 | 1 | 0 | 0 | 90
23-0122065 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2104CB | Company Initiated | 2023-09-28 11:16 | 9/26 - 10/2 | 2023-09-28 11:40 | 24 | FTS | 3312 | 138 | 11 | 3 | 4 | 0 | 0 | 5 | 24
23-0121866 | Shasta | PIT NO 3 2101 | PIT NO 3 21011480 | Unknown Cause | 2023-09-28 07:39 | 9/26 - 10/2 | 2023-09-28 12:02 | 82.1719 | FTS | 10518 | 128 | 3 | 3 | 3 | 0 | 0 | 0 | 263
23-0122213 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 110192870 | Animal | 2023-09-28 13:47 | 9/26 - 10/2 | 2023-09-28 14:46 | 59 | FTS | 39648 | 672 | 36 | 27 | 10 | 0 | 0 | 0 | 59
23-0121881 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101277014 | Equipment Failure/Involved | 2023-09-28 08:02 | 9/26 - 10/2 | 2023-09-28 14:53 | 129.4698 | FTS | 47127 | 364 | 3 | 3 | 27 | 0 | 0 | 0 | 411
23-0122078 | Tehama | CORNING 1101 | CORNING 1101972454 | Company Initiated | 2023-09-28 11:36 | 9/26 - 10/2 | 2023-09-28 15:14 | 212.3803 | FTS | 191567 | 902 | 104 | 69 | 17 | 2 | 0 | 0 | 218
23-0122229 | Yolo | MADISON 2101 | MADISON 2101274974 | Unknown Cause | 2023-09-28 14:56 | 9/26 - 10/2 | 2023-09-28 15:32 | 36 | FTS | 1080 | 30 | 4 | 4 | 2 | 0 | 0 | 0 | 36
23-0122287 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311046 | Company Initiated | 2023-09-28 17:50 | 9/26 - 10/2 | 2023-09-28 18:09 | 19 | FTS | 12958 | 682 | 49 | 38 | 14 | 2 | 0 | 7 | 19
23-0121851 | Contra Costa | TASSAJARA 2103 | TASSAJARA 2103883664 | Equipment Failure/Involved | 2023-09-28 07:21 | 9/26 - 10/2 | 2023-09-29 00:43 | 242.0624 | FTS | 159035 | 657 | 58 | 36 | 7 | 0 | 0 | 0 | 1042
23-0122360 | Marin | PETALUMA C 1108 | PETALUMA C 1108618 | Company Initiated | 2023-09-29 05:43 | 9/26 - 10/2 | 2023-09-29 06:35 | 52 | FTS | 36972 | 711 | 32 | 24 | 10 | 3 | 0 | 1 | 52
23-0122377 | Sonoma | COTATI 1105 | COTATI 110536536 | Unknown Cause | 2023-09-29 07:20 | 9/26 - 10/2 | 2023-09-29 08:08 | 48 | FTS | 576 | 12 | 1 | 1 | 0 | 0 | 0 | 1 | 48
23-0122387 | Placer | PENRYN 1105 | PENRYN 11052406 | Animal | 2023-09-29 07:37 | 9/26 - 10/2 | 2023-09-29 08:20 | 43 | FTS | 37840 | 880 | 68 | 48 | 10 | 1 | 0 | 5 | 43
23-0122370 | Sonoma | SONOMA 1104 | SONOMA 1104914376 | Unknown Cause | 2023-09-29 06:53 | 9/26 - 10/2 | 2023-09-29 09:33 | 85.1953 | FTS | 65856 | 773 | 39 | 28 | 11 | 1 | 0 | 5 | 160
23-0122282 | Butte | WYANDOTTE 1107 | WYANDOTTE 11071026 | 3rd Party | 2023-09-28 17:35 | 9/26 - 10/2 | 2023-09-29 10:11 | 377.055 | FTS | 109723 | 291 | 26 | 22 | 3 | 0 | 0 | 2 | 996
23-0122312 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 21099372 | Unknown Cause | 2023-09-28 20:56 | 9/26 - 10/2 | 2023-09-29 10:33 | 164.3643 | FTS | 411075 | 2501 | 206 | 145 | 33 | 4 | 0 | 34 | 817
23-0122525 | Placer | BELL 1108 | BELL 1108127062 | Company Initiated | 2023-09-29 10:43 | 9/26 - 10/2 | 2023-09-29 11:45 | 45.0327 | FTS | 13780 | 306 | 23 | 16 | 3 | 0 | 0 | 1 | 62
23-0122576 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 1103N58 | Company Initiated | 2023-09-29 11:46 | 9/26 - 10/2 | 2023-09-29 11:54 | 8 | FTS | 16392 | 2049 | 145 | 111 | 37 | 1 | 0 | 5 | 8
23-0122536 | Santa Clara | EDENVALE 2105 | EDENVALE 2105CB | Animal | 2023-09-29 10:55 | 9/26 - 10/2 | 2023-09-29 13:06 | 81.1871 | FTS | 499544 | 6153 | 171 | 105 | 87 | 4 | 1 | 0 | 131
23-0122358 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102537096 | Vegetation | 2023-09-29 02:48 | 9/26 - 10/2 | 2023-09-29 13:42 | 654 | FTS | 2616 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 654
23-0122577 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-09-29 11:57 | 9/26 - 10/2 | 2023-09-29 14:03 | 126 | FTS | 6804 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 126
23-0122748 | Marin | WOODACRE 1101 | WOODACRE 1101404 | Vegetation | 2023-09-29 18:18 | 9/26 - 10/2 | 2023-09-29 20:24 | 114.1624 | FTS | 84366 | 739 | 44 | 27 | 17 | 1 | 0 | 1 | 126
23-0122776 | Plumas | BUCKS CREEK 1103 | BUCKS CREEK 1103338520 | Environmental/External | 2023-09-29 21:31 | 9/26 - 10/2 | 2023-09-29 22:28 | 57 | FTS | 17898 | 314 | 3 | 3 | 2 | 0 | 0 | 0 | 57
23-0122800 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102272950 | Environmental/External | 2023-09-29 22:49 | 9/26 - 10/2 | 2023-09-30 00:49 | 75.3643 | FTS | 97446 | 1293 | 109 | 79 | 26 | 3 | 0 | 2 | 120
23-0122804 | Tehama | GERBER SUB | N/A | Unknown Cause | 2023-09-30 00:55 | 9/26 - 10/2 | 2023-09-30 02:45 | 110 | T-EPSS | 163460 | 1486 | 103 | 77 | 24 | 3 | 0 | 0 | 110
23-0122798 | Sonoma | MONTE RIO 1112 | MONTE RIO 1112212 | Vegetation | 2023-09-29 23:02 | 9/26 - 10/2 | 2023-09-30 06:06 | 424 | FTS | 71232 | 168 | 5 | 4 | 1 | 0 | 0 | 0 | 424
23-0122845 | San Luis Obispo | PERRY 1101 | PERRY 1101618168 | Animal | 2023-09-30 07:04 | 9/26 - 10/2 | 2023-09-30 08:33 | 89 | FTS | 13439 | 151 | 8 | 6 | 1 | 0 | 0 | 0 | 89
23-0122758 | Placer | DRUM 1101 | DRUM 1101CB | Company Initiated | 2023-09-29 19:04 | 9/26 - 10/2 | 2023-09-30 08:33 | 809 | FTS | 164227 | 203 | 8 | 4 | 19 | 1 | 0 | 1 | 809
23-0122869 | Nevada | HIGGINS 1107 | HIGGINS 1107CB | Vegetation | 2023-09-30 08:21 | 9/26 - 10/2 | 2023-09-30 10:10 | 109 | FTS | 187262 | 1718 | 151 | 96 | 26 | 3 | 0 | 8 | 109
23-0122895 | Plumas | BUCKS CREEK 1103 | BUCKS CREEK 1103338520 | Unknown Cause | 2023-09-30 03:46 | 9/26 - 10/2 | 2023-09-30 10:28 | 402 | FTS | 78390 | 195 | 1 | 1 | 2 | 0 | 0 | 0 | 402
23-0122894 | Amador | CLAY 1103 | CLAY 1103CB | Animal | 2023-09-30 09:26 | 9/26 - 10/2 | 2023-09-30 11:27 | 121 | FTS | 201465 | 1665 | 114 | 83 | 43 | 0 | 0 | 1 | 121
23-0122905 | Sonoma | DUNBAR 1102 | DUNBAR 1102448 | Unknown Cause | 2023-09-30 10:12 | 9/26 - 10/2 | 2023-09-30 11:56 | 101.2951 | FTS | 61790 | 610 | 40 | 29 | 12 | 0 | 0 | 6 | 104
23-0122771 | Butte | BUTTE 1105 | BUTTE 1105612016 | Equipment Failure/Involved | 2023-09-29 20:05 | 9/26 - 10/2 | 2023-09-30 14:36 | 129.8571 | FTS | 26361 | 203 | 15 | 9 | 2 | 1 | 0 | 3 | 1111
23-0122977 | Sutter | HIGGINS 1107 | HIGGINS 11071070 | Vegetation | 2023-09-30 14:08 | 9/26 - 10/2 | 2023-09-30 15:48 | 100 | FTS | 24500 | 245 | 24 | 16 | 9 | 0 | 0 | 8 | 100
23-0122972 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311046 | Vegetation | 2023-09-30 13:41 | 9/26 - 10/2 | 2023-09-30 16:22 | 161 | FTS | 56511 | 351 | 21 | 15 | 8 | 2 | 0 | 1 | 161
23-0122969 | Marin | SAN RAFAEL 1101 | SAN RAFAEL 110139156 | Unknown Cause | 2023-09-30 13:22 | 9/26 - 10/2 | 2023-09-30 17:00 | 187.6338 | FTS | 243924 | 1300 | 30 | 18 | 53 | 21 | 0 | 2 | 218
23-0122816 | Napa | PUEBLO 1105 | PUEBLO 1105684564 | 3rd Party | 2023-09-30 02:51 | 9/26 - 10/2 | 2023-09-30 18:06 | 523.5745 | FTS | 147648 | 282 | 6 | 4 | 2 | 0 | 0 | 2 | 915
23-0123006 | Monterey | SOLEDAD 2105 | SOLEDAD 2101823854 | Unknown Cause | 2023-09-30 16:19 | 9/26 - 10/2 | 2023-09-30 18:35 | 136 | FTS | 29240 | 215 | 6 | 6 | 2 | 0 | 0 | 0 | 136
23-0122979 | Monterey | SOLEDAD 2105 | SOLEDAD 2101823854 | Equipment Failure/Involved | 2023-09-30 14:26 | 9/26 - 10/2 | 2023-09-30 20:10 | 85.1982 | FTS | 18488 | 217 | 6 | 6 | 2 | 0 | 0 | 0 | 344
23-0123027 | Tehama | RED BLUFF 1101 | RED BLUFF 11011556 | Environmental/External | 2023-09-30 18:14 | 9/26 - 10/2 | 2023-09-30 20:15 | 121 | FTS | 58080 | 480 | 56 | 38 | 3 | 0 | 0 | 0 | 121
23-0123044 | Monterey | GABILAN 1101 | GABILAN 11013034 | 3rd Party | 2023-09-30 21:37 | 9/26 - 10/2 | 2023-09-30 22:43 | 66 | FTS | 35904 | 544 | 33 | 23 | 12 | 0 | 0 | 0 | 66
23-0123037 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | Environmental/External | 2023-09-30 18:04 | 9/26 - 10/2 | 2023-10-01 02:11 | 134.1912 | FTS | 9125 | 68 | 8 | 6 | 0 | 0 | 0 | 0 | 487
23-0123062 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Animal | 2023-10-01 01:10 | 9/26 - 10/2 | 2023-10-01 04:07 | 154.5263 | FTS | 264549 | 1712 | 96 | 76 | 19 | 2 | 0 | 12 | 177
23-0123021 | Shasta | COTTONWOOD 1102 | COTTONWOOD 11029026 | Environmental/External | 2023-09-30 17:47 | 9/26 - 10/2 | 2023-10-01 09:12 | 522.2688 | FTS | 382823 | 733 | 86 | 62 | 8 | 2 | 0 | 2 | 925
23-0123018 | Shasta | PANORAMA 1102 | PANORAMA 11021632 | Environmental/External | 2023-09-30 17:36 | 9/26 - 10/2 | 2023-10-01 09:22 | 946 | FTS | 9460 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 946
23-0122821 | Butte | CLARK ROAD 1102 | CLARK ROAD 110281296 | Environmental/External | 2023-09-30 03:11 | 9/26 - 10/2 | 2023-10-01 10:46 | 988.7893 | FTS | 1276527 | 1291 | 105 | 76 | 26 | 3 | 0 | 2 | 1895
23-0123069 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101CB | Equipment Failure/Involved | 2023-10-01 05:08 | 9/26 - 10/2 | 2023-10-01 11:04 | 354.2177 | FTS | 52070 | 147 | 5 | 5 | 5 | 0 | 0 | 0 | 356
23-0123093 | Contra Costa | ROSSMOOR 1109 | ROSSMOOR 110982962 | Unknown Cause | 2023-10-01 10:36 | 9/26 - 10/2 | 2023-10-01 11:21 | 45 | FTS | 15030 | 334 | 21 | 14 | 2 | 0 | 0 | 0 | 45
23-0123071 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Unknown Cause | 2023-10-01 06:40 | 9/26 - 10/2 | 2023-10-01 11:37 | 200.4847 | FTS | 32679 | 163 | 6 | 6 | 4 | 1 | 0 | 0 | 297
23-0123043 | Mendocino | LAYTONVILLE 1102 | LAYTONVILLE 110237586 | 3rd Party | 2023-09-30 21:21 | 9/26 - 10/2 | 2023-10-01 11:45 | 864 | FTS | 110592 | 128 | 6 | 1 | 6 | 1 | 0 | 0 | 864
23-0123100 | Placer | BELL 1108 | BELL 11082202 | Unknown Cause | 2023-10-01 11:54 | 9/26 - 10/2 | 2023-10-01 15:39 | 210.4008 | FTS | 110250 | 524 | 32 | 29 | 7 | 0 | 0 | 6 | 225
23-0122918 | Tuolumne | PEORIA 1705 | PEORIA 170567898 | Equipment Failure/Involved | 2023-09-30 10:31 | 9/26 - 10/2 | 2023-10-01 16:11 | 325.8638 | FTS | 351607 | 1079 | 106 | 79 | 12 | 0 | 0 | 0 | 1780
23-0123107 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011546 | Unknown Cause | 2023-10-01 13:45 | 9/26 - 10/2 | 2023-10-01 16:30 | 165 | FTS | 17820 | 108 | 7 | 5 | 2 | 0 | 0 | 0 | 165
23-0123139 | Placer | DRUM 1101 | DRUM 1101CB | Equipment Failure/Involved | 2023-10-01 19:01 | 9/26 - 10/2 | 2023-10-01 20:05 | 64 | FTS | 12992 | 203 | 8 | 4 | 19 | 1 | 0 | 1 | 64
23-0123120 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-10-01 15:40 | 9/26 - 10/2 | 2023-10-01 21:03 | 205.8772 | FTS | 11735 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 323
23-0123185 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21037062 | Unknown Cause | 2023-10-02 06:40 | 9/26 - 10/2 | 2023-10-02 08:24 | 104 | FTS | 5200 | 50 | 1 | 1 | 1 | 0 | 0 | 0 | 104
23-0123239 | Santa Barbara | ZACA 1102 | ZACA 1102Y48 | Company Initiated | 2023-10-02 08:47 | 9/26 - 10/2 | 2023-10-02 08:55 | 8 | FTS | 6616 | 827 | 27 | 13 | 16 | 15 | 0 | 2 | 8
23-0123164 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011546 | Unknown Cause | 2023-10-01 23:39 | 9/26 - 10/2 | 2023-10-02 09:35 | 567 | FTS | 61236 | 108 | 7 | 5 | 2 | 0 | 0 | 0 | 596
23-0123296 | Shasta | ANDERSON 1101 | ANDERSON 11011390 | Animal | 2023-10-02 09:46 | 9/26 - 10/2 | 2023-10-02 10:51 | 55.3991 | FTS | 12631 | 228 | 33 | 24 | 1 | 1 | 0 | 0 | 65
23-0123189 | Yuba | NARROWS 2101 | NARROWS 21011202 | Unknown Cause | 2023-10-02 06:52 | 9/26 - 10/2 | 2023-10-02 11:07 | 255 | FTS | 127755 | 501 | 41 | 26 | 2 | 0 | 0 | 4 | 255
23-0123124 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104982992 | Unknown Cause | 2023-10-01 16:39 | 9/26 - 10/2 | 2023-10-02 11:32 | 126.2547 | FTS | 60981 | 483 | 3 | 3 | 10 | 0 | 0 | 0 | 1133
23-0123190 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Animal | 2023-10-02 06:55 | 9/26 - 10/2 | 2023-10-02 11:35 | 163.5162 | FTS | 65570 | 401 | 26 | 23 | 10 | 0 | 0 | 1 | 280
23-0123271 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 21099372 | Unknown Cause | 2023-10-02 09:30 | 9/26 - 10/2 | 2023-10-02 12:17 | 83.9736 | FTS | 210018 | 2501 | 206 | 145 | 33 | 4 | 0 | 34 | 167
23-0123370 | Amador | MARTELL 1101 | MARTELL 110191216 | Vegetation | 2023-10-02 12:30 | 9/26 - 10/2 | 2023-10-02 13:15 | 45 | FTS | 19170 | 426 | 49 | 35 | 5 | 0 | 0 | 7 | 45
23-0123409 | Shasta | DESCHUTES 1104 | DESCHUTES 1104622260 | Company Initiated | 2023-10-02 13:14 | 9/26 - 10/2 | 2023-10-02 13:20 | 6 | FTS | 744 | 124 | 8 | 5 | 1 | 0 | 0 | 0 | 6
23-0123503 | Shasta | DESCHUTES 1104 | DESCHUTES 1104622260 | Company Initiated | 2023-10-02 15:21 | 9/26 - 10/2 | 2023-10-02 15:41 | 20 | FTS | 2520 | 126 | 8 | 5 | 1 | 0 | 0 | 0 | 20
23-0123460 | Humboldt | RIO DELL 1102 | RIO DELL 110275970 | Unknown Cause | 2023-10-02 14:48 | 9/26 - 10/2 | 2023-10-02 16:57 | 128.0833 | FTS | 6148 | 48 | 0 | 0 | 10 | 0 | 0 | 0 | 129
23-0123537 | Shasta | MC ARTHUR 1101 | MC ARTHUR 110153120 | Unknown Cause | 2023-10-02 17:22 | 10/3 - 10/9 | 2023-10-02 19:11 | 109 | FTS | 14606 | 134 | 7 | 4 | 0 | 0 | 0 | 0 | 109
23-0123522 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | 3rd Party | 2023-10-02 16:25 | 10/3 - 10/9 | 2023-10-03 02:36 | 243.8515 | FTS | 507455 | 2081 | 176 | 137 | 32 | 3 | 0 | 2 | 611
23-0123722 | Madera | SAN JOAQUIN #2 1103 | SAN JOAQUIN #2 110310320 | Company Initiated | 2023-10-03 10:02 | 10/3 - 10/9 | 2023-10-03 10:21 | 19 | FTS | 1311 | 69 | 5 | 3 | 0 | 0 | 0 | 0 | 19
23-0123836 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Unknown Cause | 2023-10-03 12:25 | 10/3 - 10/9 | 2023-10-03 15:02 | 157 | FTS | 32499 | 207 | 13 | 9 | 6 | 0 | 0 | 4 | 157
23-0123877 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 1103N44 | Unknown Cause | 2023-10-03 13:35 | 10/3 - 10/9 | 2023-10-03 15:17 | 78.0656 | FTS | 92820 | 1189 | 38 | 22 | 25 | 1 | 0 | 3 | 102
23-0123912 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V46 | Unknown Cause | 2023-10-03 14:14 | 10/3 - 10/9 | 2023-10-03 16:36 | 142 | FTS | 30956 | 218 | 3 | 3 | 10 | 0 | 0 | 0 | 142
23-0123904 | Shasta | WHITMORE 1101 | WHITMORE 110145262 | Unknown Cause | 2023-10-03 14:04 | 10/3 - 10/9 | 2023-10-03 16:58 | 174 | FTS | 29406 | 169 | 13 | 6 | 1 | 0 | 0 | 0 | 174
23-0123620 | Fresno | AUBERRY 1101 | AUBERRY 1101R2845 | 3rd Party | 2023-10-03 07:22 | 10/3 - 10/9 | 2023-10-03 17:42 | 214.4484 | FTS | 180780 | 843 | 46 | 36 | 23 | 3 | 0 | 1 | 620
23-0124024 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V02 | Unknown Cause | 2023-10-03 16:36 | 10/3 - 10/9 | 2023-10-03 18:28 | 107.0025 | FTS | 215396 | 2013 | 66 | 53 | 42 | 2 | 0 | 24 | 112
23-0124030 | Napa | SILVERADO 2102 | SILVERADO 2102285782 | Animal | 2023-10-03 16:49 | 10/3 - 10/9 | 2023-10-03 18:32 | 103 | FTS | 10815 | 105 | 1 | 1 | 1 | 0 | 0 | 0 | 103
23-0124040 | Madera | COARSEGOLD 2102 | COARSEGOLD 2102383092 | 3rd Party | 2023-10-03 17:16 | 10/3 - 10/9 | 2023-10-04 02:25 | 140.1361 | FTS | 191566 | 1367 | 118 | 88 | 34 | 5 | 0 | 2 | 549
23-0124130 | Mendocino | POINT ARENA 1101 | POINT ARENA 1101476 | Animal | 2023-10-04 05:30 | 10/3 - 10/9 | 2023-10-04 07:02 | 42.25 | FTS | 10816 | 256 | 12 | 8 | 9 | 1 | 0 | 0 | 92
23-0124166 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106974130 | Unknown Cause | 2023-10-04 07:15 | 10/3 - 10/9 | 2023-10-04 08:45 | 90 | FTS | 8190 | 91 | 11 | 11 | 1 | 0 | 0 | 0 | 90
23-0124220 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 1101964556 | Unknown Cause | 2023-10-04 08:26 | 10/3 - 10/9 | 2023-10-04 11:41 | 131.2245 | FTS | 6430 | 49 | 3 | 3 | 2 | 0 | 0 | 0 | 195
23-0124357 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V02 | Company Initiated | 2023-10-04 11:42 | 10/3 - 10/9 | 2023-10-04 12:10 | 28 | FTS | 55804 | 1993 | 64 | 51 | 42 | 2 | 0 | 24 | 28
23-0124213 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | Vegetation | 2023-10-04 11:14 | 10/3 - 10/9 | 2023-10-04 13:23 | 129 | FTS | 11610 | 90 | 5 | 5 | 1 | 1 | 0 | 0 | 129
23-0124363 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111349826 | Vegetation | 2023-10-04 11:38 | 10/3 - 10/9 | 2023-10-04 13:49 | 47.4471 | FTS | 56557 | 1192 | 43 | 29 | 15 | 0 | 0 | 9 | 131
23-0124342 | Colusa | MAXWELL 1102 | MAXWELL 11023306 | Unknown Cause | 2023-10-04 11:17 | 10/3 - 10/9 | 2023-10-04 14:28 | 191 | FTS | 30560 | 160 | 4 | 2 | 2 | 0 | 0 | 0 | 191
23-0124282 | Butte | ORO FINO 1102 | ORO FINO 1102787504 | Vegetation | 2023-10-04 09:41 | 10/3 - 10/9 | 2023-10-04 16:41 | 126.6954 | FTS | 44090 | 348 | 21 | 14 | 11 | 2 | 0 | 0 | 420
23-0124460 | Yolo | MADISON 2101 | MADISON 21017702 | Unknown Cause | 2023-10-04 14:04 | 10/3 - 10/9 | 2023-10-04 17:48 | 220.322 | FTS | 206662 | 938 | 29 | 17 | 18 | 14 | 0 | 2 | 224
23-0124565 | Santa Barbara | BUELLTON 1102 | BUELLTON 1102CB | Unknown Cause | 2023-10-04 15:48 | 10/3 - 10/9 | 2023-10-04 18:25 | 157 | FTS | 319181 | 2033 | 40 | 35 | 32 | 7 | 0 | 0 | 157
23-0124567 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR268 | Equipment Failure/Involved | 2023-10-04 15:51 | 10/3 - 10/9 | 2023-10-04 18:42 | 171 | FTS | 11286 | 66 | 4 | 3 | 0 | 0 | 0 | 0 | 171
23-0124610 | Alameda | SAN RAMON 2107 | SAN RAMON 2107824562 | Company Initiated | 2023-10-04 17:01 | 10/3 - 10/9 | 2023-10-04 18:52 | 111 | FTS | 92019 | 829 | 44 | 28 | 15 | 3 | 0 | 0 | 111
23-0124646 | Sonoma | MIRABEL 1101 | MIRABEL 1101298 | Equipment Failure/Involved | 2023-10-04 19:24 | 10/3 - 10/9 | 2023-10-04 20:38 | 74 | FTS | 16872 | 228 | 11 | 10 | 2 | 0 | 0 | 0 | 74
23-0124595 | Napa | PUEBLO 2103 | PUEBLO 210378504 | Unknown Cause | 2023-10-04 16:37 | 10/3 - 10/9 | 2023-10-04 20:49 | 143.1471 | FTS | 19468 | 136 | 11 | 7 | 1 | 0 | 0 | 4 | 252
23-0124640 | Nevada | NARROWS 2102 | NARROWS 210248484 | Unknown Cause | 2023-10-04 18:59 | 10/3 - 10/9 | 2023-10-04 21:36 | 155.7696 | FTS | 139258 | 894 | 56 | 35 | 19 | 6 | 0 | 12 | 157
23-0124421 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | 3rd Party | 2023-10-04 13:10 | 10/3 - 10/9 | 2023-10-04 23:41 | 186.6711 | FTS | 153817 | 824 | 45 | 28 | 28 | 2 | 0 | 2 | 631
23-0124696 | Marin | ALTO 1125 | ALTO 1125296476 | Unknown Cause | 2023-10-05 03:32 | 10/3 - 10/9 | 2023-10-05 04:28 | 56 | FTS | 6664 | 119 | 10 | 10 | 1 | 0 | 0 | 0 | 56
23-0124715 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108233646 | Unknown Cause | 2023-10-05 06:51 | 10/3 - 10/9 | 2023-10-05 08:09 | 78 | FTS | 21060 | 270 | 8 | 8 | 4 | 0 | 0 | 3 | 78
23-0124769 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V46 | Company Initiated | 2023-10-05 08:48 | 10/3 - 10/9 | 2023-10-05 09:04 | 16 | FTS | 3488 | 218 | 3 | 3 | 10 | 0 | 0 | 0 | 16
23-0124690 | Yolo | MADISON 2101 | MADISON 21017702 | Unknown Cause | 2023-10-05 00:52 | 10/3 - 10/9 | 2023-10-05 09:09 | 90.0235 | FTS | 84352 | 937 | 29 | 17 | 18 | 14 | 0 | 2 | 497
23-0124716 | Marin | COTATI 1103 | COTATI 110361736 | Unknown Cause | 2023-10-05 06:58 | 10/3 - 10/9 | 2023-10-05 10:34 | 118.341 | FTS | 102720 | 868 | 30 | 22 | 30 | 7 | 0 | 0 | 216
23-0124693 | Napa | PUEBLO 2103 | PUEBLO 210378504 | Unknown Cause | 2023-10-05 01:52 | 10/3 - 10/9 | 2023-10-05 10:51 | 484.0368 | FTS | 65829 | 136 | 11 | 7 | 1 | 0 | 0 | 4 | 539
23-0124816 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113587564 | Unknown Cause | 2023-10-05 10:16 | 10/3 - 10/9 | 2023-10-05 11:40 | 84 | FTS | 1764 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 84
23-0124906 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101135762 | Animal | 2023-10-05 12:21 | 10/3 - 10/9 | 2023-10-05 12:57 | 36 | FTS | 1332 | 37 | 1 | 1 | 0 | 0 | 0 | 0 | 36
23-0124856 | Marin | BOLINAS 1101 | BOLINAS 11011064 | Unknown Cause | 2023-10-05 11:09 | 10/3 - 10/9 | 2023-10-05 13:43 | 147.0737 | FTS | 41916 | 285 | 3 | 2 | 6 | 2 | 0 | 0 | 154
23-0124697 | Mendocino | WILLITS 1103 | WILLITS 110391948 | 3rd Party | 2023-10-05 02:47 | 10/3 - 10/9 | 2023-10-05 13:49 | 196.3248 | FTS | 22970 | 117 | 7 | 6 | 2 | 0 | 0 | 0 | 662
23-0124988 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110N30 | Company Initiated | 2023-10-05 14:20 | 10/3 - 10/9 | 2023-10-05 14:38 | 18 | FTS | 8118 | 451 | 25 | 16 | 7 | 0 | 0 | 1 | 18
23-0124865 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207P148 | Equipment Failure/Involved | 2023-10-05 11:19 | 10/3 - 10/9 | 2023-10-05 15:38 | 135.7188 | FTS | 98939 | 729 | 40 | 28 | 7 | 2 | 0 | 0 | 259
23-0125082 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | 3rd Party | 2023-10-05 16:57 | 10/3 - 10/9 | 2023-10-05 19:02 | 42.2285 | FTS | 79094 | 1873 | 146 | 105 | 19 | 1 | 0 | 4 | 125
23-0124903 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 1101CB | 3rd Party | 2023-10-05 10:33 | 10/3 - 10/9 | 2023-10-05 19:30 | 204.973 | FTS | 7584 | 37 | 1 | 1 | 1 | 1 | 0 | 0 | 537
23-0125101 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-10-05 19:39 | 10/3 - 10/9 | 2023-10-05 19:57 | 18 | FTS | 324 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 18
23-0125136 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | 3rd Party | 2023-10-05 22:28 | 10/3 - 10/9 | 2023-10-05 23:28 | 60 | FTS | 24000 | 400 | 19 | 8 | 4 | 0 | 0 | 0 | 60
23-0125095 | Shasta | JESSUP 1101 | JESSUP 110168362 | Unknown Cause | 2023-10-05 18:09 | 10/3 - 10/9 | 2023-10-06 00:08 | 310.9254 | FTS | 479447 | 1542 | 182 | 140 | 17 | 4 | 0 | 0 | 359
23-0125143 | Monterey | BORONDA SUB | N/A | Unknown Cause | 2023-10-05 23:47 | 10/3 - 10/9 | 2023-10-06 03:02 | 152.1857 | T-EPSS | 136054 | 894 | 47 | 37 | 18 | 5 | 0 | 0 | 195
23-0125153 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102347280 | 3rd Party | 2023-10-06 04:14 | 10/3 - 10/9 | 2023-10-06 05:06 | 52 | FTS | 5200 | 100 | 4 | 3 | 1 | 0 | 0 | 2 | 52
23-0125147 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | 3rd Party | 2023-10-06 00:37 | 10/3 - 10/9 | 2023-10-06 06:52 | 99.3678 | FTS | 693885 | 6983 | 286 | 226 | 101 | 5 | 2 | 0 | 375
23-0125174 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Unknown Cause | 2023-10-06 06:57 | 10/3 - 10/9 | 2023-10-06 08:08 | 71 | FTS | 12070 | 170 | 12 | 7 | 13 | 0 | 0 | 1 | 71
23-0125403 | San Luis Obispo | SAN MIGUEL 1105 | SAN MIGUEL 1105CB | Unknown Cause | 2023-10-06 11:30 | 10/3 - 10/9 | 2023-10-06 12:22 | 52 | FTS | 884 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 52
23-0125417 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 21035404 | Vegetation | 2023-10-06 11:35 | 10/3 - 10/9 | 2023-10-06 13:16 | 85.723 | FTS | 63435 | 740 | 47 | 41 | 17 | 0 | 0 | 0 | 101
23-0125382 | Calaveras | CORRAL 1101 | CORRAL 110112606 | Animal | 2023-10-06 11:08 | 10/3 - 10/9 | 2023-10-06 13:20 | 132 | FTS | 44088 | 334 | 26 | 17 | 7 | 0 | 0 | 0 | 132
23-0125427 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | Unknown Cause | 2023-10-06 11:52 | 10/3 - 10/9 | 2023-10-06 16:29 | 201.5579 | FTS | 170518 | 846 | 55 | 36 | 16 | 2 | 0 | 3 | 277
23-0125623 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108618 | Unknown Cause | 2023-10-06 18:17 | 10/3 - 10/9 | 2023-10-06 19:29 | 37.1461 | FTS | 26448 | 712 | 33 | 25 | 10 | 3 | 0 | 1 | 72
23-0125630 | Placer | PENRYN 1105 | PENRYN 11052406 | Animal | 2023-10-06 19:07 | 10/3 - 10/9 | 2023-10-06 22:25 | 90.7952 | FTS | 97968 | 1079 | 67 | 47 | 10 | 1 | 0 | 5 | 198
23-0125664 | Monterey | JOLON 1102 | JOLON 1102CB | Animal | 2023-10-07 01:51 | 10/3 - 10/9 | 2023-10-07 03:16 | 85 | FTS | 51510 | 606 | 22 | 16 | 24 | 2 | 0 | 7 | 85
23-0125665 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062392 | Unknown Cause | 2023-10-07 02:28 | 10/3 - 10/9 | 2023-10-07 05:48 | 91.4229 | FTS | 50374 | 551 | 37 | 28 | 9 | 2 | 0 | 2 | 200
23-0125673 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651484 | Company Initiated | 2023-10-07 04:39 | 10/3 - 10/9 | 2023-10-07 07:29 | 170 | FTS | 3570 | 21 | 1 | 1 | 0 | 0 | 0 | 0 | 170
23-0125640 | Yuba | BROWNS VALLEY 1101 | BROWNS VALLEY 110193870 | Animal | 2023-10-06 19:52 | 10/3 - 10/9 | 2023-10-07 08:24 | 593.2419 | FTS | 311452 | 525 | 46 | 29 | 5 | 1 | 0 | 8 | 752
23-0125676 | Santa Clara | HICKS 2101 | HICKS 2101XR250 | Animal | 2023-10-07 07:19 | 10/3 - 10/9 | 2023-10-07 08:57 | 98 | FTS | 309582 | 3159 | 199 | 139 | 47 | 9 | 0 | 0 | 98
23-0125694 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Animal | 2023-10-07 08:41 | 10/3 - 10/9 | 2023-10-07 09:11 | 19.0634 | FTS | 33056 | 1734 | 128 | 80 | 29 | 7 | 0 | 4 | 30
23-0125668 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Equipment Failure/Involved | 2023-10-07 04:39 | 10/3 - 10/9 | 2023-10-07 09:12 | 214.2841 | FTS | 133499 | 623 | 73 | 53 | 7 | 0 | 0 | 1 | 273
23-0125675 | Tulare | OROSI 1102 | OROSI 1102CB | Unknown Cause | 2023-10-07 07:13 | 10/3 - 10/9 | 2023-10-07 09:29 | 91.5756 | FTS | 34524 | 377 | 6 | 5 | 1 | 0 | 0 | 0 | 136
23-0125671 | Lake | UPPER LAKE 1101 | UPPER LAKE 110142378 | Unknown Cause | 2023-10-07 05:50 | 10/3 - 10/9 | 2023-10-07 10:14 | 89.5974 | FTS | 62091 | 693 | 42 | 29 | 11 | 5 | 0 | 1 | 264
23-0125667 | Amador | CLAY 1101 | CLAY 110113442 | Unknown Cause | 2023-10-07 03:13 | 10/3 - 10/9 | 2023-10-07 12:39 | 278.0175 | FTS | 222970 | 802 | 65 | 44 | 8 | 0 | 0 | 4 | 566
23-0125761 | Shasta | ANTLER 1101 | ANTLER 1101718316 | Company Initiated | 2023-10-07 14:23 | 10/3 - 10/9 | 2023-10-07 14:31 | 8 | FTS | 80 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 8
23-0125726 | Santa Clara | STELLING 1109 | STELLING 110913228 | Vegetation | 2023-10-07 11:54 | 10/3 - 10/9 | 2023-10-07 15:18 | 129.5515 | FTS | 184870 | 1427 | 51 | 31 | 17 | 3 | 0 | 0 | 204
23-0125730 | Napa | SILVERADO 2105 | SILVERADO 2105768606 | Unknown Cause | 2023-10-07 12:36 | 10/3 - 10/9 | 2023-10-07 17:05 | 105.2614 | FTS | 9263 | 88 | 2 | 1 | 2 | 0 | 0 | 0 | 269
23-0125732 | Humboldt | FRUITLAND 1142 | FRUITLAND 1141866852 | Vegetation | 2023-10-07 12:42 | 10/3 - 10/9 | 2023-10-07 19:37 | 237 | FTS | 4977 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 415
23-0125837 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Unknown Cause | 2023-10-08 06:53 | 10/3 - 10/9 | 2023-10-08 08:12 | 79 | FTS | 13430 | 170 | 12 | 7 | 13 | 0 | 0 | 1 | 79
23-0125844 | Tehama | COTTONWOOD 1103 | COTTONWOOD 1103957942 | Unknown Cause | 2023-10-08 08:27 | 10/3 - 10/9 | 2023-10-08 09:37 | 70 | FTS | 7560 | 108 | 7 | 4 | 1 | 0 | 0 | 0 | 70
23-0125836 | Napa | MONTICELLO 1101 | MONTICELLO 110165454 | Unknown Cause | 2023-10-08 06:52 | 10/3 - 10/9 | 2023-10-08 10:43 | 231 | FTS | 30723 | 133 | 8 | 5 | 1 | 0 | 0 | 0 | 231
23-0125855 | Placer | LINCOLN 1104 | LINCOLN 1104818790 | Animal | 2023-10-08 08:56 | 10/3 - 10/9 | 2023-10-08 11:43 | 143.8889 | FTS | 7770 | 54 | 4 | 3 | 0 | 0 | 0 | 1 | 167
23-0125838 | Placer | WISE 1102 | WISE 11022230 | Unknown Cause | 2023-10-08 06:58 | 10/3 - 10/9 | 2023-10-08 14:42 | 102.2517 | FTS | 88959 | 870 | 75 | 58 | 4 | 0 | 0 | 13 | 464
23-0125866 | Amador | CLAY 1101 | CLAY 110113442 | Unknown Cause | 2023-10-08 12:51 | 10/3 - 10/9 | 2023-10-08 15:50 | 114.2494 | FTS | 91628 | 802 | 65 | 44 | 8 | 0 | 0 | 4 | 179
23-0125830 | Shasta | DESCHUTES 1101 | DESCHUTES 11011380 | Equipment Failure/Involved | 2023-10-08 01:45 | 10/3 - 10/9 | 2023-10-08 17:16 | 175.1075 | FTS | 359846 | 2055 | 198 | 154 | 28 | 1 | 0 | 2 | 931
23-0125884 | Contra Costa | TIDEWATER 2106 | TIDEWATER 210657926 | Animal | 2023-10-08 20:48 | 10/3 - 10/9 | 2023-10-09 01:22 | 247.1164 | FTS | 154942 | 627 | 31 | 21 | 49 | 1 | 0 | 0 | 274
23-0125923 | Lake | UPPER LAKE 1101 | UPPER LAKE 110142378 | Animal | 2023-10-09 07:05 | 10/3 - 10/9 | 2023-10-09 08:51 | 73.5065 | FTS | 50940 | 693 | 42 | 29 | 11 | 5 | 0 | 1 | 106
23-0125921 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108233646 | Unknown Cause | 2023-10-09 07:04 | 10/3 - 10/9 | 2023-10-09 09:00 | 116 | FTS | 31320 | 270 | 8 | 8 | 4 | 0 | 0 | 3 | 116
23-0125917 | Alameda | CAYETANO 2109 | CAYETANO 2109MR186 | Unknown Cause | 2023-10-09 06:54 | 10/3 - 10/9 | 2023-10-09 09:00 | 126 | FTS | 1512 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 126
23-0125918 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210533542 | Vegetation | 2023-10-09 06:56 | 10/3 - 10/9 | 2023-10-09 09:52 | 151.09 | FTS | 60436 | 400 | 42 | 30 | 8 | 0 | 0 | 0 | 176
23-0125931 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410960 | Unknown Cause | 2023-10-09 07:20 | 10/3 - 10/9 | 2023-10-09 09:53 | 153 | FTS | 366129 | 2393 | 184 | 153 | 34 | 6 | 0 | 2 | 153
23-0125951 | Tuolumne | RACETRACK 1703 | RACETRACK 170311270 | Unknown Cause | 2023-10-09 08:22 | 10/3 - 10/9 | 2023-10-09 11:04 | 160.4967 | FTS | 72384 | 451 | 43 | 30 | 8 | 0 | 0 | 0 | 162
23-0125841 | Napa | PUEBLO 2103 | PUEBLO 21031970 | Equipment Failure/Involved | 2023-10-08 08:12 | 10/3 - 10/9 | 2023-10-09 11:30 | 157.2064 | FTS | 246028 | 1565 | 113 | 86 | 16 | 1 | 0 | 0 | 1638
23-0125876 | San Luis Obispo | CAYUCOS 1101 | CAYUCOS 1101W58 | Unknown Cause | 2023-10-08 18:58 | 10/3 - 10/9 | 2023-10-09 12:16 | 231.4182 | FTS | 76368 | 330 | 5 | 5 | 7 | 0 | 0 | 0 | 1038
23-0125973 | Butte | OROVILLE 1104 | OROVILLE 11042588 | Unknown Cause | 2023-10-09 09:05 | 10/3 - 10/9 | 2023-10-09 13:05 | 161.9203 | FTS | 268140 | 1656 | 179 | 126 | 19 | 5 | 1 | 0 | 240
23-0125880 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-10-08 20:20 | 10/3 - 10/9 | 2023-10-09 14:19 | 978.6316 | FTS | 55782 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 1079
23-0125873 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Company Initiated | 2023-10-08 17:57 | 10/3 - 10/9 | 2023-10-09 15:06 | 600.0847 | FTS | 2210712 | 3684 | 43 | 23 | 23 | 9 | 0 | 0 | 1269
23-0126102 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103CB | Unknown Cause | 2023-10-09 12:32 | 10/3 - 10/9 | 2023-10-09 15:26 | 102.7824 | FTS | 174319 | 1696 | 56 | 46 | 19 | 1 | 0 | 1 | 174
23-0126131 | Santa Barbara | PURISIMA 1101 | PURISIMA 1101Y44 | Animal | 2023-10-09 13:23 | 10/3 - 10/9 | 2023-10-09 16:03 | 119.2957 | FTS | 22189 | 186 | 1 | 1 | 14 | 0 | 0 | 0 | 160
23-0126087 | Humboldt | ARCATA 1122 | ARCATA 11225384 | Vegetation | 2023-10-09 12:01 | 10/3 - 10/9 | 2023-10-09 16:15 | 71.5983 | FTS | 25489 | 356 | 21 | 18 | 2 | 1 | 0 | 5 | 254
23-0126164 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21011346 | Unknown Cause | 2023-10-09 14:35 | 10/3 - 10/9 | 2023-10-09 16:41 | 87.6498 | FTS | 140152 | 1599 | 141 | 92 | 24 | 0 | 0 | 1 | 126
23-0126153 | Shasta | RISING RIVER 1101 | RISING RIVER 11011530 | Vegetation | 2023-10-09 14:08 | 10/3 - 10/9 | 2023-10-09 16:54 | 112.5806 | FTS | 59330 | 527 | 28 | 25 | 11 | 0 | 0 | 0 | 166
23-0126230 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Unknown Cause | 2023-10-09 17:11 | 10/10 - 10/16 | 2023-10-09 18:25 | 40.3375 | FTS | 74342 | 1843 | 132 | 99 | 26 | 5 | 0 | 2 | 74
23-0126154 | Fresno | AUBERRY 1101 | AUBERRY 1101R314 | Unknown Cause | 2023-10-09 14:09 | 10/10 - 10/16 | 2023-10-09 18:30 | 261 | FTS | 104400 | 400 | 43 | 30 | 4 | 0 | 0 | 5 | 261
23-0126123 | Santa Barbara | SISQUOC 1103 | SISQUOC 1103M98 | Equipment Failure/Involved | 2023-10-09 10:21 | 10/10 - 10/16 | 2023-10-09 19:21 | 540 | FTS | 18900 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 540
23-0126257 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11021510 | Unknown Cause | 2023-10-09 18:19 | 10/10 - 10/16 | 2023-10-09 21:50 | 211 | FTS | 176185 | 835 | 18 | 14 | 29 | 6 | 0 | 0 | 211
23-0126235 | Humboldt | HOOPA 1101 | HOOPA 110182542 | Vegetation | 2023-10-09 17:14 | 10/10 - 10/16 | 2023-10-10 01:39 | 71.7405 | FTS | 150368 | 2096 | 101 | 73 | 61 | 17 | 1 | 0 | 505
23-0126242 | Contra Costa | CAMP EVERS 2104 | CAMP EVERS 210411048 | Vegetation | 2023-10-09 17:39 | 10/10 - 10/16 | 2023-10-10 07:26 | 187.7126 | FTS | 140409 | 748 | 40 | 37 | 6 | 0 | 0 | 3 | 827
23-0126322 | Santa Barbara | PURISIMA 1101 | PURISIMA 1101Y44 | Unknown Cause | 2023-10-10 04:19 | 10/10 - 10/16 | 2023-10-10 08:15 | 236 | FTS | 43660 | 185 | 1 | 1 | 14 | 0 | 0 | 0 | 236
23-0126264 | Santa Barbara | PURISIMA 1101 | PURISIMA 1101Y44 | Equipment Failure/Involved | 2023-10-09 19:15 | 10/10 - 10/16 | 2023-10-10 08:16 | 124.5376 | FTS | 23164 | 186 | 1 | 1 | 14 | 0 | 0 | 0 | 781
23-0126240 | Mendocino | FORT BRAGG A 1102 | FORT BRAGG A 110231304 | Unknown Cause | 2023-10-09 17:18 | 10/10 - 10/16 | 2023-10-10 08:17 | 178.3333 | FTS | 25680 | 144 | 7 | 6 | 8 | 0 | 0 | 0 | 899
23-0126365 | Mendocino | UKIAH 1113 | UKIAH 1113CB | Unknown Cause | 2023-10-10 07:36 | 10/10 - 10/16 | 2023-10-10 08:18 | 42 | FTS | 50778 | 1209 | 62 | 36 | 26 | 3 | 0 | 0 | 42
23-0126366 | Mendocino | UKIAH 1114 | UKIAH 1114822 | Unknown Cause | 2023-10-10 07:38 | 10/10 - 10/16 | 2023-10-10 08:57 | 79 | FTS | 60830 | 770 | 47 | 28 | 11 | 1 | 0 | 0 | 79
23-0126410 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 1103351084 | Animal | 2023-10-10 08:51 | 10/10 - 10/16 | 2023-10-10 09:56 | 57.5183 | FTS | 20419 | 355 | 16 | 12 | 4 | 0 | 0 | 0 | 65
23-0126450 | Mendocino | FORT BRAGG A 1102 | FORT BRAGG A 1102265870 | Unknown Cause | 2023-10-10 09:50 | 10/10 - 10/16 | 2023-10-10 10:30 | 40 | FTS | 200 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 40
23-0126367 | Mendocino | UKIAH 1115 | UKIAH 11151216 | Unknown Cause | 2023-10-10 07:37 | 10/10 - 10/16 | 2023-10-10 11:13 | 188.8173 | FTS | 279072 | 1478 | 72 | 50 | 26 | 1 | 2 | 0 | 216
23-0126525 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Company Initiated | 2023-10-10 12:11 | 10/10 - 10/16 | 2023-10-10 12:18 | 6.3004 | FTS | 10591 | 1681 | 123 | 77 | 28 | 7 | 0 | 4 | 7
23-0126316 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-10-10 01:21 | 10/10 - 10/16 | 2023-10-10 12:35 | 538.2281 | FTS | 30679 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 674
23-0126561 | Sonoma | SONOMA 1105 | SONOMA 1105229588 | Company Initiated | 2023-10-10 12:46 | 10/10 - 10/16 | 2023-10-10 13:11 | 23.4801 | FTS | 15943 | 679 | 32 | 22 | 7 | 0 | 0 | 6 | 25
23-0126694 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 1101740076 | Animal | 2023-10-10 15:38 | 10/10 - 10/16 | 2023-10-10 16:53 | 75 | FTS | 13950 | 186 | 21 | 12 | 2 | 0 | 0 | 0 | 75
23-0126693 | Marin | STAFFORD 1102 | STAFFORD 1102524 | Equipment Failure/Involved | 2023-10-10 15:27 | 10/10 - 10/16 | 2023-10-10 20:17 | 288.2959 | FTS | 454066 | 1575 | 100 | 60 | 13 | 1 | 0 | 0 | 290
23-0126766 | Napa | SILVERADO 2104 | SILVERADO 2104722 | Unknown Cause | 2023-10-10 19:42 | 10/10 - 10/16 | 2023-10-10 21:49 | 127 | FTS | 66421 | 523 | 37 | 28 | 17 | 2 | 2 | 2 | 127
23-0126627 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107869946 | 3rd Party | 2023-10-10 14:06 | 10/10 - 10/16 | 2023-10-10 22:07 | 90.1289 | FTS | 25867 | 287 | 37 | 28 | 3 | 0 | 0 | 0 | 481
23-0126506 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103CB | Equipment Failure/Involved | 2023-10-10 11:38 | 10/10 - 10/16 | 2023-10-10 22:26 | 242.0945 | FTS | 66576 | 275 | 56 | 46 | 19 | 1 | 0 | 1 | 648
23-0126857 | Amador | ELECTRA 1101 | ELECTRA 11011238 | Unknown Cause | 2023-10-11 07:40 | 10/10 - 10/16 | 2023-10-11 08:51 | 71 | FTS | 39050 | 550 | 34 | 25 | 5 | 1 | 2 | 0 | 71
23-0126854 | Monterey | OTTER 1101 | OTTER 1101440 | Vegetation | 2023-10-11 07:26 | 10/10 - 10/16 | 2023-10-11 09:02 | 75.1058 | FTS | 28390 | 378 | 13 | 9 | 5 | 1 | 0 | 0 | 96
23-0126809 | Humboldt | FORT SEWARD 1121 | FORT SEWARD 1121CB | Vegetation | 2023-10-11 02:46 | 10/10 - 10/16 | 2023-10-11 10:04 | 292.8504 | FTS | 68527 | 234 | 13 | 9 | 11 | 4 | 0 | 0 | 438
23-0126905 | Madera | SAN JOAQUIN #3 1101 | SAN JOAQUIN #3 1101CB | Company Initiated | 2023-10-11 09:05 | 10/10 - 10/16 | 2023-10-11 10:15 | 69.4744 | FTS | 48771 | 702 | 44 | 34 | 22 | 0 | 0 | 1 | 70
23-0126934 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 11021382 | Unknown Cause | 2023-10-11 10:10 | 10/10 - 10/16 | 2023-10-11 11:23 | 65.2172 | FTS | 15913 | 244 | 23 | 20 | 1 | 0 | 0 | 0 | 73
23-0127061 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Company Initiated | 2023-10-11 13:06 | 10/10 - 10/16 | 2023-10-11 13:48 | 42 | FTS | 37590 | 895 | 66 | 45 | 16 | 0 | 0 | 0 | 42
23-0127064 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Company Initiated | 2023-10-11 13:06 | 10/10 - 10/16 | 2023-10-11 14:05 | 32.4248 | FTS | 153888 | 4746 | 148 | 112 | 67 | 5 | 2 | 0 | 59
23-0127042 | Butte | WYANDOTTE 1107 | WYANDOTTE 110777578 | Unknown Cause | 2023-10-11 12:38 | 10/10 - 10/16 | 2023-10-11 14:19 | 77.8471 | FTS | 119651 | 1537 | 173 | 126 | 23 | 2 | 0 | 3 | 101
23-0127122 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121612266 | Company Initiated | 2023-10-11 14:16 | 10/10 - 10/16 | 2023-10-11 14:31 | 15 | FTS | 435 | 29 | 1 | 1 | 1 | 0 | 0 | 0 | 15
23-0127113 | Amador | SALT SPRINGS 2101 | SALT SPRINGS 210110416 | Company Initiated | 2023-10-11 13:05 | 10/10 - 10/16 | 2023-10-11 14:51 | 106 | FTS | 6042 | 57 | 1 | 0 | 3 | 0 | 0 | 0 | 106
23-0127092 | Fresno | AUBERRY 1101 | AUBERRY 110137536 | Company Initiated | 2023-10-11 13:34 | 10/10 - 10/16 | 2023-10-11 15:01 | 87 | FTS | 53853 | 619 | 29 | 23 | 19 | 3 | 0 | 1 | 87
23-0126994 | Amador | CLAY 1103 | CLAY 11037124 | Unknown Cause | 2023-10-11 11:31 | 10/10 - 10/16 | 2023-10-11 15:05 | 214 | FTS | 234330 | 1095 | 93 | 68 | 25 | 0 | 0 | 1 | 214
23-0126881 | Amador | CLAY 1101 | CLAY 110113442 | 3rd Party | 2023-10-11 08:19 | 10/10 - 10/16 | 2023-10-11 15:13 | 139.7406 | FTS | 112072 | 802 | 65 | 44 | 8 | 0 | 0 | 4 | 414
23-0127109 | Santa Cruz | SEACLIFF 0401 | SEACLIFF 040112946 | Unknown Cause | 2023-10-11 14:13 | 10/10 - 10/16 | 2023-10-11 15:35 | 82 | FTS | 17466 | 213 | 20 | 16 | 5 | 0 | 0 | 0 | 82
23-0126808 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2023-10-11 01:25 | 10/10 - 10/16 | 2023-10-11 15:40 | 696.2632 | FTS | 39687 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 855
23-0127197 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111236 | Company Initiated | 2023-10-11 15:52 | 10/10 - 10/16 | 2023-10-11 15:59 | 7 | FTS | 637 | 91 | 4 | 3 | 6 | 0 | 0 | 0 | 7
23-0127177 | Amador | CLAY 1101 | CLAY 110113442 | 3rd Party | 2023-10-11 15:31 | 10/10 - 10/16 | 2023-10-11 16:50 | 79 | FTS | 63279 | 801 | 65 | 44 | 7 | 0 | 0 | 4 | 79
23-0127031 | Mendocino | GUALALA 1112 | GUALALA 111135562 | Equipment Failure/Involved | 2023-10-11 12:21 | 10/10 - 10/16 | 2023-10-11 17:38 | 45.7518 | FTS | 18621 | 407 | 24 | 16 | 8 | 0 | 0 | 0 | 317
23-0127239 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212124 | Unknown Cause | 2023-10-11 18:40 | 10/10 - 10/16 | 2023-10-11 19:47 | 30.2729 | FTS | 14531 | 480 | 31 | 24 | 4 | 0 | 0 | 0 | 67
23-0127123 | Santa Cruz | CAMP EVERS 2104 | CAMP EVERS 210411048 | Equipment Failure/Involved | 2023-10-11 14:29 | 10/10 - 10/16 | 2023-10-11 20:24 | 100.2126 | FTS | 74959 | 748 | 40 | 37 | 6 | 0 | 0 | 3 | 355
23-0127256 | Calaveras | PEORIA 1704 | PEORIA 170459596 | Unknown Cause | 2023-10-11 19:46 | 10/10 - 10/16 | 2023-10-11 23:34 | 228 | FTS | 149796 | 657 | 60 | 48 | 23 | 0 | 0 | 1 | 228
23-0127156 | Monterey | PRUNEDALE 1110 | PRUNEDALE 1110557716 | Vegetation | 2023-10-11 15:09 | 10/10 - 10/16 | 2023-10-12 03:08 | 183.5856 | FTS | 61134 | 333 | 19 | 17 | 5 | 0 | 0 | 0 | 719
23-0127408 | Amador | OLETA 1101 | OLETA 1101296804 | Company Initiated | 2023-10-12 08:26 | 10/10 - 10/16 | 2023-10-12 10:05 | 99 | FTS | 105930 | 1070 | 60 | 41 | 22 | 4 | 0 | 1 | 99
23-0127440 | Fresno | SAND CREEK 1103 | SAND CREEK 11037140 | Unknown Cause | 2023-10-12 08:43 | 10/10 - 10/16 | 2023-10-12 12:20 | 213.4989 | FTS | 97142 | 455 | 56 | 33 | 3 | 0 | 0 | 0 | 217
23-0127509 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR586 | Company Initiated | 2023-10-12 11:17 | 10/10 - 10/16 | 2023-10-12 12:28 | 71 | FTS | 3053 | 43 | 1 | 1 | 2 | 0 | 0 | 1 | 71
23-0127528 | Mendocino | UKIAH 1114 | UKIAH 1114408 | Equipment Failure/Involved | 2023-10-12 12:15 | 10/10 - 10/16 | 2023-10-12 14:07 | 64.3528 | FTS | 49616 | 771 | 47 | 28 | 11 | 1 | 0 | 0 | 112
23-0127620 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651484 | Company Initiated | 2023-10-12 13:54 | 10/10 - 10/16 | 2023-10-12 15:17 | 83 | FTS | 498 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 83
23-0127521 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113202 | Vegetation | 2023-10-12 12:02 | 10/10 - 10/16 | 2023-10-12 16:45 | 97.8348 | FTS | 11251 | 115 | 12 | 8 | 1 | 0 | 0 | 0 | 283
23-0127589 | Marin | ALTO 1124 | ALTO 1124870444 | 3rd Party | 2023-10-12 13:41 | 10/10 - 10/16 | 2023-10-12 17:18 | 139.0141 | FTS | 29610 | 213 | 7 | 2 | 2 | 0 | 0 | 0 | 217
23-0127609 | Santa Clara | SARATOGA 1103 | SARATOGA 1103LC16 | Vegetation | 2023-10-12 14:09 | 10/10 - 10/16 | 2023-10-12 17:53 | 151.9032 | FTS | 100408 | 661 | 20 | 11 | 4 | 0 | 0 | 0 | 224
23-0127616 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104CB | Equipment Failure/Involved | 2023-10-12 14:31 | 10/10 - 10/16 | 2023-10-12 18:50 | 205.787 | FTS | 469606 | 2282 | 75 | 58 | 42 | 3 | 0 | 1 | 259
23-0127898 | Santa Clara | PIERCY 2110 | PIERCY 2110XR258 | Company Initiated | 2023-10-13 09:01 | 10/10 - 10/16 | 2023-10-13 09:19 | 15.4203 | FTS | 10640 | 690 | 32 | 20 | 12 | 0 | 0 | 0 | 18
23-0127833 | San Benito | HOLLISTER 2102 | HOLLISTER 2102855412 | Unknown Cause | 2023-10-13 07:22 | 10/10 - 10/16 | 2023-10-13 11:42 | 180.835 | FTS | 18626 | 103 | 0 | 0 | 16 | 0 | 0 | 0 | 260
23-0128027 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Company Initiated | 2023-10-13 11:46 | 10/10 - 10/16 | 2023-10-13 12:06 | 19.3167 | FTS | 7746 | 401 | 26 | 23 | 10 | 0 | 0 | 1 | 20
23-0128091 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 211051800 | 3rd Party | 2023-10-13 13:22 | 10/10 - 10/16 | 2023-10-13 16:46 | 156.2149 | FTS | 157777 | 1010 | 96 | 65 | 12 | 7 | 0 | 9 | 204
23-0128159 | Kern | KERN OIL 1106 | KERN OIL 110646960 | Unknown Cause | 2023-10-13 14:53 | 10/10 - 10/16 | 2023-10-13 17:07 | 134 | FTS | 1072 | 8 | 0 | 0 | 4 | 0 | 0 | 0 | 134
23-0128238 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 210612828 | Vegetation | 2023-10-13 21:55 | 10/10 - 10/16 | 2023-10-13 23:40 | 105 | FTS | 66990 | 638 | 38 | 30 | 10 | 2 | 0 | 0 | 105
23-0128245 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410960 | Unknown Cause | 2023-10-14 03:00 | 10/10 - 10/16 | 2023-10-14 08:15 | 140.2194 | FTS | 335545 | 2393 | 184 | 153 | 34 | 6 | 0 | 2 | 315
23-0128252 | Tuolumne | CURTIS 1705 | CURTIS 170565908 | Animal | 2023-10-14 07:20 | 10/10 - 10/16 | 2023-10-14 08:44 | 84 | FTS | 57708 | 687 | 69 | 45 | 7 | 5 | 0 | 0 | 84
23-0128251 | Yuba | DOBBINS 1101 | DOBBINS 11011264 | Animal | 2023-10-14 07:03 | 10/10 - 10/16 | 2023-10-14 09:55 | 101.7544 | FTS | 52200 | 513 | 54 | 39 | 14 | 1 | 0 | 3 | 172
23-0128272 | San Benito | HOLLISTER 2105 | HOLLISTER 21054048 | Animal | 2023-10-14 09:14 | 10/10 - 10/16 | 2023-10-14 10:07 | 53 | FTS | 6731 | 127 | 2 | 2 | 2 | 2 | 0 | 0 | 53
23-0128255 | Tuolumne | CURTIS 1702 | CURTIS 170210940 | Unknown Cause | 2023-10-14 07:45 | 10/10 - 10/16 | 2023-10-14 10:19 | 113.7764 | FTS | 72248 | 635 | 66 | 44 | 3 | 1 | 0 | 0 | 154
23-0128243 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Unknown Cause | 2023-10-14 01:20 | 10/10 - 10/16 | 2023-10-14 12:35 | 609.6018 | FTS | 1734317 | 2845 | 231 | 170 | 26 | 1 | 0 | 1 | 675
23-0128314 | Placer | BELL 1108 | BELL 1108339792 | Animal | 2023-10-14 13:09 | 10/10 - 10/16 | 2023-10-14 14:04 | 55 | FTS | 4730 | 86 | 9 | 5 | 0 | 0 | 0 | 3 | 55
23-0128186 | Nevada | GRASS VALLEY 1101 | GRASS VALLEY 11012208 | Equipment Failure/Involved | 2023-10-13 17:34 | 10/10 - 10/16 | 2023-10-14 14:04 | 437.9428 | FTS | 176053 | 402 | 35 | 29 | 6 | 0 | 0 | 1 | 1230
23-0128303 | Napa | SILVERADO 2105 | SILVERADO 2105768606 | Unknown Cause | 2023-10-14 12:37 | 10/10 - 10/16 | 2023-10-14 14:12 | 94.3182 | FTS | 4150 | 44 | 2 | 1 | 2 | 0 | 0 | 0 | 95
23-0128322 | Napa | SILVERADO 2105 | SILVERADO 2105768606 | Unknown Cause | 2023-10-14 14:17 | 10/10 - 10/16 | 2023-10-14 14:53 | 33.5 | FTS | 1474 | 44 | 2 | 1 | 2 | 0 | 0 | 0 | 36
23-0128308 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Unknown Cause | 2023-10-14 13:04 | 10/10 - 10/16 | 2023-10-14 15:26 | 142 | FTS | 127090 | 895 | 66 | 45 | 16 | 0 | 0 | 0 | 142
23-0128164 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 110169866 | Vegetation | 2023-10-13 15:55 | 10/10 - 10/16 | 2023-10-14 17:42 | 1524.9963 | FTS | 1239822 | 813 | 34 | 26 | 16 | 3 | 0 | 0 | 1547
23-0128317 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041634 | Equipment Failure/Involved | 2023-10-14 13:56 | 10/10 - 10/16 | 2023-10-14 20:10 | 134.4317 | FTS | 74744 | 556 | 54 | 36 | 6 | 0 | 0 | 2 | 374
23-0128337 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X06 | Unknown Cause | 2023-10-14 15:39 | 10/10 - 10/16 | 2023-10-14 21:11 | 311.7674 | FTS | 53624 | 172 | 4 | 4 | 7 | 2 | 0 | 0 | 332
23-0128380 | Placer | HALSEY 1102 | HALSEY 1102164068 | Unknown Cause | 2023-10-15 00:57 | 10/10 - 10/16 | 2023-10-15 08:54 | 197.8923 | FTS | 192945 | 975 | 45 | 33 | 19 | 2 | 0 | 0 | 477
23-0128378 | Napa | SILVERADO 2105 | SILVERADO 2105247660 | 3rd Party | 2023-10-15 00:42 | 10/10 - 10/16 | 2023-10-15 15:29 | 475.8085 | FTS | 22363 | 47 | 1 | 1 | 1 | 0 | 0 | 0 | 887
23-0128423 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Vegetation | 2023-10-15 14:30 | 10/10 - 10/16 | 2023-10-15 18:08 | 74.7056 | FTS | 159123 | 2130 | 163 | 124 | 19 | 3 | 0 | 14 | 218
23-0128457 | Nevada | NARROWS 2105 | NARROWS 21052748 | Unknown Cause | 2023-10-15 18:59 | 10/10 - 10/16 | 2023-10-15 20:46 | 87.1561 | FTS | 78179 | 897 | 68 | 45 | 8 | 0 | 0 | 4 | 107
23-0128472 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210576694 | Unknown Cause | 2023-10-15 21:41 | 10/10 - 10/16 | 2023-10-16 02:58 | 317 | FTS | 10461 | 33 | 6 | 3 | 0 | 0 | 0 | 0 | 317
23-0128498 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111R86 | Animal | 2023-10-16 02:50 | 10/10 - 10/16 | 2023-10-16 07:03 | 213.4539 | FTS | 30097 | 141 | 6 | 6 | 0 | 0 | 0 | 1 | 253
23-0128509 | Sonoma | MOLINO 1102 | MOLINO 1102381468 | Animal | 2023-10-16 06:32 | 10/10 - 10/16 | 2023-10-16 08:02 | 90 | FTS | 3780 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 90
23-0128511 | Lake | HARTLEY 1101 | HARTLEY 1101658 | Unknown Cause | 2023-10-16 06:57 | 10/10 - 10/16 | 2023-10-16 10:03 | 75.1138 | FTS | 43566 | 580 | 31 | 21 | 8 | 0 | 0 | 2 | 186
23-0128575 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | Vegetation | 2023-10-16 09:10 | 10/10 - 10/16 | 2023-10-16 10:17 | 67 | FTS | 44957 | 671 | 52 | 35 | 3 | 0 | 0 | 5 | 67
23-0128530 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR070 | Unknown Cause | 2023-10-16 07:44 | 10/10 - 10/16 | 2023-10-16 10:24 | 153.2515 | FTS | 24980 | 163 | 8 | 5 | 2 | 0 | 0 | 1 | 160
23-0128635 | Amador | CLAY 1101 | CLAY 110113450 | Animal | 2023-10-16 10:28 | 10/10 - 10/16 | 2023-10-16 11:17 | 49 | FTS | 21756 | 444 | 44 | 32 | 5 | 0 | 0 | 0 | 49
23-0128578 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210961892 | Animal | 2023-10-16 09:12 | 10/10 - 10/16 | 2023-10-16 11:28 | 136 | FTS | 55624 | 409 | 45 | 29 | 2 | 0 | 0 | 4 | 136
23-0128714 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-10-16 12:42 | 10/10 - 10/16 | 2023-10-16 15:24 | 161.0175 | FTS | 9178 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 162
23-0128858 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Equipment Failure/Involved | 2023-10-16 15:33 | 10/17 - 10/23 | 2023-10-16 17:53 | 140 | FTS | 185220 | 1323 | 120 | 99 | 15 | 1 | 0 | 0 | 140
23-0128496 | Monterey | HATTON 1101 | HATTON 11012026 | Equipment Failure/Involved | 2023-10-16 02:03 | 10/17 - 10/23 | 2023-10-16 18:58 | 128.6879 | FTS | 390439 | 3034 | 91 | 61 | 80 | 8 | 0 | 0 | 1015
23-0129095 | Calaveras | SALT SPRINGS 2101 | SALT SPRINGS 21013116 | Company Initiated | 2023-10-17 10:31 | 10/17 - 10/23 | 2023-10-17 10:41 | 10 | FTS | 9360 | 936 | 18 | 15 | 10 | 2 | 0 | 0 | 10
23-0129056 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X06 | Unknown Cause | 2023-10-17 09:35 | 10/17 - 10/23 | 2023-10-17 13:10 | 185.8372 | FTS | 31964 | 172 | 4 | 4 | 7 | 2 | 0 | 0 | 215
23-0129219 | Humboldt | WILLOW CREEK 1101 | WILLOW CREEK 11015002 | Animal | 2023-10-17 13:14 | 10/17 - 10/23 | 2023-10-17 13:44 | 30 | FTS | 17880 | 596 | 28 | 21 | 5 | 0 | 1 | 0 | 30
23-0129044 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110180930 | Unknown Cause | 2023-10-17 09:24 | 10/17 - 10/23 | 2023-10-17 13:46 | 262 | FTS | 182352 | 696 | 41 | 32 | 18 | 0 | 0 | 0 | 262
23-0128962 | Butte | SYCAMORE CREEK 1109 | SYCAMORE CREEK 1109CB | Unknown Cause | 2023-10-17 07:14 | 10/17 - 10/23 | 2023-10-17 14:18 | 130.5858 | FTS | 115699 | 886 | 54 | 36 | 12 | 1 | 0 | 0 | 424
23-0129004 | Monterey | PRUNEDALE 1110 | PRUNEDALE 1110557716 | Animal | 2023-10-17 08:19 | 10/17 - 10/23 | 2023-10-17 15:15 | 136.8408 | FTS | 45568 | 333 | 19 | 17 | 5 | 0 | 0 | 0 | 416
23-0128952 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown Cause | 2023-10-17 07:02 | 10/17 - 10/23 | 2023-10-17 16:11 | 287.9484 | FTS | 145126 | 504 | 30 | 21 | 11 | 0 | 0 | 2 | 549
23-0129150 | Butte | CLARK ROAD 1102 | CLARK ROAD 110281296 | 3rd Party | 2023-10-17 11:24 | 10/17 - 10/23 | 2023-10-17 18:19 | 81.5151 | FTS | 105399 | 1293 | 105 | 76 | 26 | 3 | 0 | 2 | 415
23-0110859 | Monterey | LAURELES 1112 | LAURELES 1112CB | Company Initiated | 2023-10-17 20:25 | 10/17 - 10/23 | 2023-10-17 21:29 | 64 | FTS | 156416 | 2444 | 101 | 76 | 71 | 3 | 0 | 0 | 64
23-0129402 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-10-18 06:21 | 10/17 - 10/23 | 2023-10-18 08:24 | 123 | FTS | 7011 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 123
23-0129416 | Placer | WEIMAR 1101 | WEIMAR 11012058 | Unknown Cause | 2023-10-18 07:00 | 10/17 - 10/23 | 2023-10-18 10:49 | 182.7997 | FTS | 108583 | 594 | 39 | 28 | 9 | 0 | 0 | 3 | 229
23-0129649 | Santa Clara | STELLING 1110 | STELLING 1110396595 | Unknown Cause | 2023-10-18 11:05 | 10/17 - 10/23 | 2023-10-18 12:11 | 66 | FTS | 2838 | 43 | 2 | 2 | 1 | 0 | 0 | 0 | 66
23-0129611 | San Mateo | MENLO 1102 | MENLO 1102628458 | Unknown Cause | 2023-10-18 11:30 | 10/17 - 10/23 | 2023-10-18 12:49 | 79 | FTS | 1501 | 19 | 1 | 1 | 1 | 0 | 0 | 0 | 79
23-0129745 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | 3rd Party | 2023-10-18 14:46 | 10/17 - 10/23 | 2023-10-18 15:03 | 15.0037 | FTS | 8207 | 547 | 20 | 11 | 9 | 1 | 0 | 2 | 17
23-0129896 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | 3rd Party | 2023-10-18 20:58 | 10/17 - 10/23 | 2023-10-18 22:19 | 52.053 | FTS | 28473 | 547 | 20 | 11 | 9 | 1 | 0 | 2 | 81
23-0130045 | Marin | STAFFORD 1102 | STAFFORD 1102524 | Company Initiated | 2023-10-19 09:21 | 10/17 - 10/23 | 2023-10-19 09:45 | 24 | FTS | 35688 | 1487 | 98 | 58 | 12 | 1 | 0 | 0 | 24
23-0130000 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Animal | 2023-10-19 08:05 | 10/17 - 10/23 | 2023-10-19 10:06 | 81.2649 | FTS | 84678 | 1042 | 84 | 61 | 18 | 5 | 0 | 2 | 121
23-0130086 | Contra Costa | SOBRANTE 1103 | SOBRANTE 1103LA401R | Unknown Cause | 2023-10-19 10:08 | 10/17 - 10/23 | 2023-10-19 11:44 | 96 | FTS | 56832 | 592 | 36 | 26 | 6 | 0 | 0 | 0 | 96
23-0130190 | Monterey | GABILAN 1101 | GABILAN 1101566352 | Unknown Cause | 2023-10-19 12:27 | 10/17 - 10/23 | 2023-10-19 13:33 | 66 | FTS | 330 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66
23-0130188 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR292 | Unknown Cause | 2023-10-19 12:22 | 10/17 - 10/23 | 2023-10-19 14:11 | 108.5201 | FTS | 83669 | 771 | 60 | 48 | 17 | 0 | 0 | 3 | 109
23-0129948 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | 3rd Party | 2023-10-19 05:20 | 10/17 - 10/23 | 2023-10-19 14:26 | 148.1277 | FTS | 125316 | 846 | 51 | 34 | 11 | 0 | 0 | 3 | 546
23-0130340 | Monterey | JOLON 1102 | JOLON 11027002 | Unknown Cause | 2023-10-19 15:36 | 10/17 - 10/23 | 2023-10-19 17:04 | 88 | FTS | 12144 | 138 | 7 | 5 | 3 | 2 | 0 | 3 | 88
23-0130420 | Sonoma | FULTON 1107 | FULTON 1107126742 | Vegetation | 2023-10-19 23:59 | 10/17 - 10/23 | 2023-10-20 01:37 | 98 | FTS | 92120 | 940 | 65 | 52 | 22 | 2 | 0 | 5 | 98
23-0130423 | Monterey | SPENCE 1101 | SPENCE 1101965598 | Unknown Cause | 2023-10-20 01:30 | 10/17 - 10/23 | 2023-10-20 05:27 | 237 | FTS | 39816 | 168 | 4 | 3 | 2 | 0 | 0 | 1 | 237
23-0130443 | Shasta | STILLWATER 1101 | STILLWATER 1101747294 | Company Initiated | 2023-10-20 06:30 | 10/17 - 10/23 | 2023-10-20 06:40 | 10 | FTS | 140 | 14 | 0 | 0 | 5 | 0 | 0 | 0 | 10
23-0130364 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | 3rd Party | 2023-10-19 18:19 | 10/17 - 10/23 | 2023-10-20 08:56 | 374.4104 | FTS | 194319 | 519 | 35 | 22 | 14 | 4 | 0 | 7 | 877
23-0130520 | Mendocino | WILLITS 1103 | WILLITS 1103696 | Company Initiated | 2023-10-20 09:02 | 10/17 - 10/23 | 2023-10-20 10:18 | 73.655 | FTS | 33734 | 458 | 37 | 30 | 7 | 0 | 0 | 1 | 76
23-0130130 | Napa | PUEBLO 2103 | PUEBLO 210398394 | Unknown Cause | 2023-10-19 10:52 | 10/17 - 10/23 | 2023-10-20 12:24 | 173.5715 | FTS | 425771 | 2453 | 150 | 111 | 25 | 4 | 0 | 4 | 1532
23-0130523 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R56 | Unknown Cause | 2023-10-20 09:12 | 10/17 - 10/23 | 2023-10-20 13:43 | 228.8491 | FTS | 53093 | 232 | 13 | 13 | 10 | 0 | 0 | 1 | 271
23-0130704 | Butte | NOTRE DAME 1104 | NOTRE DAME 11042028 | Company Initiated | 2023-10-20 14:02 | 10/17 - 10/23 | 2023-10-20 14:33 | 31 | FTS | 744 | 24 | 1 | 1 | 0 | 0 | 0 | 0 | 31
23-0130738 | Mendocino | WILLITS 1103 | WILLITS 1103696 | Company Initiated | 2023-10-20 14:51 | 10/17 - 10/23 | 2023-10-20 15:32 | 39.4435 | FTS | 18144 | 460 | 37 | 30 | 7 | 0 | 0 | 1 | 41
23-0130801 | Humboldt | FRUITLAND 1142 | FRUITLAND 1142899734 | Unknown Cause | 2023-10-20 18:44 | 10/17 - 10/23 | 2023-10-20 22:22 | 80.3988 | FTS | 41325 | 514 | 13 | 8 | 13 | 4 | 0 | 0 | 218
23-0130858 | Mendocino | MENDOCINO 1101 | MENDOCINO 1101856020 | Animal | 2023-10-21 08:30 | 10/17 - 10/23 | 2023-10-21 09:40 | 63.2246 | HLT | 47292 | 748 | 58 | 41 | 10 | 1 | 0 | 0 | 70
23-0130855 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121560 | Unknown Cause | 2023-10-21 07:40 | 10/17 - 10/23 | 2023-10-21 09:55 | 28.9703 | FTS | 6837 | 236 | 5 | 5 | 8 | 0 | 0 | 0 | 135
23-0130856 | Tuolumne | CURTIS 1702 | CURTIS 17028000 | Unknown Cause | 2023-10-21 07:48 | 10/17 - 10/23 | 2023-10-21 11:15 | 203.8646 | FTS | 234852 | 1152 | 119 | 86 | 16 | 1 | 0 | 0 | 207
23-0130850 | Napa | PUEBLO 1104 | PUEBLO 1104105708 | Unknown Cause | 2023-10-21 06:50 | 10/17 - 10/23 | 2023-10-21 11:32 | 116.5295 | FTS | 65140 | 559 | 25 | 18 | 2 | 0 | 0 | 5 | 282
23-0130904 | Monterey | DEL MONTE 2104 | LAURELES 11112020 | Company Initiated | 2023-10-21 11:02 | 10/17 - 10/23 | 2023-10-21 12:02 | 60 | FTS | 50220 | 837 | 29 | 18 | 26 | 0 | 0 | 0 | 60
23-0130882 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11016014 | Unknown Cause | 2023-10-21 09:15 | 10/17 - 10/23 | 2023-10-21 14:45 | 330 | FTS | 45540 | 138 | 4 | 2 | 10 | 3 | 0 | 0 | 330
23-0130921 | Marin | WOODACRE 1102 | WOODACRE 11021280 | Animal | 2023-10-21 13:58 | 10/17 - 10/23 | 2023-10-21 15:59 | 100.6721 | FTS | 79833 | 793 | 46 | 34 | 16 | 5 | 0 | 0 | 121
23-0130923 | El Dorado | CLARKSVILLE 2103 | CLARKSVILLE 210319572 | 3rd Party | 2023-10-21 14:28 | 10/17 - 10/23 | 2023-10-21 16:23 | 77.9736 | FTS | 29552 | 379 | 36 | 31 | 16 | 4 | 0 | 14 | 115
23-0130915 | Mendocino | WILLITS 1104 | WILLITS 1104341020 | Unknown Cause | 2023-10-21 13:05 | 10/17 - 10/23 | 2023-10-21 17:20 | 142.6768 | FTS | 60923 | 427 | 32 | 22 | 13 | 0 | 0 | 1 | 255
23-0130997 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21011703 | Animal | 2023-10-22 06:31 | 10/17 - 10/23 | 2023-10-22 08:00 | 89 | FTS | 89 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 89
23-0130941 | Amador | MARTELL 1101 | MARTELL 110111244 | Company Initiated | 2023-10-21 16:41 | 10/17 - 10/23 | 2023-10-22 10:38 | 203.4399 | FTS | 135491 | 666 | 70 | 49 | 5 | 0 | 0 | 10 | 1077
23-0131019 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11022124 | 3rd Party | 2023-10-22 10:36 | 10/17 - 10/23 | 2023-10-22 11:19 | 43 | FTS | 172 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 43
23-0131000 | Napa | SILVERADO 2104 | SILVERADO 210478268 | Animal | 2023-10-22 06:53 | 10/17 - 10/23 | 2023-10-22 11:28 | 226.4895 | FTS | 118454 | 523 | 37 | 28 | 17 | 2 | 2 | 2 | 275
23-0131016 | Sonoma | MIRABEL 1102 | MIRABEL 1102332 | Vegetation | 2023-10-22 09:58 | 10/17 - 10/23 | 2023-10-22 11:43 | 91.5245 | FTS | 85850 | 938 | 49 | 34 | 16 | 0 | 0 | 0 | 105
23-0131004 | Napa | SILVERADO 2104 | SILVERADO 2104633600 | Unknown Cause | 2023-10-22 08:18 | 10/17 - 10/23 | 2023-10-22 12:13 | 202.9364 | FTS | 70216 | 346 | 20 | 10 | 13 | 3 | 0 | 0 | 235
23-0130987 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown Cause | 2023-10-22 05:05 | 10/17 - 10/23 | 2023-10-22 12:45 | 286.9231 | FTS | 7460 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 460
23-0130981 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101890 | Unknown Cause | 2023-10-22 03:00 | 10/17 - 10/23 | 2023-10-22 13:56 | 310.2674 | FTS | 53366 | 172 | 4 | 4 | 1 | 0 | 0 | 0 | 656
23-0131039 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown Cause | 2023-10-22 13:15 | 10/17 - 10/23 | 2023-10-22 15:09 | 114 | FTS | 2964 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 114
23-0131059 | El Dorado | DIAMOND SPRINGS 1107 | DIAMOND SPRINGS 11071402 | Unknown Cause | 2023-10-22 15:34 | 10/17 - 10/23 | 2023-10-22 16:44 | 70 | FTS | 66150 | 945 | 90 | 62 | 13 | 7 | 0 | 6 | 70
23-0131082 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210119752 | Unknown Cause | 2023-10-22 18:58 | 10/17 - 10/23 | 2023-10-22 19:16 | 18 | FTS | 19656 | 1092 | 102 | 75 | 13 | 2 | 0 | 2 | 18
23-0131070 | Santa Cruz | ROB ROY 2105 | ROB ROY 21055090 | Unknown Cause | 2023-10-22 18:13 | 10/17 - 10/23 | 2023-10-22 20:30 | 83.7908 | FTS | 36449 | 435 | 26 | 20 | 5 | 1 | 0 | 4 | 137
23-0131098 | Tuolumne | PEORIA 1705 | PEORIA 170567898 | Company Initiated | 2023-10-22 20:56 | 10/17 - 10/23 | 2023-10-22 21:18 | 22 | FTS | 23738 | 1079 | 106 | 79 | 12 | 0 | 0 | 0 | 22
23-0131076 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102317156 | Vegetation | 2023-10-22 18:55 | 10/17 - 10/23 | 2023-10-22 21:39 | 110.2885 | FTS | 5735 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 164
23-0131096 | Tuolumne | PEORIA 1704 | PEORIA 1704CB | Unknown Cause | 2023-10-22 20:55 | 10/17 - 10/23 | 2023-10-22 22:49 | 107.3172 | FTS | 345132 | 3216 | 285 | 207 | 78 | 1 | 1 | 2 | 114
23-0131053 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210519062 | Equipment Failure/Involved | 2023-10-22 14:55 | 10/17 - 10/23 | 2023-10-22 22:51 | 124.3022 | FTS | 71971 | 579 | 37 | 25 | 26 | 4 | 0 | 0 | 476
23-0131028 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Equipment Failure/Involved | 2023-10-22 11:58 | 10/17 - 10/23 | 2023-10-23 00:48 | 91.4921 | FTS | 250231 | 2735 | 180 | 146 | 41 | 7 | 0 | 0 | 770
23-0131101 | Tuolumne | PEORIA 1705 | PEORIA 170567898 | Company Initiated | 2023-10-22 21:28 | 10/17 - 10/23 | 2023-10-23 04:17 | 348.7442 | FTS | 376295 | 1079 | 106 | 79 | 12 | 0 | 0 | 0 | 409
23-0131031 | Santa Cruz | ROB ROY 2104 | ROB ROY 2104974520 | Vegetation | 2023-10-22 12:26 | 10/17 - 10/23 | 2023-10-23 04:28 | 52.6818 | FTS | 17385 | 330 | 24 | 21 | 4 | 0 | 0 | 1 | 962
23-0131161 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106974130 | Unknown Cause | 2023-10-23 07:11 | 10/17 - 10/23 | 2023-10-23 08:36 | 85 | FTS | 7735 | 91 | 11 | 11 | 1 | 0 | 0 | 0 | 85
23-0131160 | Solano | JAMESON 1105 | JAMESON 1105466348 | Unknown Cause | 2023-10-23 07:01 | 10/17 - 10/23 | 2023-10-23 08:38 | 97 | FTS | 33950 | 350 | 12 | 6 | 7 | 2 | 0 | 2 | 97
23-0130989 | Contra Costa | TIDEWATER 2106 | TIDEWATER 210657926 | Equipment Failure/Involved | 2023-10-22 05:35 | 10/17 - 10/23 | 2023-10-23 10:22 | 197.9914 | FTS | 346485 | 1750 | 138 | 90 | 65 | 5 | 0 | 0 | 1727
23-0131163 | Mendocino | WILLITS 1103 | WILLITS 11032506 | Unknown Cause | 2023-10-23 07:16 | 10/17 - 10/23 | 2023-10-23 10:58 | 100.9161 | FTS | 15642 | 155 | 15 | 12 | 1 | 0 | 0 | 0 | 222
23-0131224 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102262 | Vegetation | 2023-10-23 09:20 | 10/17 - 10/23 | 2023-10-23 11:53 | 137.6173 | FTS | 44588 | 324 | 18 | 14 | 11 | 0 | 0 | 4 | 153
23-0131136 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101730862 | 3rd Party | 2023-10-23 04:57 | 10/17 - 10/23 | 2023-10-23 12:28 | 451 | FTS | 14432 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 451
23-0131345 | Monterey | JOLON 1102 | JOLON 11027002 | Unknown Cause | 2023-10-23 11:00 | 10/17 - 10/23 | 2023-10-23 12:41 | 101 | FTS | 13938 | 138 | 7 | 5 | 3 | 2 | 0 | 3 | 101
23-0131132 | Monterey | LAURELES 1111 | LAURELES 1111432 | Unknown Cause | 2023-10-23 03:14 | 10/17 - 10/23 | 2023-10-23 14:34 | 521.6211 | FTS | 167962 | 322 | 6 | 5 | 7 | 0 | 0 | 0 | 680
23-0131121 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210961892 | Equipment Failure/Involved | 2023-10-22 22:53 | 10/24 - 10/30 | 2023-10-23 20:31 | 376.8337 | FTS | 154125 | 409 | 45 | 29 | 2 | 0 | 0 | 4 | 1298
23-0131606 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110317796 | Unknown Cause | 2023-10-23 22:41 | 10/24 - 10/30 | 2023-10-24 00:41 | 114.3048 | FTS | 158655 | 1388 | 42 | 31 | 18 | 0 | 0 | 13 | 120
23-0131617 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011750 | Vegetation | 2023-10-24 00:24 | 10/24 - 10/30 | 2023-10-24 03:11 | 167 | FTS | 15364 | 92 | 2 | 1 | 2 | 0 | 0 | 0 | 167
23-0131554 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210312990 | Vegetation | 2023-10-23 17:06 | 10/24 - 10/30 | 2023-10-24 04:10 | 74.8622 | FTS | 59216 | 791 | 64 | 55 | 17 | 2 | 0 | 10 | 664
23-0131630 | Mendocino | WILLITS 1103 | WILLITS 1103564506 | Company Initiated | 2023-10-24 06:44 | 10/24 - 10/30 | 2023-10-24 07:31 | 47 | FTS | 5264 | 112 | 10 | 6 | 4 | 0 | 0 | 1 | 47
23-0131615 | Calaveras | WEST POINT 1102 | WEST POINT 11024788 | Unknown Cause | 2023-10-24 00:09 | 10/24 - 10/30 | 2023-10-24 09:36 | 267.4299 | FTS | 200305 | 749 | 49 | 35 | 7 | 0 | 0 | 1 | 567
23-0131665 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112238418 | Unknown Cause | 2023-10-24 08:04 | 10/24 - 10/30 | 2023-10-24 09:56 | 112 | FTS | 1344 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 112
23-0131705 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Company Initiated | 2023-10-24 08:54 | 10/24 - 10/30 | 2023-10-24 10:16 | 82 | FTS | 144812 | 1766 | 127 | 97 | 26 | 5 | 0 | 2 | 82
23-0131139 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | 3rd Party | 2023-10-23 05:31 | 10/24 - 10/30 | 2023-10-24 10:52 | 237.0261 | FTS | 27258 | 115 | 5 | 5 | 5 | 0 | 0 | 0 | 1761
23-0131727 | Nevada | NARROWS 2102 | NARROWS 21022728 | Unknown Cause | 2023-10-24 09:28 | 10/24 - 10/30 | 2023-10-24 12:23 | 92.2343 | FTS | 207896 | 2254 | 182 | 122 | 38 | 6 | 0 | 14 | 175
23-0131851 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Company Initiated | 2023-10-24 12:27 | 10/24 - 10/30 | 2023-10-24 12:36 | 9 | FTS | 1530 | 170 | 12 | 7 | 13 | 0 | 0 | 1 | 9
23-0131557 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Equipment Failure/Involved | 2023-10-23 17:15 | 10/24 - 10/30 | 2023-10-24 15:55 | 1350.3023 | FTS | 768322 | 569 | 37 | 25 | 27 | 3 | 0 | 0 | 1360
23-0131619 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106697500 | Equipment Failure/Involved | 2023-10-24 03:58 | 10/24 - 10/30 | 2023-10-24 17:11 | 674.9986 | FTS | 1451922 | 2151 | 188 | 148 | 54 | 8 | 0 | 10 | 793
23-0132019 | Sonoma | DUNBAR 1101 | DUNBAR 1101534 | Company Initiated | 2023-10-24 15:46 | 10/24 - 10/30 | 2023-10-24 17:32 | 106 | FTS | 7102 | 67 | 2 | 1 | 2 | 0 | 0 | 3 | 106
23-0132039 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-10-24 17:12 | 10/24 - 10/30 | 2023-10-24 18:37 | 85 | FTS | 4845 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 85
23-0132052 | Mendocino | POINT ARENA 1101 | POINT ARENA 11013702 | Unknown Cause | 2023-10-24 18:28 | 10/24 - 10/30 | 2023-10-24 20:03 | 95 | FTS | 5415 | 57 | 3 | 3 | 1 | 0 | 0 | 0 | 95
23-0132055 | San Mateo | MENLO 1102 | MENLO 1102154024 | Unknown Cause | 2023-10-24 18:42 | 10/24 - 10/30 | 2023-10-25 07:17 | 751.85 | FTS | 75185 | 100 | 4 | 3 | 5 | 0 | 0 | 0 | 755
23-0132162 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111514592 | Animal | 2023-10-25 07:40 | 10/24 - 10/30 | 2023-10-25 08:59 | 77.2319 | FTS | 158557 | 2053 | 145 | 95 | 33 | 7 | 0 | 5 | 79
23-0132243 | Tuolumne | PEORIA 1705 | PEORIA 170567898 | Company Initiated | 2023-10-25 09:21 | 10/24 - 10/30 | 2023-10-25 09:34 | 13 | FTS | 11713 | 901 | 90 | 70 | 12 | 0 | 0 | 0 | 13
23-0132269 | Monterey | HATTON 1101 | HATTON 11012026 | Unknown Cause | 2023-10-25 09:48 | 10/24 - 10/30 | 2023-10-25 10:30 | 35.0542 | FTS | 45290 | 1292 | 53 | 40 | 39 | 5 | 0 | 0 | 42
23-0132319 | Tehama | CORNING 1102 | CORNING 11021900 | Unknown Cause | 2023-10-25 10:56 | 10/24 - 10/30 | 2023-10-25 12:06 | 65.6995 | FTS | 24703 | 376 | 27 | 22 | 11 | 3 | 0 | 1 | 70
23-0132417 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Company Initiated | 2023-10-25 13:03 | 10/24 - 10/30 | 2023-10-25 13:16 | 10.3657 | FTS | 27780 | 2680 | 180 | 146 | 41 | 7 | 0 | 0 | 13
23-0132325 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Unknown Cause | 2023-10-25 10:59 | 10/24 - 10/30 | 2023-10-25 13:18 | 105.1957 | FTS | 248367 | 2361 | 69 | 54 | 49 | 2 | 0 | 4 | 139
23-0132433 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062104 | Company Initiated | 2023-10-25 13:18 | 10/24 - 10/30 | 2023-10-25 14:01 | 34.2414 | FTS | 68928 | 2013 | 31 | 23 | 4 | 0 | 0 | 0 | 43
23-0132443 | Nevada | SUMMIT 1102 | SUMMIT 1102CB | Unknown Cause | 2023-10-25 13:35 | 10/24 - 10/30 | 2023-10-25 17:12 | 217 | FTS | 45136 | 208 | 1 | 0 | 3 | 0 | 0 | 0 | 217
23-0132603 | Santa Barbara | CUYAMA 1103 | CUYAMA 1103282557 | Unknown Cause | 2023-10-25 19:10 | 10/24 - 10/30 | 2023-10-25 21:12 | 122 | FTS | 28182 | 231 | 14 | 11 | 2 | 1 | 0 | 0 | 122
23-0132594 | Shasta | ANTLER 1101 | ANTLER 1101718316 | Vegetation | 2023-10-25 18:13 | 10/24 - 10/30 | 2023-10-25 22:00 | 91.325 | FTS | 36530 | 400 | 19 | 11 | 9 | 1 | 0 | 0 | 227
23-0132558 | Butte | WYANDOTTE 1109 | WYANDOTTE 1109759354 | 3rd Party | 2023-10-25 16:04 | 10/24 - 10/30 | 2023-10-26 03:30 | 87.5969 | FTS | 125614 | 1434 | 152 | 108 | 19 | 7 | 0 | 2 | 686
23-0132573 | Mendocino | UKIAH 1114 | UKIAH 1114822 | 3rd Party | 2023-10-25 16:42 | 10/24 - 10/30 | 2023-10-26 03:34 | 245.2179 | FTS | 189063 | 771 | 47 | 28 | 11 | 1 | 0 | 0 | 652
23-0132673 | Monterey | LAURELES 1112 | LAURELES 11122142 | Unknown Cause | 2023-10-26 02:20 | 10/24 - 10/30 | 2023-10-26 06:32 | 129.514 | FTS | 97265 | 751 | 31 | 23 | 12 | 2 | 0 | 0 | 252
23-0132675 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101975548 | Unknown Cause | 2023-10-26 05:08 | 10/24 - 10/30 | 2023-10-26 07:17 | 129 | FTS | 290895 | 2255 | 181 | 135 | 45 | 4 | 0 | 0 | 129
23-0132684 | Fresno | FIREBAUGH SUB | N/A | Unknown Cause | 2023-10-26 06:37 | 10/24 - 10/30 | 2023-10-26 07:28 | 48.5023 | T-EPSS | 177470 | 3659 | 151 | 95 | 51 | 14 | 0 | 0 | 51
23-0132623 | Placer | PENRYN 1107 | PENRYN 11072706 | 3rd Party | 2023-10-25 21:46 | 10/24 - 10/30 | 2023-10-26 07:33 | 98.4511 | FTS | 106721 | 1084 | 88 | 57 | 13 | 1 | 0 | 7 | 587
23-0132688 | Fresno | ORO LOMA SUB | N/A | Unknown Cause | 2023-10-26 06:37 | 10/24 - 10/30 | 2023-10-26 07:37 | 58.8228 | T-EPSS | 37176 | 632 | 7 | 5 | 10 | 0 | 0 | 0 | 60
23-0132719 | Amador | CLAY 1101 | CLAY 1101CB | 3rd Party | 2023-10-26 07:33 | 10/24 - 10/30 | 2023-10-26 08:19 | 46 | FTS | 79764 | 1734 | 138 | 94 | 25 | 3 | 0 | 4 | 46
23-0132685 | Merced | DOS PALOS SUB | N/A | Unknown Cause | 2023-10-26 06:37 | 10/24 - 10/30 | 2023-10-26 09:08 | 55.0373 | T-EPSS | 141666 | 2574 | 171 | 104 | 25 | 3 | 0 | 0 | 151
23-0132687 | Merced | SANTA RITA SUB | N/A | Unknown Cause | 2023-10-26 06:37 | 10/24 - 10/30 | 2023-10-26 09:18 | 161 | T-EPSS | 156492 | 972 | 26 | 21 | 10 | 0 | 0 | 0 | 161
23-0132736 | Tulare | REEDLEY 1112 | REEDLEY 1112477952 | Unknown Cause | 2023-10-26 08:14 | 10/24 - 10/30 | 2023-10-26 09:21 | 67 | FTS | 603 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 67
23-0132674 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Vegetation | 2023-10-26 04:20 | 10/24 - 10/30 | 2023-10-26 09:36 | 230.0385 | FTS | 143544 | 624 | 73 | 53 | 7 | 0 | 0 | 1 | 316
23-0132761 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102156 | Company Initiated | 2023-10-26 09:06 | 10/24 - 10/30 | 2023-10-26 09:44 | 38 | FTS | 19570 | 515 | 34 | 20 | 9 | 0 | 0 | 0 | 38
23-0132747 | Fresno | AUBERRY 1101 | AUBERRY 1101R324 | Company Initiated | 2023-10-26 08:33 | 10/24 - 10/30 | 2023-10-26 09:50 | 77 | FTS | 11242 | 146 | 6 | 4 | 5 | 0 | 0 | 1 | 77
23-0132696 | Tuolumne | PEORIA 1705 | PEORIA 1701169700 | Unknown Cause | 2023-10-26 06:59 | 10/24 - 10/30 | 2023-10-26 11:17 | 258 | FTS | 388548 | 1506 | 90 | 72 | 17 | 1 | 0 | 0 | 258
23-0132700 | Santa Clara | LOS GATOS 1107 | LOS GATOS 1107CB | Animal | 2023-10-26 07:20 | 10/24 - 10/30 | 2023-10-26 12:28 | 270.6736 | FTS | 626068 | 2313 | 132 | 95 | 72 | 2 | 0 | 13 | 308
23-0132772 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 11029470 | Unknown Cause | 2023-10-26 09:23 | 10/24 - 10/30 | 2023-10-26 13:09 | 148.809 | FTS | 98958 | 665 | 66 | 44 | 9 | 3 | 0 | 0 | 226
23-0133022 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Unknown Cause | 2023-10-26 21:11 | 10/24 - 10/30 | 2023-10-27 10:23 | 792 | FTS | 55440 | 70 | 3 | 2 | 1 | 0 | 0 | 0 | 792
23-0133136 | Placer | BELL 1108 | BELL 11082202 | Animal | 2023-10-27 08:54 | 10/24 - 10/30 | 2023-10-27 11:20 | 106.2634 | FTS | 55682 | 524 | 32 | 29 | 7 | 0 | 0 | 6 | 146
23-0133250 | Sonoma | SONOMA 1105 | SONOMA 1105138 | Unknown Cause | 2023-10-27 12:04 | 10/24 - 10/30 | 2023-10-27 15:05 | 141.5059 | FTS | 120280 | 850 | 38 | 26 | 9 | 0 | 0 | 8 | 181
23-0133361 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 040116010 | Vegetation | 2023-10-27 14:51 | 10/24 - 10/30 | 2023-10-27 16:20 | 89 | FTS | 23585 | 265 | 19 | 16 | 7 | 1 | 0 | 0 | 89
23-0133432 | San Mateo | HALF MOON BAY 1102 | HALF MOON BAY 11022032 | Company Initiated | 2023-10-27 19:39 | 10/24 - 10/30 | 2023-10-27 20:26 | 38.2116 | FTS | 124952 | 3270 | 167 | 121 | 60 | 5 | 1 | 6 | 47
23-0133441 | Napa | MONTICELLO 1101 | MONTICELLO 110152910 | Unknown Cause | 2023-10-27 20:10 | 10/24 - 10/30 | 2023-10-27 22:50 | 160 | FTS | 44160 | 276 | 15 | 8 | 7 | 1 | 0 | 0 | 160
23-0133489 | Nevada | BRUNSWICK 1107 | BRUNSWICK 1107357568 | Animal | 2023-10-28 08:18 | 10/24 - 10/30 | 2023-10-28 09:05 | 44.6047 | FTS | 57094 | 1280 | 69 | 38 | 13 | 1 | 0 | 0 | 47
23-0133475 | Shasta | VOLTA 1101 | VOLTA 1101507876 | 3rd Party | 2023-10-28 06:55 | 10/24 - 10/30 | 2023-10-28 09:16 | 141 | HLT | 141 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 141
23-0133414 | San Mateo | WOODSIDE 1104 | WOODSIDE 11049116 | Animal | 2023-10-27 17:16 | 10/24 - 10/30 | 2023-10-28 09:17 | 248.2843 | FTS | 637594 | 2568 | 93 | 68 | 34 | 6 | 0 | 0 | 961
23-0133439 | Marin | SAN RAFAEL 1104 | SAN RAFAEL 1104802 | Unknown Cause | 2023-10-27 20:24 | 10/24 - 10/30 | 2023-10-28 09:57 | 746.0483 | FTS | 1051182 | 1409 | 62 | 40 | 15 | 3 | 0 | 0 | 813
23-0133491 | Contra Costa | CLAYTON 2215 | CLAYTON 2215CB | Vegetation | 2023-10-28 08:41 | 10/24 - 10/30 | 2023-10-28 11:59 | 144.0142 | FTS | 651088 | 4521 | 343 | 239 | 65 | 6 | 0 | 0 | 198
23-0133521 | Marin | SAN RAFAEL 1104 | SAN RAFAEL 1104802 | Unknown Cause | 2023-10-28 10:30 | 10/24 - 10/30 | 2023-10-28 13:09 | 159 | FTS | 224031 | 1409 | 62 | 40 | 15 | 3 | 0 | 0 | 159
23-0133460 | Marin | STAFFORD 1102 | STAFFORD 11021202 | 3rd Party | 2023-10-28 00:57 | 10/24 - 10/30 | 2023-10-28 13:45 | 207.9623 | FTS | 11022 | 53 | 1 | 1 | 1 | 0 | 0 | 0 | 768
23-0133492 | Contra Costa | CLAYTON 2217 | CLAYTON 2217CB | Equipment Failure/Involved | 2023-10-28 08:41 | 10/24 - 10/30 | 2023-10-28 13:47 | 263.1466 | FTS | 1403361 | 5333 | 381 | 256 | 60 | 7 | 0 | 0 | 306
23-0133567 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015144 | Unknown Cause | 2023-10-28 14:10 | 10/24 - 10/30 | 2023-10-28 18:00 | 230 | FTS | 34270 | 149 | 11 | 8 | 5 | 0 | 0 | 0 | 230
23-0133640 | Placer | WISE 1102 | WISE 11022234 | Unknown Cause | 2023-10-28 22:28 | 10/24 - 10/30 | 2023-10-29 08:42 | 259.7463 | FTS | 69612 | 268 | 21 | 14 | 0 | 0 | 0 | 2 | 614
23-0133597 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Vegetation | 2023-10-28 17:43 | 10/24 - 10/30 | 2023-10-29 09:06 | 918.7877 | FTS | 822315 | 895 | 66 | 45 | 16 | 0 | 0 | 0 | 923
23-0133646 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018884 | Vegetation | 2023-10-29 01:24 | 10/24 - 10/30 | 2023-10-29 09:25 | 475.0408 | FTS | 162939 | 343 | 20 | 11 | 28 | 1 | 0 | 0 | 481
23-0133563 | Plumas | GANSNER 1101 | GANSNER 110152664 | Equipment Failure/Involved | 2023-10-28 13:36 | 10/24 - 10/30 | 2023-10-29 11:12 | 204.0701 | FTS | 460178 | 2255 | 105 | 76 | 48 | 17 | 1 | 0 | 1296
23-0133582 | Monterey | LAURELES 1111 | LAURELES 11112020 | Unknown Cause | 2023-10-28 15:47 | 10/24 - 10/30 | 2023-10-29 11:12 | 1165 | FTS | 976270 | 838 | 29 | 18 | 26 | 0 | 0 | 0 | 1165
23-0133655 | Contra Costa | RESEARCH 2101 | RESEARCH 2101D576R | Unknown Cause | 2023-10-29 06:21 | 10/24 - 10/30 | 2023-10-29 12:30 | 369 | FTS | 149814 | 406 | 10 | 5 | 9 | 2 | 0 | 0 | 369
23-0133637 | San Benito | SAN BENITO 2104 | SAN BENITO 2104785888 | 3rd Party | 2023-10-28 22:27 | 10/24 - 10/30 | 2023-10-29 12:34 | 116.7123 | FTS | 150909 | 1293 | 98 | 81 | 23 | 3 | 0 | 3 | 847
23-0133668 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | Unknown Cause | 2023-10-29 08:40 | 10/24 - 10/30 | 2023-10-29 12:34 | 184.9056 | FTS | 95966 | 519 | 35 | 22 | 14 | 4 | 0 | 7 | 234
23-0133664 | Marin | COTATI 1102 | COTATI 1102282 | 3rd Party | 2023-10-29 07:59 | 10/24 - 10/30 | 2023-10-29 13:29 | 324.0465 | FTS | 41802 | 129 | 4 | 4 | 2 | 0 | 0 | 1 | 330
23-0133686 | Contra Costa | LAKEWOOD 2227 | LAKEWOOD 2227W503R | Vegetation | 2023-10-29 11:07 | 10/24 - 10/30 | 2023-10-29 13:31 | 129.1944 | FTS | 165498 | 1281 | 58 | 41 | 10 | 0 | 1 | 0 | 144
23-0133634 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101806 | Equipment Failure/Involved | 2023-10-28 21:57 | 10/24 - 10/30 | 2023-10-29 13:54 | 957 | FTS | 79431 | 83 | 3 | 2 | 1 | 0 | 0 | 0 | 957
23-0133679 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210912392 | Animal | 2023-10-29 10:34 | 10/24 - 10/30 | 2023-10-29 14:20 | 164.4211 | FTS | 3124 | 19 | 1 | 1 | 1 | 0 | 0 | 1 | 226
23-0133671 | Alameda | OAKLAND K 1104 | OAKLAND K 1104CB | Unknown Cause | 2023-10-29 09:17 | 10/24 - 10/30 | 2023-10-29 15:09 | 337.4376 | FTS | 792641 | 2349 | 99 | 73 | 53 | 6 | 0 | 0 | 352
23-0133606 | Colusa | MAXWELL 1105 | MAXWELL 1105910362 | Unknown Cause | 2023-10-28 18:34 | 10/24 - 10/30 | 2023-10-29 15:34 | 326.5714 | FTS | 41148 | 126 | 2 | 1 | 1 | 0 | 0 | 0 | 1260
23-0133652 | San Joaquin | AVENA 1702 | AVENA 17025494 | Equipment Failure/Involved | 2023-10-29 05:02 | 10/24 - 10/30 | 2023-10-29 15:54 | 184.6739 | FTS | 67960 | 368 | 19 | 14 | 8 | 2 | 0 | 0 | 652
23-0133680 | Napa | SILVERADO 2102 | SILVERADO 210234959 | Vegetation | 2023-10-29 10:41 | 10/24 - 10/30 | 2023-10-29 17:06 | 351.6745 | FTS | 74555 | 212 | 2 | 2 | 4 | 0 | 0 | 1 | 385
23-0133722 | Santa Clara | HICKS 2103 | HICKS 2103XR248 | Animal | 2023-10-29 16:03 | 10/24 - 10/30 | 2023-10-29 17:13 | 70 | FTS | 29190 | 417 | 25 | 16 | 5 | 0 | 0 | 0 | 70
23-0133715 | San Benito | PANOCHE 1103 | PANOCHE 1103107270 | Equipment Failure/Involved | 2023-10-29 14:22 | 10/24 - 10/30 | 2023-10-29 20:44 | 382 | FTS | 58064 | 152 | 1 | 1 | 6 | 1 | 0 | 0 | 382
23-0133740 | Placer | FORESTHILL 1101 | FORESTHILL 110150486 | Unknown Cause | 2023-10-29 19:06 | 10/24 - 10/30 | 2023-10-29 22:28 | 202 | FTS | 186244 | 922 | 97 | 64 | 10 | 0 | 0 | 0 | 202
23-0133725 | Contra Costa | KIRKER 2105 | KIRKER 2105A536R | Equipment Failure/Involved | 2023-10-29 16:25 | 10/24 - 10/30 | 2023-10-30 02:52 | 75.6388 | FTS | 166481 | 2201 | 265 | 182 | 18 | 1 | 0 | 0 | 627
23-0133772 | Monterey | JOLON 1102 | JOLON 11027002 | Unknown Cause | 2023-10-29 23:33 | 10/24 - 10/30 | 2023-10-30 03:09 | 216 | FTS | 29808 | 138 | 7 | 5 | 3 | 2 | 0 | 3 | 216
23-0133763 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Unknown Cause | 2023-10-29 23:49 | 10/24 - 10/30 | 2023-10-30 03:21 | 141.4406 | FTS | 235640 | 1666 | 174 | 115 | 17 | 2 | 0 | 0 | 212
23-0133802 | Plumas | GANSNER 1101 | GANSNER 110152664 | Unknown Cause | 2023-10-30 07:37 | 10/24 - 10/30 | 2023-10-30 08:23 | 46 | FTS | 920 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 46
23-0133842 | Nevada | HIGGINS 1103 | HIGGINS 110350072 | Unknown Cause | 2023-10-30 09:04 | 10/24 - 10/30 | 2023-10-30 11:35 | 151 | FTS | 97999 | 649 | 49 | 30 | 3 | 0 | 0 | 11 | 151
23-0133821 | Tuolumne | MIWUK 1701 | MIWUK 1701953336 | Company Initiated | 2023-10-30 08:30 | 10/24 - 10/30 | 2023-10-30 11:59 | 209 | FTS | 185383 | 887 | 43 | 32 | 8 | 1 | 0 | 0 | 209
23-0133957 | El Dorado | PLACERVILLE 1112 | PLACERVILLE 111219712 | Animal | 2023-10-30 11:23 | 10/24 - 10/30 | 2023-10-30 12:40 | 77 | FTS | 37037 | 481 | 54 | 40 | 8 | 0 | 1 | 2 | 77
23-0134043 | Tuolumne | MIWUK 1701 | MIWUK 1701953336 | Company Initiated | 2023-10-30 13:05 | 10/24 - 10/30 | 2023-10-30 14:05 | 60 | FTS | 53220 | 887 | 43 | 32 | 8 | 1 | 0 | 0 | 60
23-0128851 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018912 | Company Initiated | 2023-10-30 14:14 | 10/24 - 10/30 | 2023-10-30 14:24 | 10 | FTS | 460 | 46 | 2 | 0 | 1 | 0 | 0 | 0 | 10
23-0133774 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Unknown Cause | 2023-10-30 03:35 | 10/24 - 10/30 | 2023-10-30 15:42 | 354.7643 | FTS | 918130 | 2588 | 174 | 115 | 17 | 2 | 0 | 0 | 727
23-0134108 | San Luis Obispo | ATASCADERO 1101 | ATASCADERO 1101A50 | Company Initiated | 2023-10-30 16:08 | 10/24 - 10/30 | 2023-10-30 16:22 | 14 | FTS | 3150 | 225 | 15 | 9 | 2 | 0 | 0 | 0 | 14
23-0134096 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Animal | 2023-10-30 15:11 | 10/24 - 10/30 | 2023-10-30 16:35 | 84 | FTS | 10668 | 127 | 2 | 2 | 1 | 0 | 0 | 0 | 84
23-0134197 | Tehama | COTTONWOOD 1103 | COTTONWOOD 1103389928 | Unknown Cause | 2023-10-31 02:36 | 10/31 - 11/6 | 2023-10-31 04:10 | 94 | FTS | 940 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 94
23-0134188 | Napa | MONTICELLO 1101 | MONTICELLO 110165454 | Unknown Cause | 2023-10-30 23:36 | 10/31 - 11/6 | 2023-10-31 09:19 | 582.1128 | FTS | 77421 | 133 | 8 | 5 | 1 | 0 | 0 | 0 | 583
23-0134258 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102604702 | Animal | 2023-10-31 09:41 | 10/31 - 11/6 | 2023-10-31 10:16 | 35 | FTS | 70630 | 2018 | 226 | 160 | 22 | 9 | 0 | 0 | 35
23-0134306 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102501650 | Equipment Failure/Involved | 2023-10-31 11:15 | 10/31 - 11/6 | 2023-10-31 12:27 | 42 | HLT | 1722 | 41 | 2 | 2 | 1 | 0 | 0 | 0 | 72
23-0134261 | Kern | LAMONT 1104 | LAMONT 11043855 | 3rd Party | 2023-10-31 09:41 | 10/31 - 11/6 | 2023-10-31 13:45 | 91.1111 | HLT | 8200 | 90 | 1 | 0 | 3 | 0 | 0 | 0 | 244
23-0134378 | Contra Costa | KIRKER 2104 | KIRKER 210475648 | Animal | 2023-10-31 14:39 | 10/31 - 11/6 | 2023-10-31 16:00 | 81 | FTS | 113724 | 1404 | 163 | 111 | 14 | 2 | 0 | 0 | 81
23-0134419 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21011102 | Company Initiated | 2023-10-31 16:27 | 10/31 - 11/6 | 2023-10-31 17:11 | 44 | FTS | 35112 | 798 | 93 | 62 | 10 | 0 | 0 | 13 | 44
23-0134485 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-01 02:09 | 10/31 - 11/6 | 2023-11-01 04:50 | 161 | FTS | 9177 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 161
23-0134490 | Nevada | BRUNSWICK 1102 | BRUNSWICK 1102940 | Animal | 2023-11-01 03:48 | 10/31 - 11/6 | 2023-11-01 05:57 | 129 | FTS | 68112 | 528 | 4 | 3 | 11 | 0 | 0 | 3 | 129
23-0134496 | Butte | WYANDOTTE 1106 | WYANDOTTE 110641650 | 3rd Party | 2023-11-01 05:59 | 10/31 - 11/6 | 2023-11-01 09:01 | 87.6593 | FTS | 15954 | 182 | 14 | 9 | 1 | 0 | 0 | 0 | 182
23-0134520 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21037062 | Unknown Cause | 2023-11-01 07:21 | 10/31 - 11/6 | 2023-11-01 09:15 | 114 | FTS | 5700 | 50 | 1 | 1 | 1 | 0 | 0 | 0 | 114
23-0134581 | Placer | WISE 1102 | WISE 11022054 | Unknown Cause | 2023-11-01 09:09 | 10/31 - 11/6 | 2023-11-01 10:39 | 90 | FTS | 19710 | 219 | 18 | 11 | 2 | 0 | 0 | 6 | 90
23-0134482 | Kern | CUYAMA 1103 | CUYAMA 1103622728 | 3rd Party | 2023-11-01 00:21 | 10/31 - 11/6 | 2023-11-01 10:48 | 627 | FTS | 33858 | 54 | 0 | 0 | 4 | 0 | 0 | 0 | 627
23-0134609 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 1103351084 | Animal | 2023-11-01 09:59 | 10/31 - 11/6 | 2023-11-01 11:02 | 36.8141 | FTS | 13069 | 355 | 15 | 11 | 4 | 0 | 0 | 0 | 63
23-0134199 | San Benito | SAN BENITO 2104 | SAN BENITO 2104785888 | 3rd Party | 2023-10-31 04:38 | 10/31 - 11/6 | 2023-11-01 13:15 | 219.5228 | FTS | 283843 | 1293 | 101 | 84 | 23 | 3 | 0 | 3 | 1957
23-0134489 | Butte | SYCAMORE CREEK 1111 | SYCAMORE CREEK 11112602 | Equipment Failure/Involved | 2023-11-01 03:27 | 10/31 - 11/6 | 2023-11-01 15:22 | 82.8298 | FTS | 3893 | 47 | 0 | 0 | 9 | 0 | 0 | 0 | 715
23-0126234 | Tuolumne | CURTIS 1704 | CURTIS 170411290 | Unknown Cause | 2023-11-01 11:41 | 10/31 - 11/6 | 2023-11-01 16:50 | 304.9626 | FTS | 220183 | 722 | 81 | 64 | 8 | 4 | 0 | 3 | 309
23-0134904 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 110192870 | Unknown Cause | 2023-11-01 17:11 | 10/31 - 11/6 | 2023-11-01 18:45 | 34.5357 | FTS | 23208 | 672 | 37 | 29 | 10 | 0 | 0 | 0 | 94
23-0134819 | Mendocino | LAYTONVILLE 1102 | LAYTONVILLE 1102572 | Equipment Failure/Involved | 2023-11-01 15:05 | 10/31 - 11/6 | 2023-11-01 22:55 | 100.4297 | FTS | 25710 | 256 | 17 | 12 | 9 | 1 | 0 | 0 | 470
23-0134945 | Nevada | NARROWS 2105 | NARROWS 21052426 | Unknown Cause | 2023-11-01 22:18 | 10/31 - 11/6 | 2023-11-02 00:01 | 103 | FTS | 3502 | 34 | 5 | 3 | 0 | 0 | 0 | 0 | 103
23-0134951 | Amador | WEST POINT 1101 | WEST POINT 110112256 | 3rd Party | 2023-11-01 23:07 | 10/31 - 11/6 | 2023-11-02 03:21 | 208.1066 | FTS | 370846 | 1782 | 158 | 122 | 15 | 0 | 0 | 2 | 254
23-0134965 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Equipment Failure/Involved | 2023-11-02 02:40 | 10/31 - 11/6 | 2023-11-02 05:59 | 69.8451 | FTS | 116362 | 1666 | 179 | 119 | 17 | 2 | 0 | 0 | 199
23-0135067 | Mendocino | HOPLAND 1101 | HOPLAND 1101154790 | Company Initiated | 2023-11-02 09:11 | 10/31 - 11/6 | 2023-11-02 09:39 | 28 | FTS | 11872 | 424 | 39 | 31 | 6 | 0 | 0 | 0 | 28
23-0134915 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Unknown Cause | 2023-11-01 18:32 | 10/31 - 11/6 | 2023-11-02 09:49 | 538.2294 | FTS | 91499 | 170 | 12 | 7 | 13 | 0 | 0 | 1 | 917
23-0134926 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121204 | 3rd Party | 2023-11-01 18:25 | 10/31 - 11/6 | 2023-11-02 10:36 | 971 | FTS | 24275 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 971
23-0135111 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-02 09:59 | 10/31 - 11/6 | 2023-11-02 12:10 | 131 | FTS | 7467 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 131
23-0135172 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | Animal | 2023-11-02 11:05 | 10/31 - 11/6 | 2023-11-02 13:04 | 119 | FTS | 34510 | 290 | 7 | 3 | 14 | 19 | 0 | 0 | 119
23-0135266 | Contra Costa | VALLEY VIEW 1103 | VALLEY VIEW 1106P176 | Company Initiated | 2023-11-02 12:53 | 10/31 - 11/6 | 2023-11-02 13:27 | 34 | FTS | 782 | 23 | 1 | 1 | 1 | 0 | 0 | 0 | 34
23-0135178 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Unknown Cause | 2023-11-02 11:08 | 10/31 - 11/6 | 2023-11-02 13:44 | 156 | FTS | 23088 | 148 | 12 | 7 | 1 | 0 | 0 | 1 | 156
23-0135049 | Mendocino | COVELO 1101 | COVELO 1101562360 | 3rd Party | 2023-11-02 08:49 | 10/31 - 11/6 | 2023-11-02 19:54 | 146.0039 | FTS | 75630 | 518 | 24 | 20 | 2 | 3 | 0 | 0 | 665
23-0135444 | Nevada | NARROWS 2105 | NARROWS 21052426 | Company Initiated | 2023-11-03 06:36 | 10/31 - 11/6 | 2023-11-03 07:02 | 26 | FTS | 884 | 34 | 5 | 3 | 0 | 0 | 0 | 0 | 26
23-0135430 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-03 05:42 | 10/31 - 11/6 | 2023-11-03 08:05 | 143 | FTS | 8151 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 143
23-0135626 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210985766 | Company Initiated | 2023-11-03 11:32 | 10/31 - 11/6 | 2023-11-03 11:51 | 19 | FTS | 4940 | 260 | 13 | 10 | 2 | 0 | 0 | 10 | 19
23-0135650 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Company Initiated | 2023-11-03 12:36 | 10/31 - 11/6 | 2023-11-03 12:42 | 6 | FTS | 1254 | 209 | 3 | 1 | 9 | 0 | 0 | 0 | 6
23-0135648 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Company Initiated | 2023-11-03 12:16 | 10/31 - 11/6 | 2023-11-03 13:10 | 54 | FTS | 8046 | 149 | 6 | 5 | 1 | 0 | 0 | 0 | 54
23-0135514 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Equipment Failure/Involved | 2023-11-03 09:05 | 10/31 - 11/6 | 2023-11-03 14:21 | 62.3295 | FTS | 21566 | 346 | 5 | 5 | 10 | 0 | 0 | 0 | 316
23-0135588 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Company Initiated | 2023-11-03 08:18 | 10/31 - 11/6 | 2023-11-03 14:31 | 50.8772 | FTS | 93665 | 1841 | 132 | 99 | 26 | 5 | 0 | 2 | 373
23-0135730 | Fresno | CANTUA 1103 | CANTUA 11039900 | Equipment Failure/Involved | 2023-11-03 15:37 | 10/31 - 11/6 | 2023-11-03 16:59 | 77.2881 | FTS | 22800 | 295 | 4 | 3 | 7 | 1 | 0 | 0 | 82
23-0135733 | El Dorado | DIAMOND SPRINGS 1107 | DIAMOND SPRINGS 1107CB | Unknown Cause | 2023-11-03 15:34 | 10/31 - 11/6 | 2023-11-03 17:19 | 77.2727 | FTS | 142800 | 1848 | 145 | 98 | 35 | 11 | 0 | 7 | 105
23-0135428 | Napa | SILVERADO 2102 | SILVERADO 2102285782 | Equipment Failure/Involved | 2023-11-03 01:40 | 10/31 - 11/6 | 2023-11-03 18:20 | 430.9333 | FTS | 45248 | 105 | 1 | 1 | 1 | 0 | 0 | 0 | 1000
23-0135734 | Santa Barbara | ZACA 1101 | ZACA 1101CB | Unknown Cause | 2023-11-03 15:42 | 10/31 - 11/6 | 2023-11-03 18:25 | 146.092 | FTS | 149306 | 1022 | 21 | 16 | 19 | 13 | 0 | 0 | 163
23-0135753 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | 3rd Party | 2023-11-03 16:15 | 10/31 - 11/6 | 2023-11-03 19:32 | 119.3909 | FTS | 327131 | 2740 | 251 | 185 | 40 | 8 | 0 | 17 | 197
23-0135801 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Company Initiated | 2023-11-03 19:44 | 10/31 - 11/6 | 2023-11-03 23:15 | 55.5136 | FTS | 171204 | 3084 | 215 | 162 | 43 | 1 | 0 | 4 | 211
23-0135830 | Tulare | OROSI 1102 | OROSI 1102CB | Unknown Cause | 2023-11-03 23:32 | 10/31 - 11/6 | 2023-11-04 01:15 | 103 | FTS | 37389 | 363 | 6 | 5 | 1 | 0 | 0 | 0 | 103
23-0135803 | Nevada | NARROWS 2105 | NARROWS 21052748 | Vegetation | 2023-11-03 19:56 | 10/31 - 11/6 | 2023-11-04 02:51 | 89.7915 | FTS | 80543 | 897 | 68 | 45 | 8 | 0 | 0 | 4 | 415
23-0135837 | Mariposa | MARIPOSA 2102 | MARIPOSA 21021960 | Animal | 2023-11-04 03:36 | 10/31 - 11/6 | 2023-11-04 05:37 | 104.5255 | FTS | 100240 | 959 | 67 | 52 | 18 | 5 | 0 | 1 | 121
23-0135840 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-04 05:31 | 10/31 - 11/6 | 2023-11-04 09:42 | 251 | FTS | 14307 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 251
23-0135861 | Shasta | DESCHUTES 1104 | DESCHUTES 1104421598 | Unknown Cause | 2023-11-04 08:41 | 10/31 - 11/6 | 2023-11-04 11:12 | 62.987 | FTS | 29100 | 462 | 37 | 23 | 4 | 0 | 0 | 4 | 151
23-0135897 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210595050 | Company Initiated | 2023-11-04 12:11 | 10/31 - 11/6 | 2023-11-04 12:26 | 15 | FTS | 555 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 15
23-0135877 | Monterey | SOLEDAD 2104 | SOLEDAD 21027008 | Unknown Cause | 2023-11-04 10:12 | 10/31 - 11/6 | 2023-11-04 12:30 | 138 | FTS | 11040 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 138
23-0135875 | Napa | SILVERADO 2104 | SILVERADO 210478268 | Unknown Cause | 2023-11-04 09:57 | 10/31 - 11/6 | 2023-11-04 15:46 | 249.2414 | FTS | 130104 | 522 | 37 | 28 | 17 | 2 | 2 | 2 | 349
23-0135925 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Company Initiated | 2023-11-04 15:27 | 10/31 - 11/6 | 2023-11-04 16:07 | 40 | FTS | 6120 | 153 | 7 | 6 | 1 | 0 | 0 | 0 | 40
23-0135901 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | Unknown Cause | 2023-11-04 12:44 | 10/31 - 11/6 | 2023-11-04 17:14 | 270 | FTS | 174690 | 647 | 66 | 44 | 4 | 0 | 0 | 14 | 270
23-0135938 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21069712 | Animal | 2023-11-04 18:06 | 10/31 - 11/6 | 2023-11-04 19:51 | 92.7231 | FTS | 144648 | 1560 | 116 | 91 | 44 | 9 | 0 | 1 | 105
23-0135852 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | Equipment Failure/Involved | 2023-11-04 08:04 | 10/31 - 11/6 | 2023-11-04 20:40 | 298.0614 | FTS | 33979 | 114 | 3 | 2 | 9 | 2 | 0 | 0 | 756
23-0135928 | Nevada | HIGGINS 1110 | HIGGINS 11102408 | Equipment Failure/Involved | 2023-11-04 16:01 | 10/31 - 11/6 | 2023-11-04 23:38 | 427.7194 | FTS | 192046 | 449 | 43 | 28 | 4 | 0 | 0 | 7 | 457
23-0135907 | Butte | PARADISE 1103 | PARADISE 11032486 | 3rd Party | 2023-11-04 13:45 | 10/31 - 11/6 | 2023-11-05 01:00 | 40.417 | FTS | 34799 | 861 | 70 | 50 | 12 | 0 | 0 | 4 | 675
23-0135967 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | Unknown Cause | 2023-11-04 23:17 | 10/31 - 11/6 | 2023-11-05 01:32 | 135 | FTS | 65205 | 483 | 45 | 32 | 5 | 0 | 0 | 0 | 135
23-0135991 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-05 08:57 | 10/31 - 11/6 | 2023-11-05 10:17 | 80 | FTS | 4560 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 80
23-0136004 | Mendocino | CALPELLA 1102 | CALPELLA 1102421412 | Unknown Cause | 2023-11-05 11:22 | 10/31 - 11/6 | 2023-11-05 12:52 | 90 | FTS | 7830 | 87 | 4 | 3 | 3 | 0 | 0 | 0 | 90
23-0135999 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015144 | Unknown Cause | 2023-11-05 10:22 | 10/31 - 11/6 | 2023-11-05 13:15 | 173 | FTS | 25777 | 149 | 11 | 8 | 5 | 0 | 0 | 0 | 173
23-0135972 | Contra Costa | LONE TREE 2105 | LONE TREE 2105CB | 3rd Party | 2023-11-05 01:00 | 10/31 - 11/6 | 2023-11-05 15:34 | 181.1397 | FTS | 477303 | 2635 | 191 | 135 | 43 | 5 | 1 | 0 | 934
23-0136022 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101890 | Vegetation | 2023-11-05 14:59 | 10/31 - 11/6 | 2023-11-05 16:50 | 104.6471 | FTS | 17790 | 170 | 4 | 4 | 1 | 0 | 0 | 0 | 111
23-0136013 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062796 | Equipment Failure/Involved | 2023-11-05 14:36 | 10/31 - 11/6 | 2023-11-05 19:16 | 80.0341 | FTS | 119571 | 1494 | 134 | 93 | 15 | 0 | 0 | 7 | 280
23-0135969 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104597930 | 3rd Party | 2023-11-04 23:23 | 10/31 - 11/6 | 2023-11-05 19:25 | 115.9088 | FTS | 143611 | 1239 | 34 | 25 | 12 | 3 | 0 | 0 | 1262
23-0136040 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q10 | Unknown Cause | 2023-11-05 20:03 | 10/31 - 11/6 | 2023-11-05 22:29 | 146 | FTS | 43946 | 301 | 20 | 16 | 2 | 0 | 0 | 5 | 146
23-0136078 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210510214 | Vegetation | 2023-11-05 23:05 | 10/31 - 11/6 | 2023-11-06 01:03 | 69.4351 | FTS | 136926 | 1972 | 196 | 158 | 29 | 1 | 0 | 6 | 118
23-0136060 | El Dorado | CLARKSVILLE 2103 | CLARKSVILLE 2103593454 | Unknown Cause | 2023-11-05 21:33 | 10/31 - 11/6 | 2023-11-06 01:48 | 255 | FTS | 95880 | 376 | 37 | 32 | 13 | 4 | 0 | 14 | 255
23-0136096 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-06 01:37 | 10/31 - 11/6 | 2023-11-06 02:47 | 70 | FTS | 3990 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 70
23-0136097 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210152456 | Company Initiated | 2023-11-06 01:25 | 10/31 - 11/6 | 2023-11-06 03:01 | 78.7063 | FTS | 80123 | 1018 | 27 | 18 | 54 | 1 | 0 | 0 | 96
23-0136105 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210119612 | Unknown Cause | 2023-11-06 04:59 | 10/31 - 11/6 | 2023-11-06 05:25 | 26 | FTS | 33644 | 1294 | 44 | 29 | 80 | 1 | 0 | 0 | 26
23-0135980 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Equipment Failure/Involved | 2023-11-05 05:34 | 10/31 - 11/6 | 2023-11-06 05:49 | 287.1295 | FTS | 447922 | 1560 | 218 | 165 | 25 | 0 | 0 | 0 | 1455
23-0136110 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101586340 | Unknown Cause | 2023-11-06 06:16 | 10/31 - 11/6 | 2023-11-06 08:05 | 86.6901 | FTS | 61550 | 710 | 64 | 43 | 17 | 2 | 0 | 0 | 109
23-0136107 | Mendocino | COVELO 1101 | COVELO 110137328 | Unknown Cause | 2023-11-06 05:27 | 10/31 - 11/6 | 2023-11-06 08:31 | 150.9955 | FTS | 168360 | 1115 | 58 | 43 | 23 | 16 | 0 | 0 | 184
23-0136032 | Shasta | OREGON TRAIL 1103 | OREGON TRAIL 110335002 | Unknown Cause | 2023-11-05 18:16 | 10/31 - 11/6 | 2023-11-06 09:45 | 612.7423 | FTS | 658698 | 1075 | 100 | 74 | 19 | 3 | 0 | 1 | 929
23-0136198 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110170 | Unknown Cause | 2023-11-06 09:51 | 10/31 - 11/6 | 2023-11-06 10:22 | 31 | FTS | 5611 | 181 | 13 | 6 | 6 | 0 | 0 | 0 | 31
23-0136038 | Mendocino | WILLITS 1103 | WILLITS 1103564506 | Unknown Cause | 2023-11-05 19:32 | 10/31 - 11/6 | 2023-11-06 10:41 | 193.9391 | FTS | 22303 | 115 | 11 | 6 | 4 | 0 | 0 | 1 | 909
23-0136172 | San Benito | HOLLISTER 2102 | HOLLISTER 2102113634 | Unknown Cause | 2023-11-06 09:07 | 10/31 - 11/6 | 2023-11-06 10:48 | 50.011 | FTS | 4551 | 91 | 2 | 0 | 3 | 0 | 0 | 0 | 101
23-0136081 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | Equipment Failure/Involved | 2023-11-06 00:01 | 10/31 - 11/6 | 2023-11-06 11:14 | 187.946 | FTS | 668336 | 3556 | 355 | 253 | 51 | 8 | 0 | 19 | 673
23-0136283 | Mendocino | UKIAH 1114 | UKIAH 1114408 | 3rd Party | 2023-11-06 12:07 | 10/31 - 11/6 | 2023-11-06 12:45 | 38 | FTS | 12274 | 323 | 17 | 9 | 8 | 1 | 0 | 0 | 38
23-0136291 | Tuolumne | TAR FLAT 0402 | TAR FLAT 04023144 | Company Initiated | 2023-11-06 12:31 | 10/31 - 11/6 | 2023-11-06 12:47 | 16 | FTS | 2224 | 139 | 9 | 7 | 1 | 0 | 0 | 0 | 16
23-0136098 | Monterey | SOLEDAD 2105 | SOLEDAD 2101107872 | Unknown Cause | 2023-11-06 03:21 | 10/31 - 11/6 | 2023-11-06 12:52 | 521.9091 | FTS | 17223 | 33 | 1 | 1 | 0 | 0 | 0 | 0 | 571
23-0136188 | Napa | PUEBLO 2103 | PUEBLO 210398394 | Unknown Cause | 2023-11-06 09:29 | 10/31 - 11/6 | 2023-11-06 13:29 | 211.6867 | FTS | 482434 | 2279 | 342 | 244 | 60 | 11 | 0 | 2 | 240
23-0136393 | Shasta | BURNEY 1101 | BURNEY 11011322 | Environmental/External | 2023-11-06 14:44 | 10/31 - 11/6 | 2023-11-06 15:24 | 40 | FTS | 2680 | 67 | 3 | 3 | 0 | 0 | 0 | 0 | 40
23-0136083 | Alameda | NORTH DUBLIN 2103 | NORTH DUBLIN 2103CB | Equipment Failure/Involved | 2023-11-06 00:12 | 11/7 - 11/13 | 2023-11-06 16:25 | 79.0596 | FTS | 395377 | 5001 | 189 | 137 | 50 | 6 | 0 | 0 | 973
23-0136451 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | Unknown Cause | 2023-11-06 17:15 | 11/7 - 11/13 | 2023-11-06 17:46 | 26.6365 | FTS | 72984 | 2740 | 251 | 185 | 40 | 8 | 0 | 17 | 31
23-0136467 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029690 | Equipment Failure/Involved | 2023-11-06 19:54 | 11/7 - 11/13 | 2023-11-07 10:25 | 773.1422 | FTS | 532695 | 689 | 19 | 12 | 8 | 0 | 0 | 0 | 871
23-0136603 | Tehama | RED BLUFF 1101 | RED BLUFF 11011556 | Unknown Cause | 2023-11-07 08:48 | 11/7 - 11/13 | 2023-11-07 11:03 | 109.625 | FTS | 52620 | 480 | 55 | 38 | 3 | 0 | 0 | 0 | 135
23-0136462 | Mendocino | UKIAH 1114 | UKIAH 1114408 | Unknown Cause | 2023-11-06 18:53 | 11/7 - 11/13 | 2023-11-07 13:00 | 154.0588 | FTS | 49761 | 323 | 17 | 9 | 8 | 1 | 0 | 0 | 1087
23-0136517 | Calaveras | CORRAL 1102 | CORRAL 1102CB | 3rd Party | 2023-11-07 03:33 | 11/7 - 11/13 | 2023-11-07 14:19 | 189.5992 | FTS | 787595 | 4154 | 384 | 250 | 57 | 0 | 0 | 5 | 646
23-0136786 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-07 12:45 | 11/7 - 11/13 | 2023-11-07 15:23 | 158 | FTS | 9006 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 158
23-0136908 | Monterey | SOLEDAD 2105 | SOLEDAD 2101107872 | Company Initiated | 2023-11-07 22:39 | 11/7 - 11/13 | 2023-11-07 23:06 | 27 | FTS | 891 | 33 | 1 | 1 | 0 | 0 | 0 | 0 | 27
23-0136854 | Mariposa | MARIPOSA 2102 | MARIPOSA 21021960 | Company Initiated | 2023-11-07 16:22 | 11/7 - 11/13 | 2023-11-07 23:53 | 21.1783 | FTS | 20310 | 959 | 67 | 52 | 18 | 5 | 0 | 1 | 451
23-0136885 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-07 19:17 | 11/7 - 11/13 | 2023-11-08 00:08 | 291 | FTS | 16587 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 291
23-0136628 | Santa Cruz | CAMP EVERS 2104 | CAMP EVERS 2106257600 | Equipment Failure/Involved | 2023-11-07 09:21 | 11/7 - 11/13 | 2023-11-08 03:00 | 335.6296 | FTS | 812895 | 2422 | 222 | 178 | 44 | 7 | 0 | 15 | 1059
23-0136924 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101Y52 | Unknown Cause | 2023-11-08 06:20 | 11/7 - 11/13 | 2023-11-08 08:56 | 156 | FTS | 29796 | 191 | 1 | 1 | 25 | 0 | 0 | 0 | 156
23-0136800 | Placer | HALSEY 1102 | HALSEY 110239104 | Unknown Cause | 2023-11-07 14:04 | 11/7 - 11/13 | 2023-11-08 09:23 | 397.4562 | FTS | 358108 | 901 | 87 | 60 | 19 | 7 | 0 | 12 | 1159
23-0137152 | Sonoma | SONOMA 1105 | SONOMA 1105138 | Company Initiated | 2023-11-08 12:43 | 11/7 - 11/13 | 2023-11-08 13:03 | 18.3975 | FTS | 11848 | 644 | 32 | 22 | 7 | 0 | 0 | 5 | 20
23-0137117 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 1103N58 | Unknown Cause | 2023-11-08 11:23 | 11/7 - 11/13 | 2023-11-08 13:38 | 135 | FTS | 350325 | 2595 | 158 | 120 | 40 | 1 | 0 | 5 | 135
23-0137071 | San Joaquin | CORRAL 1101 | CORRAL 1101173174 | 3rd Party | 2023-11-08 10:52 | 11/7 - 11/13 | 2023-11-08 13:46 | 82.6667 | FTS | 248 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 174
23-0137200 | Amador | OLETA 1101 | OLETA 1101296804 | Company Initiated | 2023-11-08 14:18 | 11/7 - 11/13 | 2023-11-08 15:10 | 52 | FTS | 55796 | 1073 | 60 | 41 | 22 | 4 | 0 | 1 | 52
23-0137236 | Tuolumne | CURTIS 1705 | CURTIS 17058110 | Company Initiated | 2023-11-08 15:43 | 11/7 - 11/13 | 2023-11-08 15:57 | 14 | FTS | 5600 | 400 | 31 | 25 | 11 | 2 | 0 | 0 | 14
23-0137222 | Nevada | NARROWS 2102 | NARROWS 21052426 | Animal | 2023-11-08 15:09 | 11/7 - 11/13 | 2023-11-08 16:27 | 61.0493 | FTS | 112697 | 1846 | 152 | 83 | 22 | 4 | 0 | 16 | 78
23-0137223 | Santa Barbara | ZACA 1101 | ZACA 1101CB | Unknown Cause | 2023-11-08 15:13 | 11/7 - 11/13 | 2023-11-08 16:31 | 78 | FTS | 79716 | 1022 | 21 | 16 | 19 | 13 | 0 | 0 | 78
23-0137255 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Unknown Cause | 2023-11-08 17:14 | 11/7 - 11/13 | 2023-11-08 21:48 | 207.2102 | FTS | 215913 | 1042 | 86 | 63 | 18 | 5 | 0 | 2 | 274
23-0137260 | Monterey | HATTON 1101 | HATTON 110137088 | Unknown Cause | 2023-11-08 17:44 | 11/7 - 11/13 | 2023-11-09 04:06 | 171.4274 | FTS | 520625 | 3037 | 92 | 62 | 80 | 8 | 0 | 0 | 622
23-0137328 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101370948 | Vegetation | 2023-11-09 06:11 | 11/7 - 11/13 | 2023-11-09 08:03 | 112 | FTS | 80416 | 718 | 57 | 47 | 12 | 0 | 0 | 0 | 112
23-0137359 | Santa Barbara | ZACA 1102 | ZACA 1102CB | Unknown Cause | 2023-11-09 07:38 | 11/7 - 11/13 | 2023-11-09 09:57 | 113.4938 | FTS | 163658 | 1442 | 36 | 19 | 25 | 16 | 0 | 4 | 139
23-0137490 | Shasta | VOLTA 1101 | VOLTA 1101507876 | Unknown Cause | 2023-11-09 11:36 | 11/7 - 11/13 | 2023-11-09 13:13 | 97 | HLT | 97 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 97
23-0137572 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | 3rd Party | 2023-11-09 14:12 | 11/7 - 11/13 | 2023-11-09 15:13 | 47.7041 | FTS | 88348 | 1852 | 132 | 99 | 26 | 5 | 0 | 2 | 61
23-0137527 | Santa Clara | LOS GATOS 1107 | LOS GATOS 110760092 | Vegetation | 2023-11-09 12:28 | 11/7 - 11/13 | 2023-11-09 16:25 | 170.8936 | FTS | 194306 | 1137 | 91 | 66 | 42 | 1 | 0 | 12 | 237
23-0137612 | Amador | PINE GROVE 1102 | PINE GROVE 110283098 | Unknown Cause | 2023-11-09 16:06 | 11/7 - 11/13 | 2023-11-09 19:08 | 182 | FTS | 37674 | 207 | 24 | 20 | 4 | 0 | 0 | 1 | 182
23-0137697 | Monterey | JOLON 1102 | JOLON 11027070 | Unknown Cause | 2023-11-10 02:05 | 11/7 - 11/13 | 2023-11-10 07:26 | 319.7308 | FTS | 83130 | 260 | 7 | 6 | 19 | 0 | 0 | 3 | 321
23-0137705 | Solano | VACA DIXON 1101 | VACA DIXON 110118292 | Company Initiated | 2023-11-10 03:32 | 11/7 - 11/13 | 2023-11-10 08:05 | 273 | FTS | 384384 | 1408 | 156 | 117 | 17 | 0 | 0 | 9 | 273
23-0137713 | Tulare | OROSI 1102 | OROSI 1102CB | Unknown Cause | 2023-11-10 06:12 | 11/7 - 11/13 | 2023-11-10 08:33 | 118.3687 | FTS | 44625 | 377 | 6 | 5 | 1 | 0 | 0 | 0 | 141
23-0137775 | Shasta | VOLTA 1102 | VOLTA 11021502 | Company Initiated | 2023-11-10 08:34 | 11/7 - 11/13 | 2023-11-10 09:05 | 31 | FTS | 42191 | 1361 | 147 | 120 | 13 | 0 | 0 | 0 | 31
23-0137717 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown Cause | 2023-11-10 06:31 | 11/7 - 11/13 | 2023-11-10 12:32 | 314.0492 | FTS | 383140 | 1220 | 119 | 95 | 17 | 3 | 0 | 4 | 361
23-0137927 | San Luis Obispo | MESA 1101 | MESA 1101M86 | 3rd Party | 2023-11-10 13:23 | 11/7 - 11/13 | 2023-11-10 14:38 | 62.5344 | FTS | 47276 | 756 | 38 | 27 | 14 | 3 | 0 | 8 | 75
23-0137969 | Santa Clara | STELLING 1109 | STELLING 110913228 | Animal | 2023-11-10 14:49 | 11/7 - 11/13 | 2023-11-10 16:08 | 79 | FTS | 3476 | 44 | 2 | 2 | 2 | 0 | 0 | 0 | 79
23-0137961 | Placer | WEIMAR 1101 | WEIMAR 11012740 | Equipment Failure/Involved | 2023-11-10 14:44 | 11/7 - 11/13 | 2023-11-10 16:54 | 110.8667 | FTS | 49890 | 450 | 34 | 24 | 4 | 3 | 0 | 0 | 130
23-0138004 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown Cause | 2023-11-10 17:05 | 11/7 - 11/13 | 2023-11-10 19:53 | 163.1565 | FTS | 136562 | 837 | 89 | 58 | 13 | 2 | 0 | 1 | 168
23-0137710 | Nevada | SUMMIT 1101 | SUMMIT 1101742 | Equipment Failure/Involved | 2023-11-10 05:25 | 11/7 - 11/13 | 2023-11-10 22:01 | 285.3553 | FTS | 43374 | 152 | 24 | 13 | 31 | 1 | 0 | 0 | 996
23-0138038 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105502672 | Unknown Cause | 2023-11-11 06:35 | 11/7 - 11/13 | 2023-11-11 07:20 | 44.2727 | FTS | 4383 | 99 | 5 | 1 | 8 | 0 | 0 | 0 | 45
23-0138072 | Yuba | BRUNSWICK 1104 | BRUNSWICK 1104CB | Animal | 2023-11-11 09:48 | 11/7 - 11/13 | 2023-11-11 10:42 | 48.3214 | FTS | 123896 | 2564 | 163 | 109 | 37 | 10 | 0 | 27 | 54
23-0138045 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Unknown Cause | 2023-11-11 07:59 | 11/7 - 11/13 | 2023-11-11 12:29 | 66.9131 | FTS | 123923 | 1852 | 132 | 99 | 26 | 5 | 0 | 2 | 270
23-0138099 | Nevada | NARROWS 2105 | NARROWS 21052228 | Animal | 2023-11-11 13:00 | 11/7 - 11/13 | 2023-11-11 14:32 | 92 | FTS | 24196 | 263 | 12 | 7 | 5 | 0 | 0 | 2 | 92
23-0138176 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-12 04:56 | 11/7 - 11/13 | 2023-11-12 07:40 | 164 | FTS | 9348 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 164
23-0138170 | San Benito | SAN BENITO 2104 | SAN BENITO 2104785888 | Unknown Cause | 2023-11-12 06:29 | 11/7 - 11/13 | 2023-11-12 08:14 | 103.0882 | FTS | 133190 | 1292 | 101 | 84 | 23 | 3 | 0 | 3 | 105
23-0138168 | Calaveras | CORRAL 1101 | CORRAL 110136652 | 3rd Party | 2023-11-12 06:23 | 11/7 - 11/13 | 2023-11-12 08:58 | 102.6014 | FTS | 45555 | 444 | 41 | 27 | 3 | 0 | 0 | 2 | 155
23-0138210 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Unknown Cause | 2023-11-12 13:06 | 11/7 - 11/13 | 2023-11-12 15:31 | 99.1716 | FTS | 117915 | 1189 | 38 | 22 | 25 | 1 | 0 | 3 | 145
23-0138214 | San Benito | SAN BENITO 2101 | SAN BENITO 2101295566 | Unknown Cause | 2023-11-12 13:46 | 11/7 - 11/13 | 2023-11-12 16:06 | 126.6667 | FTS | 4560 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 140
23-0138228 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown Cause | 2023-11-12 17:04 | 11/7 - 11/13 | 2023-11-12 19:13 | 127.638 | FTS | 106833 | 837 | 89 | 58 | 13 | 2 | 0 | 1 | 129
23-0138230 | Santa Cruz | BURNS 2101 | BURNS 210136516 | Unknown Cause | 2023-11-12 17:19 | 11/7 - 11/13 | 2023-11-12 21:37 | 250.9293 | FTS | 99368 | 396 | 29 | 21 | 9 | 0 | 0 | 7 | 258
23-0138286 | Monterey | DEL MONTE 2104 | LAURELES 11112020 | Company Initiated | 2023-11-13 07:03 | 11/7 - 11/13 | 2023-11-13 07:18 | 15 | FTS | 12585 | 839 | 29 | 18 | 26 | 0 | 0 | 0 | 15
23-0138304 | Calaveras | FROGTOWN 1702 | FROGTOWN 17028482 | Company Initiated | 2023-11-13 07:57 | 11/7 - 11/13 | 2023-11-13 08:28 | 31 | FTS | 25110 | 810 | 39 | 23 | 36 | 2 | 0 | 1 | 31
23-0138275 | Alameda | FREMONT 1104 | FREMONT 1104645342 | Unknown Cause | 2023-11-13 02:10 | 11/7 - 11/13 | 2023-11-13 09:30 | 440 | FTS | 11440 | 26 | 1 | 1 | 0 | 0 | 0 | 0 | 440
23-0138358 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Company Initiated | 2023-11-13 09:30 | 11/7 - 11/13 | 2023-11-13 09:59 | 29 | FTS | 1479 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 29
23-0138368 | Alameda | FREMONT 1104 | FREMONT 1104645342 | 3rd Party | 2023-11-13 09:49 | 11/7 - 11/13 | 2023-11-13 10:16 | 27 | FTS | 702 | 26 | 1 | 1 | 0 | 0 | 0 | 0 | 27
23-0138413 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-12 17:55 | 11/7 - 11/13 | 2023-11-13 11:18 | 1043 | FTS | 59451 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 1043
23-0138434 | Placer | SHADY GLEN 1102 | BONNIE NOOK 1102542186 | Company Initiated | 2023-11-13 11:51 | 11/7 - 11/13 | 2023-11-13 12:49 | 58 | FTS | 5336 | 92 | 2 | 2 | 1 | 0 | 0 | 0 | 58
23-0138458 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Company Initiated | 2023-11-13 12:46 | 11/7 - 11/13 | 2023-11-13 13:13 | 27 | FTS | 3510 | 130 | 6 | 5 | 1 | 0 | 0 | 0 | 27
23-0138539 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Company Initiated | 2023-11-13 15:44 | 11/14 - 11/20 | 2023-11-13 16:27 | 43 | FTS | 46053 | 1071 | 89 | 62 | 14 | 0 | 0 | 6 | 43
23-0138386 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Unknown Cause | 2023-11-13 10:22 | 11/14 - 11/20 | 2023-11-13 16:41 | 263.1232 | FTS | 149454 | 568 | 37 | 25 | 27 | 3 | 0 | 0 | 379
23-0138546 | Tuolumne | PEORIA 1705 | RACETRACK 170455798 | Unknown Cause | 2023-11-13 16:01 | 11/14 - 11/20 | 2023-11-13 17:07 | 53.0707 | FTS | 19530 | 368 | 40 | 32 | 1 | 0 | 0 | 2 | 66
23-0138623 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | Animal | 2023-11-13 21:38 | 11/14 - 11/20 | 2023-11-14 00:02 | 91.1632 | FTS | 53057 | 582 | 46 | 34 | 7 | 1 | 0 | 1 | 144
23-0138576 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702737236 | 3rd Party | 2023-11-13 17:43 | 11/14 - 11/20 | 2023-11-14 02:58 | 207.0426 | FTS | 145965 | 705 | 56 | 43 | 11 | 4 | 0 | 1 | 555
23-0138706 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062104 | Company Initiated | 2023-11-14 08:02 | 11/14 - 11/20 | 2023-11-14 08:26 | 24 | FTS | 46896 | 1954 | 153 | 117 | 18 | 3 | 0 | 14 | 24
23-0127579 | San Luis Obispo | PASO ROBLES 1103 | OILFIELDS 1103N04 | Company Initiated | 2023-11-14 09:36 | 11/14 - 11/20 | 2023-11-14 09:52 | 8.457 | FTS | 17210 | 2035 | 81 | 53 | 47 | 2 | 0 | 3 | 16
23-0138765 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Company Initiated | 2023-11-14 09:33 | 11/14 - 11/20 | 2023-11-14 09:53 | 20 | FTS | 3100 | 155 | 7 | 6 | 1 | 0 | 0 | 0 | 20
23-0138781 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | Unknown Cause | 2023-11-14 10:02 | 11/14 - 11/20 | 2023-11-14 12:03 | 47.8343 | FTS | 55153 | 1153 | 115 | 77 | 18 | 0 | 0 | 2 | 121
23-0138879 | Monterey | JOLON 1102 | JOLON 11027070 | Unknown Cause | 2023-11-14 09:49 | 11/14 - 11/20 | 2023-11-14 12:46 | 177 | FTS | 46020 | 260 | 7 | 6 | 19 | 0 | 0 | 3 | 177
23-0138775 | Calaveras | FROGTOWN 1702 | FROGTOWN 17027134 | Animal | 2023-11-14 09:44 | 11/14 - 11/20 | 2023-11-14 13:05 | 77.775 | FTS | 12444 | 160 | 4 | 3 | 1 | 0 | 0 | 0 | 201
23-0138815 | Monterey | CHOLAME 2102 | CHOLAME 2102796386 | Animal | 2023-11-14 10:59 | 11/14 - 11/20 | 2023-11-14 14:09 | 190 | FTS | 28120 | 148 | 4 | 4 | 6 | 2 | 0 | 0 | 190
23-0138975 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210595050 | Unknown Cause | 2023-11-14 14:37 | 11/14 - 11/20 | 2023-11-14 16:50 | 45.5437 | FTS | 107802 | 2367 | 183 | 143 | 40 | 3 | 0 | 11 | 133
23-0139048 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Company Initiated | 2023-11-14 17:28 | 11/14 - 11/20 | 2023-11-14 19:26 | 118 | FTS | 86140 | 730 | 22 | 14 | 14 | 1 | 0 | 0 | 118
23-0139090 | San Luis Obispo | PERRY 1101 | PERRY 110185870 | Unknown Cause | 2023-11-15 00:40 | 11/14 - 11/20 | 2023-11-15 02:54 | 109.9852 | FTS | 379669 | 3452 | 121 | 83 | 42 | 3 | 3 | 0 | 134
23-0139224 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | Animal | 2023-11-15 10:06 | 11/14 - 11/20 | 2023-11-15 11:34 | 88 | FTS | 25696 | 292 | 7 | 3 | 14 | 19 | 0 | 0 | 88
23-0139127 | Alameda | VASCO 1102 | VASCO 1102546328 | Unknown Cause | 2023-11-15 07:27 | 11/14 - 11/20 | 2023-11-15 14:58 | 380.885 | FTS | 86080 | 226 | 20 | 15 | 7 | 0 | 0 | 1 | 451
23-0139575 | San Luis Obispo | PERRY 1101 | PERRY 1101925053 | Unknown Cause | 2023-11-15 16:11 | 11/14 - 11/20 | 2023-11-15 17:16 | 63.9074 | FTS | 210383 | 3292 | 120 | 82 | 40 | 3 | 0 | 0 | 65
23-0139577 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | Environmental/External | 2023-11-15 16:22 | 11/14 - 11/20 | 2023-11-15 17:39 | 77 | FTS | 21560 | 280 | 13 | 13 | 2 | 0 | 0 | 0 | 77
23-0139546 | Monterey | CHOLAME 2102 | CHOLAME 2102796386 | Unknown Cause | 2023-11-15 15:47 | 11/14 - 11/20 | 2023-11-15 17:44 | 117 | FTS | 17316 | 148 | 4 | 4 | 6 | 2 | 0 | 0 | 117
23-0139750 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210611132 | Unknown Cause | 2023-11-16 06:40 | 11/14 - 11/20 | 2023-11-16 07:08 | 25.0658 | FTS | 76526 | 3053 | 238 | 180 | 66 | 14 | 0 | 4 | 28
23-0139746 | Monterey | PRUNEDALE 1110 | PRUNEDALE 1110826224 | Unknown Cause | 2023-11-16 06:29 | 11/14 - 11/20 | 2023-11-16 08:02 | 93 | FTS | 33294 | 358 | 21 | 17 | 6 | 0 | 0 | 0 | 93
23-0139988 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-16 12:00 | 11/14 - 11/20 | 2023-11-16 14:38 | 158 | FTS | 9006 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 158
23-0140230 | Madera | COARSEGOLD 2103 | COARSEGOLD 2103CB | Unknown Cause | 2023-11-16 22:21 | 11/14 - 11/20 | 2023-11-17 00:26 | 87.9811 | FTS | 181329 | 2061 | 262 | 181 | 74 | 6 | 0 | 0 | 125
23-0140267 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101V102 | Unknown Cause | 2023-11-17 07:20 | 11/14 - 11/20 | 2023-11-17 08:08 | 48 | FTS | 288 | 6 | 0 | 0 | 1 | 2 | 0 | 0 | 48
23-0140288 | Fresno | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-17 08:06 | 11/14 - 11/20 | 2023-11-17 10:54 | 167.1845 | FTS | 51660 | 309 | 10 | 6 | 7 | 0 | 0 | 0 | 168
23-0140334 | Tuolumne | SPRING GAP 1702 | SPRING GAP 170210720 | Unknown Cause | 2023-11-17 09:16 | 11/14 - 11/20 | 2023-11-17 11:34 | 138 | FTS | 21390 | 155 | 5 | 5 | 3 | 0 | 0 | 0 | 138
23-0140656 | Sonoma | MOLINO 1102 | MOLINO 1102485246 | Vegetation | 2023-11-17 16:11 | 11/14 - 11/20 | 2023-11-17 18:42 | 68.5833 | FTS | 13168 | 192 | 15 | 10 | 1 | 0 | 6 | 1 | 151
23-0140686 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | Vegetation | 2023-11-17 17:30 | 11/14 - 11/20 | 2023-11-17 22:29 | 73.0729 | FTS | 40117 | 549 | 20 | 11 | 9 | 1 | 0 | 2 | 299
23-0140733 | Fresno | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-17 22:43 | 11/14 - 11/20 | 2023-11-17 23:42 | 59 | FTS | 18231 | 309 | 10 | 6 | 7 | 0 | 0 | 0 | 59
23-0140742 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113205874 | Vegetation | 2023-11-18 03:00 | 11/14 - 11/20 | 2023-11-18 04:44 | 104 | FTS | 21216 | 204 | 17 | 17 | 3 | 0 | 0 | 4 | 104
23-0140743 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237282 | Equipment Failure/Involved | 2023-11-18 03:14 | 11/14 - 11/20 | 2023-11-18 06:16 | 182 | FTS | 387114 | 2127 | 145 | 106 | 34 | 6 | 0 | 2 | 182
23-0140776 | Calaveras | Valley Springs 1101 | Valley Springs 110111158 | 3rd Party | 2023-11-18 07:37 | 11/14 - 11/20 | 2023-11-18 08:11 | 34 | FTS | 14008 | 412 | 31 | 19 | 12 | 0 | 0 | 3 | 34
23-0140753 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102867686 | Unknown Cause | 2023-11-18 05:11 | 11/14 - 11/20 | 2023-11-18 10:51 | 340 | FTS | 19040 | 56 | 0 | 0 | 3 | 0 | 0 | 0 | 340
23-0140846 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Unknown Cause | 2023-11-18 10:35 | 11/14 - 11/20 | 2023-11-18 11:36 | 61 | FTS | 91439 | 1499 | 66 | 55 | 15 | 3 | 0 | 13 | 61
23-0140791 | Calaveras | Valley Springs 1101 | Valley Springs 110111158 | 3rd Party | 2023-11-18 08:16 | 11/14 - 11/20 | 2023-11-18 12:23 | 247 | FTS | 101764 | 412 | 31 | 19 | 12 | 0 | 0 | 3 | 247
23-0140829 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A32 | Equipment Failure/Involved | 2023-11-18 10:11 | 11/14 - 11/20 | 2023-11-18 12:47 | 71.0116 | FTS | 311812 | 4391 | 226 | 168 | 64 | 7 | 1 | 20 | 156
23-0140878 | Calaveras | Valley Springs 1101 | Valley Springs 110111158 | 3rd Party | 2023-11-18 12:30 | 11/14 - 11/20 | 2023-11-18 14:41 | 131 | FTS | 53972 | 412 | 31 | 19 | 12 | 0 | 0 | 3 | 131
23-0140929 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | Unknown Cause | 2023-11-18 16:08 | 11/14 - 11/20 | 2023-11-18 16:20 | 12 | FTS | 1368 | 114 | 3 | 2 | 9 | 2 | 0 | 0 | 12
23-0140927 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101CB | Animal | 2023-11-18 15:40 | 11/14 - 11/20 | 2023-11-18 17:08 | 88 | FTS | 310552 | 3529 | 261 | 185 | 97 | 15 | 5 | 1 | 88
23-0141108 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Unknown Cause | 2023-11-19 11:04 | 11/14 - 11/20 | 2023-11-19 14:21 | 197 | FTS | 11229 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 197
23-0141231 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Unknown Cause | 2023-11-20 08:32 | 11/14 - 11/20 | 2023-11-20 14:37 | 360.979 | FTS | 206119 | 571 | 37 | 25 | 27 | 3 | 0 | 0 | 365
23-0141176 | Santa Cruz | POINT MORETTI SUB | N/A | Vegetation | 2023-11-20 03:19 | 11/14 - 11/20 | 2023-11-20 15:01 | 209.6133 | T-EPSS | 163708 | 781 | 42 | 29 | 41 | 16 | 0 | 11 | 702
23-0141511 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Company Initiated | 2023-11-20 15:31 | 11/21 - 11/27 | 2023-11-20 16:06 | 35 | FTS | 19985 | 571 | 37 | 25 | 27 | 3 | 0 | 0 | 35
23-0141607 | Tehama | CORNING 1102 | CORNING 11021900 | Unknown Cause | 2023-11-20 21:17 | 11/21 - 11/27 | 2023-11-21 08:44 | 333.2201 | FTS | 119626 | 359 | 28 | 23 | 10 | 3 | 0 | 1 | 687
23-0141690 | San Benito | HOLLISTER 2105 | HOLLISTER 2105475946 | Vegetation | 2023-11-21 08:09 | 11/21 - 11/27 | 2023-11-21 09:39 | 50.381 | FTS | 6348 | 126 | 2 | 2 | 2 | 2 | 0 | 0 | 90
23-0142144 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Unknown Cause | 2023-11-22 06:43 | 11/21 - 11/27 | 2023-11-22 09:16 | 153 | FTS | 200889 | 1313 | 124 | 89 | 20 | 2 | 0 | 2 | 153
23-0142140 | Tuolumne | CURTIS 1704 | CURTIS 170411290 | Unknown Cause | 2023-11-22 06:25 | 11/21 - 11/27 | 2023-11-22 09:53 | 208 | FTS | 28912 | 139 | 15 | 12 | 2 | 0 | 0 | 1 | 208
23-0142480 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y36 | Animal | 2023-11-22 21:18 | 11/21 - 11/27 | 2023-11-22 22:33 | 75 | FTS | 20475 | 273 | 3 | 1 | 14 | 1 | 0 | 0 | 75
23-0142445 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Vegetation | 2023-11-22 17:20 | 11/21 - 11/27 | 2023-11-23 12:25 | 349.1683 | FTS | 107893 | 309 | 19 | 17 | 10 | 5 | 0 | 0 | 1145
23-0142515 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Unknown Cause | 2023-11-23 11:24 | 11/21 - 11/27 | 2023-11-23 12:52 | 88 | FTS | 30360 | 345 | 5 | 5 | 10 | 0 | 0 | 0 | 88
23-0142580 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Unknown Cause | 2023-11-24 00:02 | 11/21 - 11/27 | 2023-11-24 10:40 | 318.0755 | FTS | 185438 | 583 | 60 | 46 | 3 | 4 | 0 | 2 | 638
23-0142586 | Yuba | DOBBINS 1101 | DOBBINS 110169722 | Animal | 2023-11-24 04:50 | 11/21 - 11/27 | 2023-11-24 12:14 | 108.1534 | FTS | 76140 | 704 | 79 | 60 | 15 | 2 | 0 | 4 | 444
23-0142642 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110610800 | Unknown Cause | 2023-11-24 12:05 | 11/21 - 11/27 | 2023-11-24 13:22 | 77 | FTS | 82159 | 1067 | 62 | 52 | 19 | 2 | 0 | 3 | 77
23-0142624 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101975548 | Equipment Failure/Involved | 2023-11-24 10:17 | 11/21 - 11/27 | 2023-11-24 13:22 | 76.1104 | FTS | 171705 | 2256 | 182 | 137 | 45 | 4 | 0 | 0 | 185
23-0142577 | Butte | KANAKA 1101 | KANAKA 1101733624 | Unknown Cause | 2023-11-23 22:06 | 11/21 - 11/27 | 2023-11-24 13:32 | 161.4138 | FTS | 9362 | 58 | 3 | 3 | 2 | 0 | 0 | 0 | 926
23-0142590 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | Equipment Failure/Involved | 2023-11-24 05:59 | 11/21 - 11/27 | 2023-11-24 14:55 | 350.9832 | FTS | 708635 | 2019 | 220 | 161 | 23 | 2 | 0 | 3 | 536
23-0142732 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110610800 | Unknown Cause | 2023-11-25 04:43 | 11/21 - 11/27 | 2023-11-25 07:04 | 141 | FTS | 150447 | 1067 | 62 | 52 | 19 | 2 | 0 | 3 | 141
23-0142731 | Yuba | DOBBINS 1101 | DOBBINS 1101CB | Animal | 2023-11-25 04:28 | 11/21 - 11/27 | 2023-11-25 07:27 | 159.8161 | FTS | 146871 | 919 | 88 | 68 | 19 | 2 | 0 | 4 | 179
23-0142736 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102367100 | Unknown Cause | 2023-11-25 06:42 | 11/21 - 11/27 | 2023-11-25 07:50 | 68 | FTS | 612 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 68
23-0142725 | Madera | SAN JOAQUIN #2 1103 | SAN JOAQUIN #2 1103CB | 3rd Party | 2023-11-24 21:26 | 11/21 - 11/27 | 2023-11-25 10:47 | 239.5075 | FTS | 208611 | 871 | 88 | 64 | 13 | 0 | 0 | 2 | 801
23-0142673 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Unknown Cause | 2023-11-24 15:24 | 11/21 - 11/27 | 2023-11-25 11:07 | 777.7055 | FTS | 126766 | 163 | 6 | 6 | 4 | 1 | 0 | 0 | 1183
23-0142812 | Monterey | DOLAN ROAD 1101 | DOLAN ROAD 110122158 | Vegetation | 2023-11-25 15:13 | 11/21 - 11/27 | 2023-11-25 16:14 | 61 | FTS | 28426 | 466 | 34 | 28 | 4 | 0 | 0 | 0 | 61
23-0142766 | Butte | BANGOR 1101 | BANGOR 1101614048 | Equipment Failure/Involved | 2023-11-25 10:50 | 11/21 - 11/27 | 2023-11-26 09:02 | 170.5276 | FTS | 21657 | 127 | 14 | 13 | 2 | 0 | 2 | 0 | 1332
23-0142894 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104828842 | Animal | 2023-11-26 09:01 | 11/21 - 11/27 | 2023-11-26 11:07 | 65.1798 | FTS | 104027 | 1596 | 164 | 124 | 21 | 1 | 0 | 0 | 126
23-0143279 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | 3rd Party | 2023-11-27 20:21 | 11/28 - 12/4 | 2023-11-28 04:18 | 477 | FTS | 147393 | 309 | 19 | 17 | 10 | 5 | 0 | 0 | 477
23-0143436 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Company Initiated | 2023-11-28 11:02 | 11/28 - 12/4 | 2023-11-28 11:27 | 25 | FTS | 4975 | 199 | 3 | 1 | 7 | 0 | 0 | 0 | 25
23-0143685 | Tulare | SAND CREEK 1103 | SAND CREEK 11037110 | Unknown Cause | 2023-11-29 06:27 | 11/28 - 12/4 | 2023-11-29 09:23 | 176 | FTS | 29920 | 170 | 4 | 2 | 8 | 0 | 0 | 0 | 176
23-0143787 | Monterey | JOLON 1102 | JOLON 11027002 | Unknown Cause | 2023-11-29 10:49 | 11/28 - 12/4 | 2023-11-29 11:02 | 13 | FTS | 1794 | 138 | 7 | 5 | 3 | 2 | 0 | 3 | 13
23-0143671 | Monterey | LAURELES 1111 | LAURELES 1111198478 | Equipment Failure/Involved | 2023-11-29 03:56 | 11/28 - 12/4 | 2023-11-29 11:43 | 467 | FTS | 111146 | 238 | 6 | 5 | 6 | 0 | 0 | 0 | 467
23-0143821 | Monterey | LAURELES 1111 | LAURELES 1111432 | Equipment Failure/Involved | 2023-11-29 12:04 | 11/28 - 12/4 | 2023-11-29 13:27 | 83 | FTS | 26892 | 324 | 6 | 5 | 7 | 0 | 0 | 0 | 83
23-0143853 | Monterey | DOLAN ROAD 1101 | DOLAN ROAD 110169466 | Unknown Cause | 2023-11-29 12:59 | 11/28 - 12/4 | 2023-11-29 15:15 | 136 | FTS | 32776 | 241 | 11 | 9 | 1 | 0 | 0 | 0 | 136
23-0144122 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101673618 | Unknown Cause | 2023-11-30 07:52 | 11/28 - 12/4 | 2023-11-30 08:36 | 44 | FTS | 616 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 44
23-0144123 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101277014 | Unknown Cause | 2023-11-30 07:55 | 11/28 - 12/4 | 2023-11-30 08:45 | 50 | FTS | 18200 | 364 | 35 | 25 | 41 | 4 | 0 | 0 | 50
23-0144098 | Monterey | LAURELES 1111 | LAURELES 1111198478 | Equipment Failure/Involved | 2023-11-30 07:07 | 11/28 - 12/4 | 2023-11-30 12:20 | 313 | FTS | 74494 | 238 | 6 | 5 | 6 | 0 | 0 | 0 | 313
23-0144397 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Unknown Cause | 2023-11-30 16:05 | 11/28 - 12/4 | 2023-12-01 09:46 | 362.175 | C/OUT | 211148 | 583 | 61 | 47 | 3 | 4 | 0 | 2 | 1061
23-0127364 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Company Initiated | 2023-12-01 08:05 | 11/28 - 12/4 | 2023-12-01 16:54 | 65 | FTS | 260 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 529
23-0144873 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | Equipment Failure/Involved | 2023-12-02 00:08 | 11/28 - 12/4 | 2023-12-02 01:43 | 95 | FTS | 45885 | 483 | 45 | 32 | 5 | 0 | 0 | 0 | 95
23-0144876 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | 3rd Party | 2023-12-02 02:13 | 11/28 - 12/4 | 2023-12-02 09:05 | 9.6729 | FTS | 4672 | 483 | 45 | 32 | 5 | 0 | 0 | 0 | 412
23-0144970 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101929360 | Unknown Cause | 2023-12-02 18:35 | 11/28 - 12/4 | 2023-12-03 09:36 | 68.435 | FTS | 196819 | 2876 | 241 | 167 | 46 | 0 | 0 | 1 | 901
23-0145421 | Santa Barbara | SISQUOC 1103 | SISQUOC 1103858898 | Unknown Cause | 2023-12-05 06:18 | 12/5 - 12/11 | 2023-12-05 07:49 | 91 | FTS | 14469 | 159 | 6 | 4 | 5 | 0 | 0 | 1 | 91
23-0145938 | Amador | WEST POINT 1102 | WEST POINT 1102CB | Unknown Cause | 2023-12-06 13:42 | 12/5 - 12/11 | 2023-12-06 16:09 | 53.9449 | FTS | 202671 | 3757 | 310 | 226 | 62 | 2 | 0 | 4 | 147
23-0146003 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-12-06 16:39 | 12/5 - 12/11 | 2023-12-06 19:48 | 189 | FTS | 6426 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 189
23-0146044 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2023-12-06 20:35 | 12/5 - 12/11 | 2023-12-07 09:55 | 800 | FTS | 112000 | 140 | 7 | 6 | 3 | 0 | 0 | 0 | 800
23-0146045 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021888 | 3rd Party | 2023-12-06 20:35 | 12/5 - 12/11 | 2023-12-07 13:03 | 180.1761 | FTS | 227202 | 1261 | 50 | 42 | 14 | 0 | 0 | 0 | 988
23-0146090 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Animal | 2023-12-07 07:41 | 12/5 - 12/11 | 2023-12-07 13:32 | 294.7824 | FTS | 545937 | 1852 | 129 | 96 | 26 | 4 | 0 | 2 | 351
23-0146063 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Unknown Cause | 2023-12-06 22:38 | 12/5 - 12/11 | 2023-12-07 14:55 | 977 | FTS | 159251 | 163 | 6 | 6 | 4 | 1 | 0 | 0 | 977
23-0146492 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110070 | Unknown Cause | 2023-12-08 10:59 | 12/5 - 12/11 | 2023-12-08 13:22 | 143 | FTS | 42471 | 297 | 30 | 19 | 3 | 0 | 0 | 0 | 143
23-0146586 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X16 | Unknown Cause | 2023-12-08 16:34 | 12/5 - 12/11 | 2023-12-08 18:41 | 96.4064 | FTS | 27283 | 283 | 8 | 4 | 14 | 2 | 0 | 0 | 127
23-0146673 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-12-09 16:35 | 12/5 - 12/11 | 2023-12-09 18:55 | 140 | FTS | 4760 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 140
23-0146585 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Equipment Failure/Involved | 2023-12-08 16:11 | 12/5 - 12/11 | 2023-12-09 23:37 | 291.5156 | FTS | 215430 | 739 | 19 | 13 | 15 | 2 | 0 | 0 | 1886
23-0146755 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103492068 | Unknown Cause | 2023-12-10 12:29 | 12/5 - 12/11 | 2023-12-10 16:18 | 137.2641 | FTS | 239114 | 1742 | 76 | 54 | 23 | 2 | 0 | 1 | 229
23-0146761 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Unknown Cause | 2023-12-10 16:07 | 12/5 - 12/11 | 2023-12-10 16:58 | 51 | FTS | 31671 | 621 | 38 | 26 | 19 | 2 | 0 | 4 | 51
23-0146763 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-12-10 16:47 | 12/5 - 12/11 | 2023-12-10 17:48 | 61 | FTS | 2074 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 61
23-0146812 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Unknown Cause | 2023-12-11 06:38 | 12/5 - 12/11 | 2023-12-11 07:46 | 68 | FTS | 8636 | 127 | 2 | 2 | 1 | 0 | 0 | 0 | 68
23-0146841 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | Company Initiated | 2023-12-11 09:17 | 12/5 - 12/11 | 2023-12-11 11:15 | 77.0213 | FTS | 39820 | 517 | 17 | 9 | 7 | 1 | 0 | 2 | 118
23-0146864 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | 3rd Party | 2023-12-11 10:56 | 12/12 - 12/18 | 2023-12-11 16:01 | 284.76 | FTS | 7119 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 305
23-0146944 | Butte | CLARK ROAD 1102 | CLARK ROAD 110290548 | Equipment Failure/Involved | 2023-12-11 20:41 | 12/12 - 12/18 | 2023-12-12 05:24 | 65.9562 | FTS | 31593 | 479 | 37 | 29 | 10 | 1 | 0 | 1 | 523
23-0147117 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Animal | 2023-12-12 16:43 | 12/12 - 12/18 | 2023-12-12 17:53 | 69.43 | FTS | 43116 | 621 | 38 | 26 | 19 | 2 | 0 | 4 | 70
23-0135180 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021888 | Company Initiated | 2023-12-13 06:34 | 12/12 - 12/18 | 2023-12-13 06:47 | 13 | FTS | 15288 | 1176 | 47 | 39 | 13 | 0 | 0 | 0 | 13
23-0147161 | Santa Barbara | ZACA 1101 | PALMER 1101M82 | Unknown Cause | 2023-12-13 06:08 | 12/12 - 12/18 | 2023-12-13 07:10 | 62 | FTS | 49042 | 791 | 20 | 16 | 8 | 1 | 0 | 0 | 62
23-0147189 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101483444 | Unknown Cause | 2023-12-13 08:34 | 12/12 - 12/18 | 2023-12-13 09:24 | 48.4089 | FTS | 143484 | 2964 | 25 | 16 | 72 | 6 | 0 | 1 | 50
23-0147265 | Fresno | AUBERRY 1101 | AUBERRY 110137536 | Company Initiated | 2023-12-13 12:40 | 12/12 - 12/18 | 2023-12-13 17:11 | 227.0017 | FTS | 136428 | 601 | 29 | 24 | 18 | 3 | 0 | 1 | 271
23-0147308 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Unknown Cause | 2023-12-13 16:24 | 12/12 - 12/18 | 2023-12-13 18:23 | 119 | FTS | 73899 | 621 | 38 | 26 | 19 | 2 | 0 | 4 | 119
23-0147560 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | 3rd Party | 2023-12-15 10:18 | 12/12 - 12/18 | 2023-12-15 17:28 | 406.6 | FTS | 10165 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 430
23-0147838 | San Benito | LOS OSITOS 2101 | LOS OSITOS 21017014 | Unknown Cause | 2023-12-18 06:19 | 12/12 - 12/18 | 2023-12-18 10:37 | 258 | FTS | 27348 | 106 | 5 | 5 | 2 | 0 | 0 | 0 | 258
23-0147867 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 210110000 | Equipment Failure/Involved | 2023-12-18 09:06 | 12/12 - 12/18 | 2023-12-18 10:40 | 94 | FTS | 24346 | 259 | 24 | 14 | 7 | 0 | 0 | 0 | 94
23-0147773 | Tulare | SAND CREEK 1103 | SAND CREEK 11037110 | Unknown Cause | 2023-12-17 16:25 | 12/12 - 12/18 | 2023-12-18 12:02 | 818.0748 | FTS | 240514 | 294 | 9 | 7 | 11 | 1 | 0 | 0 | 1177
23-0147896 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 210110000 | Equipment Failure/Involved | 2023-12-18 10:51 | 12/12 - 12/18 | 2023-12-18 13:29 | 50.834 | FTS | 13166 | 259 | 24 | 14 | 7 | 0 | 0 | 0 | 158
23-0147831 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Unknown Cause | 2023-12-18 05:21 | 12/12 - 12/18 | 2023-12-18 15:19 | 477.6295 | FTS | 171469 | 359 | 14 | 14 | 5 | 0 | 0 | 0 | 598
23-0147910 | San Benito | LOS OSITOS 2101 | LOS OSITOS 21017014 | Equipment Failure/Involved | 2023-12-18 12:26 | 12/19 - 12/25 | 2023-12-19 11:45 | 531.2086 | FTS | 86587 | 163 | 6 | 6 | 4 | 1 | 0 | 0 | 1399
23-0148122 | Santa Barbara | CUYAMA 2101 | CUYAMA 21013542 | Unknown Cause | 2023-12-19 14:50 | 12/19 - 12/25 | 2023-12-19 19:03 | 253 | FTS | 31372 | 124 | 5 | 5 | 1 | 0 | 0 | 0 | 253
23-0148200 | Sonoma | PETALUMA A SUB | N/A | Unknown Cause | 2023-12-20 03:58 | 12/19 - 12/25 | 2023-12-20 06:09 | 127.8783 | T-EPSS | 160743 | 1257 | 30 | 23 | 11 | 0 | 0 | 0 | 131
23-0148306 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Unknown Cause | 2023-12-20 16:49 | 12/19 - 12/25 | 2023-12-20 17:07 | 18 | FTS | 2286 | 127 | 2 | 2 | 1 | 0 | 0 | 0 | 18
23-0148322 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | Unknown Cause | 2023-12-20 18:00 | 12/19 - 12/25 | 2023-12-20 20:33 | 153 | FTS | 15606 | 102 | 1 | 1 | 1 | 0 | 0 | 0 | 153
23-0148394 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101730862 | Unknown Cause | 2023-12-20 22:41 | 12/19 - 12/25 | 2023-12-20 22:52 | 11 | FTS | 352 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 11
23-0148437 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108MR190 | Company Initiated | 2023-12-21 07:39 | 12/19 - 12/25 | 2023-12-21 07:52 | 13 | FTS | 24349 | 1873 | 92 | 71 | 28 | 0 | 2 | 0 | 13
23-0148418 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2023-12-21 03:00 | 12/19 - 12/25 | 2023-12-21 10:48 | 468 | FTS | 23400 | 50 | 0 | 0 | 2 | 0 | 0 | 0 | 468
23-0148642 | Fresno | SAND CREEK 1103 | SAND CREEK 11037140 | Unknown Cause | 2023-12-23 02:48 | 12/19 - 12/25 | 2023-12-23 06:09 | 163.1828 | FTS | 74085 | 454 | 55 | 32 | 3 | 0 | 0 | 0 | 201
23-0148753 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Animal | 2023-12-24 12:34 | 12/26 - 1/1/24 | 2023-12-26 15:00 | 2091.6667 | FTS | 43925 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3026
23-0148969 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Equipment Failure/Involved | 2023-12-27 07:42 | 12/26 - 1/1/24 | 2023-12-27 18:02 | 486 | FTS | 10206 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 620

## Dec Outages 120123_123123
Outages | County | Circuit | CPZ | Cause | FNL | Week | End_Date | CAIDI | EPSS_Outage_Type | Customer_Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Well_Water_Dependent | Restoration_Time_Minutes
23-0144397 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Unknown Cause | 2023-11-30 16:05 | 11/28 - 12/4 | 2023-12-01 09:46 | 362.175 | C/OUT | 211148 | 583 | 61 | 47 | 3 | 4 | 0 | 2 | 1061
23-0127364 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Company Initiated | 2023-12-01 08:05 | 11/28 - 12/4 | 2023-12-01 16:54 | 65 | FTS | 260 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 529
23-0144873 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | Equipment Failure/Involved | 2023-12-02 00:08 | 11/28 - 12/4 | 2023-12-02 01:43 | 95 | FTS | 45885 | 483 | 45 | 32 | 5 | 0 | 0 | 0 | 95
23-0144876 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | 3rd Party | 2023-12-02 02:13 | 11/28 - 12/4 | 2023-12-02 09:05 | 9.6729 | FTS | 4672 | 483 | 45 | 32 | 5 | 0 | 0 | 0 | 412
23-0144970 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101929360 | Unknown Cause | 2023-12-02 18:35 | 11/28 - 12/4 | 2023-12-03 09:36 | 68.435 | FTS | 196819 | 2876 | 241 | 167 | 46 | 0 | 0 | 1 | 901
23-0145421 | Santa Barbara | SISQUOC 1103 | SISQUOC 1103858898 | Unknown Cause | 2023-12-05 06:18 | 12/5 - 12/11 | 2023-12-05 07:49 | 91 | FTS | 14469 | 159 | 6 | 4 | 5 | 0 | 0 | 1 | 91
23-0145938 | Amador | WEST POINT 1102 | WEST POINT 1102CB | Unknown Cause | 2023-12-06 13:42 | 12/5 - 12/11 | 2023-12-06 16:09 | 53.9449 | FTS | 202671 | 3757 | 310 | 226 | 62 | 2 | 0 | 4 | 147
23-0146003 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-12-06 16:39 | 12/5 - 12/11 | 2023-12-06 19:48 | 189 | FTS | 6426 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 189
23-0146044 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2023-12-06 20:35 | 12/5 - 12/11 | 2023-12-07 09:55 | 800 | FTS | 112000 | 140 | 7 | 6 | 3 | 0 | 0 | 0 | 800
23-0146045 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021888 | 3rd Party | 2023-12-06 20:35 | 12/5 - 12/11 | 2023-12-07 13:03 | 180.1761 | FTS | 227202 | 1261 | 50 | 42 | 14 | 0 | 0 | 0 | 988
23-0146090 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Animal | 2023-12-07 07:41 | 12/5 - 12/11 | 2023-12-07 13:32 | 294.7824 | FTS | 545937 | 1852 | 129 | 96 | 26 | 4 | 0 | 2 | 351
23-0146063 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Unknown Cause | 2023-12-06 22:38 | 12/5 - 12/11 | 2023-12-07 14:55 | 977 | FTS | 159251 | 163 | 6 | 6 | 4 | 1 | 0 | 0 | 977
23-0146492 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110070 | Unknown Cause | 2023-12-08 10:59 | 12/5 - 12/11 | 2023-12-08 13:22 | 143 | FTS | 42471 | 297 | 30 | 19 | 3 | 0 | 0 | 0 | 143
23-0146586 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X16 | Unknown Cause | 2023-12-08 16:34 | 12/5 - 12/11 | 2023-12-08 18:41 | 96.4064 | FTS | 27283 | 283 | 8 | 4 | 14 | 2 | 0 | 0 | 127
23-0146673 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-12-09 16:35 | 12/5 - 12/11 | 2023-12-09 18:55 | 140 | FTS | 4760 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 140
23-0146585 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Equipment Failure/Involved | 2023-12-08 16:11 | 12/5 - 12/11 | 2023-12-09 23:37 | 291.5156 | FTS | 215430 | 739 | 19 | 13 | 15 | 2 | 0 | 0 | 1886
23-0146755 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103492068 | Unknown Cause | 2023-12-10 12:29 | 12/5 - 12/11 | 2023-12-10 16:18 | 137.2641 | FTS | 239114 | 1742 | 76 | 54 | 23 | 2 | 0 | 1 | 229
23-0146761 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Unknown Cause | 2023-12-10 16:07 | 12/5 - 12/11 | 2023-12-10 16:58 | 51 | FTS | 31671 | 621 | 38 | 26 | 19 | 2 | 0 | 4 | 51
23-0146763 | Kern | LAMONT 1104 | LAMONT 11044113 | Unknown Cause | 2023-12-10 16:47 | 12/5 - 12/11 | 2023-12-10 17:48 | 61 | FTS | 2074 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 61
23-0146812 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Unknown Cause | 2023-12-11 06:38 | 12/5 - 12/11 | 2023-12-11 07:46 | 68 | FTS | 8636 | 127 | 2 | 2 | 1 | 0 | 0 | 0 | 68
23-0146841 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | Company Initiated | 2023-12-11 09:17 | 12/5 - 12/11 | 2023-12-11 11:15 | 77.0213 | FTS | 39820 | 517 | 17 | 9 | 7 | 1 | 0 | 2 | 118
23-0146864 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | 3rd Party | 2023-12-11 10:56 | 12/12 - 12/18 | 2023-12-11 16:01 | 284.76 | FTS | 7119 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 305
23-0146944 | Butte | CLARK ROAD 1102 | CLARK ROAD 110290548 | Equipment Failure/Involved | 2023-12-11 20:41 | 12/12 - 12/18 | 2023-12-12 05:24 | 65.9562 | FTS | 31593 | 479 | 37 | 29 | 10 | 1 | 0 | 1 | 523
23-0147117 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Animal | 2023-12-12 16:43 | 12/12 - 12/18 | 2023-12-12 17:53 | 69.43 | FTS | 43116 | 621 | 38 | 26 | 19 | 2 | 0 | 4 | 70
23-0135180 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021888 | Company Initiated | 2023-12-13 06:34 | 12/12 - 12/18 | 2023-12-13 06:47 | 13 | FTS | 15288 | 1176 | 47 | 39 | 13 | 0 | 0 | 0 | 13
23-0147161 | Santa Barbara | ZACA 1101 | PALMER 1101M82 | Unknown Cause | 2023-12-13 06:08 | 12/12 - 12/18 | 2023-12-13 07:10 | 62 | FTS | 49042 | 791 | 20 | 16 | 8 | 1 | 0 | 0 | 62
23-0147189 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101483444 | Unknown Cause | 2023-12-13 08:34 | 12/12 - 12/18 | 2023-12-13 09:24 | 48.4089 | FTS | 143484 | 2964 | 25 | 16 | 72 | 6 | 0 | 1 | 50
23-0147265 | Fresno | AUBERRY 1101 | AUBERRY 110137536 | Company Initiated | 2023-12-13 12:40 | 12/12 - 12/18 | 2023-12-13 17:11 | 227.0017 | FTS | 136428 | 601 | 29 | 24 | 18 | 3 | 0 | 1 | 271
23-0147308 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Unknown Cause | 2023-12-13 16:24 | 12/12 - 12/18 | 2023-12-13 18:23 | 119 | FTS | 73899 | 621 | 38 | 26 | 19 | 2 | 0 | 4 | 119
23-0147560 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | 3rd Party | 2023-12-15 10:18 | 12/12 - 12/18 | 2023-12-15 17:28 | 406.6 | FTS | 10165 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 430
23-0147838 | San Benito | LOS OSITOS 2101 | LOS OSITOS 21017014 | Unknown Cause | 2023-12-18 06:19 | 12/12 - 12/18 | 2023-12-18 10:37 | 258 | FTS | 27348 | 106 | 5 | 5 | 2 | 0 | 0 | 0 | 258
23-0147867 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 210110000 | Equipment Failure/Involved | 2023-12-18 09:06 | 12/12 - 12/18 | 2023-12-18 10:40 | 94 | FTS | 24346 | 259 | 24 | 14 | 7 | 0 | 0 | 0 | 94
23-0147773 | Tulare | SAND CREEK 1103 | SAND CREEK 11037110 | Unknown Cause | 2023-12-17 16:25 | 12/12 - 12/18 | 2023-12-18 12:02 | 818.0748 | FTS | 240514 | 294 | 9 | 7 | 11 | 1 | 0 | 0 | 1177
23-0147896 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 210110000 | Equipment Failure/Involved | 2023-12-18 10:51 | 12/12 - 12/18 | 2023-12-18 13:29 | 50.834 | FTS | 13166 | 259 | 24 | 14 | 7 | 0 | 0 | 0 | 158
23-0147831 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Unknown Cause | 2023-12-18 05:21 | 12/12 - 12/18 | 2023-12-18 15:19 | 477.6295 | FTS | 171469 | 359 | 14 | 14 | 5 | 0 | 0 | 0 | 598
23-0147910 | San Benito | LOS OSITOS 2101 | LOS OSITOS 21017014 | Equipment Failure/Involved | 2023-12-18 12:26 | 12/19 - 12/25 | 2023-12-19 11:45 | 531.2086 | FTS | 86587 | 163 | 6 | 6 | 4 | 1 | 0 | 0 | 1399
23-0148122 | Santa Barbara | CUYAMA 2101 | CUYAMA 21013542 | Unknown Cause | 2023-12-19 14:50 | 12/19 - 12/25 | 2023-12-19 19:03 | 253 | FTS | 31372 | 124 | 5 | 5 | 1 | 0 | 0 | 0 | 253
23-0148200 | Sonoma | PETALUMA A SUB | N/A | Unknown Cause | 2023-12-20 03:58 | 12/19 - 12/25 | 2023-12-20 06:09 | 127.8783 | T-EPSS | 160743 | 1257 | 30 | 23 | 11 | 0 | 0 | 0 | 131
23-0148306 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Unknown Cause | 2023-12-20 16:49 | 12/19 - 12/25 | 2023-12-20 17:07 | 18 | FTS | 2286 | 127 | 2 | 2 | 1 | 0 | 0 | 0 | 18
23-0148322 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | Unknown Cause | 2023-12-20 18:00 | 12/19 - 12/25 | 2023-12-20 20:33 | 153 | FTS | 15606 | 102 | 1 | 1 | 1 | 0 | 0 | 0 | 153
23-0148394 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101730862 | Unknown Cause | 2023-12-20 22:41 | 12/19 - 12/25 | 2023-12-20 22:52 | 11 | FTS | 352 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 11
23-0148437 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108MR190 | Company Initiated | 2023-12-21 07:39 | 12/19 - 12/25 | 2023-12-21 07:52 | 13 | FTS | 24349 | 1873 | 92 | 71 | 28 | 0 | 2 | 0 | 13
23-0148418 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2023-12-21 03:00 | 12/19 - 12/25 | 2023-12-21 10:48 | 468 | FTS | 23400 | 50 | 0 | 0 | 2 | 0 | 0 | 0 | 468
23-0148642 | Fresno | SAND CREEK 1103 | SAND CREEK 11037140 | Unknown Cause | 2023-12-23 02:48 | 12/19 - 12/25 | 2023-12-23 06:09 | 163.1828 | FTS | 74085 | 454 | 55 | 32 | 3 | 0 | 0 | 0 | 201
23-0148753 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Animal | 2023-12-24 12:34 | 12/26 - 1/1/24 | 2023-12-26 15:00 | 2091.6667 | FTS | 43925 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3026
23-0148969 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Equipment Failure/Involved | 2023-12-27 07:42 | 12/26 - 1/1/24 | 2023-12-27 18:02 | 486 | FTS | 10206 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 620

## YTD EPSS Outages_Circuit
Circuit | Count of Outages
ALHAMBRA 1105 | 3
ALLEGHANY 1101 | 3
ALLEGHANY 1102 | 1
ALTO 1124 | 2
ALTO 1125 | 2
ANDERSON 1101 | 1
ANNAPOLIS 1101 | 2
ANNAPOLIS SUB | 1
ANTELOPE 1101 | 1
ANTLER 1101 | 4
APPLE HILL 1104 | 8
APPLE HILL 2102 | 18
ARCATA 1121 | 2
ARCATA 1122 | 1
ATASCADERO 1101 | 2
ATASCADERO 1102 | 3
ATASCADERO 1103 | 9
AUBERRY 1101 | 7
AUBERRY 1102 | 2
AUBURN 1102 | 1
AVENA 1702 | 1
AVENAL 2101 | 7
BALCH NO 1 1101 | 1
BANGOR 1101 | 10
BAY MEADOWS 2102 | 1
BAYWOOD 1101 | 3
BEAR VALLEY 2101 | 4
BEAR VALLEY 2105 | 7
BELL 1107 | 2
BELL 1108 | 5
BELLEVUE 2101 | 4
BEN LOMOND 0401 | 8
BEN LOMOND 1101 | 3
BIG BASIN 1101 | 1
BIG BASIN 1102 | 4
BIG BEND 1102 | 2
BIG MEADOWS 2101 | 3
BOLINAS 1101 | 3
BONNIE NOOK 1102 | 3
BORONDA SUB | 2
BRENTWOOD 2105 | 6
BRIDGEVILLE 1101 | 4
BRIDGEVILLE 1102 | 1
BROWNS VALLEY 1101 | 1
BRUNSWICK 1102 | 4
BRUNSWICK 1103 | 2
BRUNSWICK 1104 | 2
BRUNSWICK 1105 | 17
BRUNSWICK 1106 | 16
BRUNSWICK 1107 | 2
BUCKS CREEK 1103 | 2
BUELLTON 1101 | 7
BUELLTON 1102 | 1
BURNEY 1101 | 2
BURNS 2101 | 6
BUTTE 1105 | 2
CABRILLO 1103 | 3
CABRILLO 1104 | 4
CAL WATER 1102 | 1
CALAVERAS CEMENT 1101 | 11
CALISTOGA 1101 | 16
CALISTOGA 1102 | 8
CALPELLA 1101 | 2
CALPELLA 1102 | 1
CAMBRIA 1102 | 1
CAMP EVERS 2103 | 9
CAMP EVERS 2104 | 4
CAMP EVERS 2105 | 9
CAMP EVERS 2106 | 12
CANTUA 1103 | 1
CARLOTTA 1121 | 2
CARNERAS 1103 | 1
CASTRO VALLEY 1108 | 1
CASTRO VALLEY 1110 | 8
CASTRO VALLEY 1111 | 1
CAYETANO 2109 | 6
CAYETANO 2111 | 2
CAYUCOS 1101 | 2
CAYUCOS 1102 | 2
CEDAR CREEK 1101 | 4
CHALLENGE 1101 | 3
CHALLENGE 1102 | 1
CHESTER SUB | 1
CHOLAME 1101 | 1
CHOLAME 2102 | 12
CLARK ROAD 1101 | 1
CLARK ROAD 1102 | 11
CLARKSVILLE 2103 | 2
CLARKSVILLE 2104 | 9
CLARKSVILLE 2106 | 1
CLARKSVILLE 2110 | 1
CLAY 1101 | 6
CLAY 1102 | 1
CLAY 1103 | 5
CLAYTON 2212 | 5
CLAYTON 2215 | 6
CLAYTON 2217 | 1
CLEAR LAKE 1101 | 7
CLOVERDALE 1101 | 2
CLOVERDALE 1102 | 7
COALINGA NO 2 1105 | 2
COARSEGOLD 2102 | 3
COARSEGOLD 2103 | 5
COARSEGOLD 2104 | 12
COLUMBIA HILL 1101 | 1
COPPERMINE 1104 | 2
CORNING 1101 | 4
CORNING 1102 | 5
CORRAL 1101 | 7
CORRAL 1102 | 1
CORRAL 1103 | 1
CORRAL SUB | 1
CORTINA 1101 | 1
COTATI 1102 | 1
COTATI 1103 | 2
COTATI 1105 | 6
COTTONWOOD 1101 | 2
COTTONWOOD 1102 | 3
COTTONWOOD 1103 | 5
COVELO 1101 | 5
CRESCENT MILLS 2101 | 6
CRESCENT MILLS SUB | 1
CURTIS 1701 | 3
CURTIS 1702 | 20
CURTIS 1703 | 14
CURTIS 1704 | 12
CURTIS 1705 | 8
CUYAMA 1103 | 3
CUYAMA 2101 | 1
CUYAMA 2102 | 1
DEL MONTE 2104 | 11
DESCHUTES 1101 | 4
DESCHUTES 1104 | 4
DEVILS DEN 1101 | 3
DIAMOND SPRINGS 1103 | 2
DIAMOND SPRINGS 1104 | 2
DIAMOND SPRINGS 1105 | 3
DIAMOND SPRINGS 1106 | 3
DIAMOND SPRINGS 1107 | 2
DOBBINS 1101 | 4
DOLAN ROAD 1101 | 4
DOS PALOS SUB | 1
DRUM 1101 | 4
DUNBAR 1101 | 5
DUNBAR 1102 | 7
DUNBAR 1103 | 4
DUNLAP 1102 | 29
DUNLAP 1103 | 12
EAST MARYSVILLE 1108 | 1
EAST QUINCY 1101 | 1
EDENVALE 1102 | 1
EDENVALE 2105 | 3
EEL RIVER 1102 | 3
EL DORADO PH 2101 | 11
ELECTRA 1101 | 5
ELECTRA 1102 | 2
ELECTRA SUB | 1
ELK CREEK 1101 | 9
EMERALD LAKE SUB | 1
FAIRVIEW 2207 | 3
FIREBAUGH SUB | 1
FITCH MOUNTAIN 1113 | 4
FOOTHILL 1101 | 2
FORESTHILL 1101 | 7
FORT BRAGG A 1102 | 6
FORT ROSS 1121 | 9
FORT SEWARD 1121 | 4
FORT SEWARD 1122 | 1
FREMONT 1104 | 2
FRENCH GULCH 1102 | 2
FROGTOWN 1701 | 14
FROGTOWN 1702 | 10
FRUITLAND 1141 | 1
FRUITLAND 1142 | 4
FULTON 1107 | 3
GABILAN 1101 | 4
GANSNER 1101 | 4
GARBERVILLE 1101 | 8
GARBERVILLE 1102 | 9
GARBERVILLE SUB | 1
GARCIA SUB | 1
GATES 1106 | 1
GERBER SUB | 1
GEYSERVILLE 1101 | 7
GEYSERVILLE 1102 | 5
GIRVAN 1101 | 6
GIRVAN 1102 | 2
GONZALES 1104 | 1
GRASS VALLEY 1101 | 4
GRASS VALLEY 1103 | 5
GRAYS FLAT SUB | 1
GREEN VALLEY 2101 | 13
GUALALA 1112 | 6
GUALALA SUB | 1
GUSTINE 1102 | 2
HALF MOON BAY 1101 | 2
HALF MOON BAY 1102 | 1
HALSEY 1101 | 3
HALSEY 1102 | 4
HAMILTON BRANCH 1101 | 1
HARRIS 1109 | 1
HARTLEY 1101 | 7
HARTLEY 1102 | 2
HATTON 1101 | 7
HATTON 1102 | 1
HERDLYN 1102 | 2
HICKS 2101 | 3
HICKS 2103 | 1
HIGGINS 1103 | 4
HIGGINS 1104 | 6
HIGGINS 1107 | 2
HIGGINS 1109 | 3
HIGGINS 1110 | 5
HIGHLANDS 1102 | 5
HIGHLANDS 1103 | 3
HIGHLANDS 1104 | 3
HOLLISTER 2102 | 3
HOLLISTER 2104 | 2
HOLLISTER 2105 | 2
HOLLISTER 2106 | 1
HONCUT 1102 | 1
HOOPA 1101 | 16
HOPLAND 1101 | 1
HORSESHOE 1101 | 2
HORSESHOE 1104 | 1
HUMBOLDT BAY 1102 | 1
IGNACIO 1104 | 1
INDIAN FLAT 1104 | 2
IONE 1101 | 4
JAMESON 1105 | 4
JESSUP 1101 | 7
JESSUP 1102 | 1
JOLON 1102 | 11
JOLON 1103 | 11
KANAKA 1101 | 1
KERCKHOFF 1101 | 1
KERN OIL 1106 | 3
KESWICK 1101 | 13
KETTLEMAN HILLS 2104 | 1
KING CITY 1102 | 1
KING CITY 1103 | 1
KING CITY 1106 | 1
KIRKER 2104 | 2
KIRKER 2105 | 1
KONOCTI 1102 | 2
KONOCTI 1108 | 5
LAKEVILLE 1102 | 6
LAKEWOOD 1103 | 1
LAKEWOOD 2107 | 3
LAKEWOOD 2109 | 1
LAKEWOOD 2224 | 1
LAKEWOOD 2227 | 1
LAMONT 1104 | 6
LAS POSITAS 2103 | 1
LAS POSITAS 2108 | 3
LAURELES 1111 | 12
LAURELES 1112 | 2
LAURELES SUB | 1
LAYTONVILLE 1101 | 3
LAYTONVILLE 1102 | 2
LINCOLN 1101 | 8
LINCOLN 1104 | 4
LLAGAS 2101 | 6
LOGAN CREEK 2102 | 2
LONE TREE 2105 | 1
LOS COCHES 1101 | 1
LOS GATOS 1101 | 1
LOS GATOS 1106 | 7
LOS GATOS 1107 | 7
LOS GATOS 1108 | 1
LOS MOLINOS 1101 | 1
LOS OSITOS 2101 | 6
LOS OSITOS 2102 | 1
LOS OSITOS 2103 | 5
LOYOLA 1102 | 1
LUCERNE 1103 | 5
LUCERNE 1106 | 1
MADISON 2101 | 18
MAGUNDEN 1108 | 3
MAPLE CREEK 1101 | 2
MARICOPA 1102 | 2
MARIPOSA 2101 | 8
MARIPOSA 2102 | 14
MARTELL 1101 | 4
MAXWELL 1102 | 1
MAXWELL 1105 | 3
MC ARTHUR 1101 | 12
MC ARTHUR SUB | 1
MEADOW LANE 2106 | 3
MENDOCINO 1101 | 1
MENLO 1102 | 5
MENLO 1103 | 2
MERCED FALLS 1102 | 2
MESA 1101 | 2
MIDDLETOWN 1101 | 6
MIDDLETOWN 1102 | 1
MIDDLETOWN SUB | 1
MILPITAS 1105 | 1
MILPITAS 1109 | 2
MIRABEL 1101 | 7
MIRABEL 1102 | 2
MIWUK 1701 | 5
MIWUK 1702 | 9
MOLINO 1101 | 2
MOLINO 1102 | 12
MOLINO 1104 | 1
MONTE RIO 1111 | 3
MONTE RIO 1112 | 4
MONTE RIO 1113 | 8
MONTICELLO 1101 | 12
MORAGA 1101 | 2
MORAGA 1103 | 1
MORGAN HILL 2104 | 3
MORGAN HILL 2105 | 7
MORGAN HILL 2109 | 1
MORGAN HILL 2111 | 10
MORRO BAY 1102 | 1
MOUNTAIN QUARRIES 2101 | 11
NAPA 1112 | 5
NARROWS 2101 | 3
NARROWS 2102 | 6
NARROWS 2105 | 10
NEWMAN 1105 | 1
NORTH BRANCH 1101 | 1
NORTH DUBLIN 2101 | 1
NORTH DUBLIN 2103 | 5
NORTH TOWER 2101 | 4
NOTRE DAME 1103 | 2
NOTRE DAME 1104 | 2
OAKHURST 1101 | 5
OAKHURST 1103 | 3
OAKLAND K 1104 | 2
OAKLAND X 1104 | 1
OAKLAND X 1106 | 1
OCEANO 1104 | 8
OILFIELDS 1102 | 1
OILFIELDS 1103 | 24
OLEMA 1101 | 1
OLETA 1101 | 4
OLETA 1102 | 4
OREGON TRAIL 1102 | 4
OREGON TRAIL 1103 | 2
OREGON TRAIL 1104 | 2
ORICK SUB | 1
ORO FINO 1101 | 1
ORO FINO 1102 | 4
ORO LOMA 1106 | 4
ORO LOMA SUB | 1
OROSI 1102 | 4
OROVILLE 1104 | 2
OTTER 1101 | 1
OTTER SUB | 1
PANOCHE 1103 | 1
PANORAMA 1101 | 2
PANORAMA 1102 | 1
PARADISE 1103 | 2
PARADISE 1105 | 1
PASO ROBLES 1103 | 7
PASO ROBLES 1104 | 4
PAUL SWEET 2102 | 1
PAUL SWEET 2106 | 6
PEABODY 2113 | 2
PENNGROVE 1101 | 2
PENRYN 1103 | 8
PENRYN 1105 | 6
PENRYN 1106 | 1
PENRYN 1107 | 8
PEORIA 1701 | 4
PEORIA 1704 | 10
PEORIA 1705 | 8
PERRY 1101 | 7
PETALUMA A SUB | 2
PETALUMA C 1108 | 11
PETALUMA C 1109 | 7
PHILO 1102 | 6
PHILO SUB | 1
PIERCY 2110 | 2
PIKE CITY 1101 | 1
PINE GROVE 1101 | 7
PINE GROVE 1102 | 10
PIT NO 3 2101 | 2
PIT NO 5 1101 | 6
PLACER 1103 | 3
PLACER 1104 | 1
PLACERVILLE 1111 | 1
PLACERVILLE 1112 | 1
PLACERVILLE 2106 | 19
POINT ARENA 1101 | 6
POINT ARENA SUB | 1
POINT MORETTI 1101 | 1
POINT MORETTI SUB | 1
POSO MOUNTAIN 2101 | 24
POSO MOUNTAIN 2103 | 7
POTTER VALLEY P H 1105 | 5
PRUNEDALE 1110 | 3
PUEBLO 1104 | 1
PUEBLO 1105 | 1
PUEBLO 2103 | 6
PUEBLO 2104 | 7
PURISIMA 1101 | 4
PUTAH CREEK 1102 | 3
RACETRACK 1703 | 16
RALSTON 1102 | 2
RAWSON SUB | 1
RED BLUFF 1101 | 5
RED BLUFF 1103 | 2
RED BLUFF 1104 | 2
RED BLUFF 1105 | 2
REDBUD 1101 | 4
REDBUD 1102 | 3
REEDLEY 1104 | 4
REEDLEY 1112 | 3
RESEARCH 2101 | 1
RESERVATION ROAD 1101 | 7
RESERVATION ROAD 1102 | 2
RESERVATION ROAD SUB | 1
RIO DELL 1101 | 7
RIO DELL 1102 | 1
RISING RIVER 1101 | 1
ROB ROY 2104 | 13
ROB ROY 2105 | 2
ROSSMOOR 1101 | 1
ROSSMOOR 1102 | 1
ROSSMOOR 1106 | 3
ROSSMOOR 1108 | 7
ROSSMOOR 1109 | 5
SALT SPRINGS 2101 | 7
SALT SPRINGS 2102 | 1
SAN ARDO 1102 | 5
SAN BENITO 2101 | 1
SAN BENITO 2104 | 8
SAN BERNARD 1101 | 1
SAN JOAQUIN #2 1103 | 2
SAN JOAQUIN #3 1101 | 2
SAN JOAQUIN #3 1102 | 1
SAN JOAQUIN #3 1103 | 1
SAN JUSTO 1101 | 9
SAN LUIS OBISPO 1101 | 5
SAN LUIS OBISPO 1103 | 2
SAN LUIS OBISPO 1104 | 12
SAN LUIS OBISPO 1107 | 3
SAN MIGUEL 1104 | 1
SAN MIGUEL 1105 | 1
SAN MIGUEL 1106 | 1
SAN RAFAEL 1101 | 1
SAN RAFAEL 1104 | 2
SAN RAFAEL 1107 | 3
SAN RAFAEL 1108 | 1
SAN RAMON 2107 | 1
SAN RAMON 2108 | 1
SAND CREEK 1103 | 9
SANTA MARIA 1108 | 1
SANTA NELLA 1101 | 3
SANTA RITA SUB | 1
SANTA ROSA A 1104 | 2
SANTA YNEZ 1101 | 7
SANTA YNEZ 1102 | 6
SANTA YNEZ 1104 | 4
SARATOGA 1103 | 2
SARATOGA 1106 | 5
SARATOGA 1107 | 2
SEACLIFF 0401 | 1
SHADY GLEN 1101 | 2
SHADY GLEN 1102 | 4
SHEPHERD 2111 | 1
SHINGLE SPRINGS 1103 | 2
SHINGLE SPRINGS 1104 | 2
SHINGLE SPRINGS 2108 | 4
SHINGLE SPRINGS 2109 | 11
SHINGLE SPRINGS 2110 | 4
SILVERADO 2102 | 7
SILVERADO 2103 | 1
SILVERADO 2104 | 17
SILVERADO 2105 | 7
SISQUOC 1101 | 2
SISQUOC 1102 | 6
SISQUOC 1103 | 4
SMARTVILLE 1101 | 1
SMARTVILLE SUB | 1
SNEATH LANE 1101 | 1
SOBRANTE 1101 | 4
SOBRANTE 1102 | 1
SOBRANTE 1103 | 4
SOLEDAD 2101 | 1
SOLEDAD 2102 | 1
SOLEDAD 2104 | 5
SOLEDAD 2105 | 5
SONOMA 1104 | 4
SONOMA 1105 | 4
SPAULDING 1101 | 1
SPENCE 1101 | 1
SPENCE 1104 | 1
SPRING GAP 1702 | 5
STAFFORD 1102 | 5
STANISLAUS 1701 | 17
STANISLAUS 1702 | 8
STELLING 1109 | 2
STELLING 1110 | 1
STILLWATER 1101 | 1
STILLWATER 1102 | 2
STONE CORRAL 1108 | 3
SUMMIT 1101 | 1
SUMMIT 1102 | 1
SUNOL 1101 | 1
SWIFT 2110 | 1
SYCAMORE CREEK 1109 | 1
SYCAMORE CREEK 1111 | 2
TAR FLAT 0401 | 1
TAR FLAT 0402 | 5
TASSAJARA 2103 | 2
TASSAJARA 2104 | 3
TASSAJARA 2107 | 1
TASSAJARA 2108 | 4
TASSAJARA 2112 | 1
TASSAJARA 2113 | 1
TEJON 1102 | 1
TEMBLOR 1104 | 2
TEMPLETON 2108 | 1
TEMPLETON 2110 | 4
TEMPLETON 2111 | 7
TEMPLETON 2112 | 1
TEMPLETON 2113 | 13
TEMPORARY CARBONA 1101 | 2
TIDEWATER 2106 | 5
TIGER CREEK 0201 | 1
TIVY VALLEY 1107 | 10
TRES PINOS 1111 | 1
TRINIDAD SUB | 1
TULUCAY 1101 | 1
TYLER / RAWSON SUB | 1
TYLER 1105 | 3
TYLER SUB | 3
UKIAH 1111 | 1
UKIAH 1113 | 1
UKIAH 1114 | 8
UKIAH 1115 | 1
UPPER LAKE 1101 | 5
VACA DIXON 1101 | 1
VACA DIXON 1105 | 1
VACAVILLE 1104 | 2
VACAVILLE 1108 | 2
VACAVILLE 1111 | 1
Valley Springs 1101 | 8
VALLEY VIEW 1103 | 1
VASCO 1102 | 2
VINEYARD 2107 | 1
VINEYARD 2108 | 2
VINEYARD 2110 | 1
VOLTA 1101 | 7
VOLTA 1102 | 6
WEIMAR 1101 | 5
WEIMAR 1102 | 1
WEST POINT 1101 | 2
WEST POINT 1102 | 4
WESTLEY 1101 | 1
WESTLEY 1103 | 1
WHEATLAND 1105 | 1
WHITMORE 1101 | 3
WILDWOOD 1101 | 1
WILLITS 1103 | 10
WILLITS 1104 | 2
WILLOW CREEK 1101 | 3
WILLOW CREEK 1102 | 1
WILLOW CREEK 1103 | 11
WILLOW PASS 2108 | 1
WINDSOR 1103 | 1
WISE 1102 | 6
WOODACRE 1101 | 4
WOODACRE 1102 | 2
WOODSIDE 1101 | 4
WOODSIDE 1104 | 1
WYANDOTTE 1102 | 1
WYANDOTTE 1103 | 3
WYANDOTTE 1106 | 1
WYANDOTTE 1107 | 7
WYANDOTTE 1109 | 3
WYANDOTTE 1110 | 3
ZACA 1101 | 5
ZACA 1102 | 10
Grand Total | 2263

## YTD EPSS Outages_CAIDI
Circuit | Sum of CESO | Sum of Customer_Minutes | CAIDI
ALHAMBRA 1105 | 1023 | 179913 | 175.868
ALLEGHANY 1101 | 287 | 106676 | 371.6934
ALLEGHANY 1102 | 164 | 49036 | 299
ALTO 1124 | 898 | 124140 | 138.2405
ALTO 1125 | 2752 | 773707 | 281.1435
ANDERSON 1101 | 228 | 12631 | 55.3991
ANNAPOLIS 1101 | 304 | 54541 | 179.4112
ANNAPOLIS SUB | 229 | 21984 | 96
ANTELOPE 1101 | 45 | 26685 | 593
ANTLER 1101 | 867 | 187585 | 216.361
APPLE HILL 1104 | 6273 | 959617 | 152.9758
APPLE HILL 2102 | 28293 | 5375682 | 190.0004
ARCATA 1121 | 326 | 31946 | 97.9939
ARCATA 1122 | 356 | 25489 | 71.5983
ATASCADERO 1101 | 905 | 172666 | 190.7912
ATASCADERO 1102 | 5385 | 413243 | 76.7396
ATASCADERO 1103 | 7111 | 751762 | 105.7182
AUBERRY 1101 | 4564 | 1074785 | 235.4919
AUBERRY 1102 | 665 | 125773 | 189.1323
AUBURN 1102 | 992 | 195273 | 196.8478
AVENA 1702 | 368 | 67960 | 184.6739
AVENAL 2101 | 3349 | 1641183 | 490.0517
BALCH NO 1 1101 | 27 | 16875 | 625
BANGOR 1101 | 5251 | 1171692 | 223.1369
BAY MEADOWS 2102 | 1160 | 124505 | 107.3319
BAYWOOD 1101 | 588 | 60494 | 102.881
BEAR VALLEY 2101 | 1035 | 318768 | 307.9884
BEAR VALLEY 2105 | 2015 | 294008 | 145.9097
BELL 1107 | 861 | 112185 | 130.2962
BELL 1108 | 2283 | 274321 | 120.1581
BELLEVUE 2101 | 6092 | 631883 | 103.7234
BEN LOMOND 0401 | 3749 | 1105694 | 294.9304
BEN LOMOND 1101 | 2238 | 190174 | 84.975
BIG BASIN 1101 | 230 | 8970 | 39
BIG BASIN 1102 | 2265 | 372935 | 164.6512
BIG BEND 1102 | 676 | 133886 | 198.0562
BIG MEADOWS 2101 | 1101 | 135079 | 122.6876
BOLINAS 1101 | 1384 | 314784 | 227.4451
BONNIE NOOK 1102 | 1511 | 100524 | 66.5281
BORONDA SUB | 1788 | 237076 | 132.5928
BRENTWOOD 2105 | 2125 | 160076 | 75.3299
BRIDGEVILLE 1101 | 3251 | 2256498 | 694.0935
BRIDGEVILLE 1102 | 55 | 10670 | 194
BROWNS VALLEY 1101 | 525 | 311452 | 593.2419
BRUNSWICK 1102 | 3161 | 245978 | 77.8165
BRUNSWICK 1103 | 2560 | 167836 | 65.5609
BRUNSWICK 1104 | 3095 | 314232 | 101.5289
BRUNSWICK 1105 | 18248 | 2142640 | 117.4178
BRUNSWICK 1106 | 21276 | 1349690 | 63.4372
BRUNSWICK 1107 | 4030 | 288094 | 71.4873
BUCKS CREEK 1103 | 509 | 96288 | 189.1709
BUELLTON 1101 | 2006 | 172094 | 85.7896
BUELLTON 1102 | 2033 | 319181 | 157
BURNEY 1101 | 88 | 4780 | 54.3182
BURNS 2101 | 17400 | 6069573 | 348.826
BUTTE 1105 | 405 | 63509 | 156.8123
CABRILLO 1103 | 2246 | 639922 | 284.9163
CABRILLO 1104 | 2773 | 345029 | 124.4245
CAL WATER 1102 | 54 | 31782 | 588.5556
CALAVERAS CEMENT 1101 | 15839 | 3098274 | 195.6105
CALISTOGA 1101 | 3472 | 1107860 | 319.0841
CALISTOGA 1102 | 3324 | 461832 | 138.9386
CALPELLA 1101 | 2205 | 375471 | 170.2816
CALPELLA 1102 | 87 | 7830 | 90
CAMBRIA 1102 | 332 | 32204 | 97
CAMP EVERS 2103 | 5954 | 438087 | 73.5786
CAMP EVERS 2104 | 6982 | 1144991 | 163.9918
CAMP EVERS 2105 | 13412 | 1209014 | 90.1442
CAMP EVERS 2106 | 20288 | 2544205 | 125.4044
CANTUA 1103 | 295 | 22800 | 77.2881
CARLOTTA 1121 | 1153 | 99158 | 86
CARNERAS 1103 | 14 | 6916 | 494
CASTRO VALLEY 1108 | 1852 | 418314 | 225.8715
CASTRO VALLEY 1110 | 11992 | 1203609 | 100.3677
CASTRO VALLEY 1111 | 86 | 15830 | 184.0698
CAYETANO 2109 | 6283 | 1149819 | 183.0048
CAYETANO 2111 | 4176 | 1073972 | 257.1772
CAYUCOS 1101 | 660 | 134118 | 203.2091
CAYUCOS 1102 | 155 | 135493 | 874.1484
CEDAR CREEK 1101 | 1455 | 242198 | 166.4591
CHALLENGE 1101 | 1261 | 302097 | 239.5694
CHALLENGE 1102 | 198 | 35154 | 177.5455
CHESTER SUB | 1661 | 214590 | 129.1933
CHOLAME 1101 | 572 | 130295 | 227.7885
CHOLAME 2102 | 1683 | 308805 | 183.4848
CLARK ROAD 1101 | 25 | 32125 | 1285
CLARK ROAD 1102 | 6205 | 1952725 | 314.7019
CLARKSVILLE 2103 | 755 | 125432 | 166.1351
CLARKSVILLE 2104 | 10062 | 1838689 | 182.7359
CLARKSVILLE 2106 | 847 | 89782 | 106
CLARKSVILLE 2110 | 4082 | 553016 | 135.4767
CLAY 1101 | 5385 | 591469 | 109.8364
CLAY 1102 | 3 | 365 | 121.6667
CLAY 1103 | 4017 | 992576 | 247.0939
CLAYTON 2212 | 4436 | 426132 | 96.0622
CLAYTON 2215 | 18721 | 4548103 | 242.9412
CLAYTON 2217 | 5333 | 1403361 | 263.1466
CLEAR LAKE 1101 | 3928 | 346575 | 88.2319
CLOVERDALE 1101 | 258 | 79219 | 307.0504
CLOVERDALE 1102 | 4864 | 442055 | 90.883
COALINGA NO 2 1105 | 322 | 40250 | 125
COARSEGOLD 2102 | 4271 | 897223 | 210.0733
COARSEGOLD 2103 | 3874 | 537562 | 138.7615
COARSEGOLD 2104 | 21905 | 2810927 | 128.3235
COLUMBIA HILL 1101 | 37 | 7584 | 204.973
COPPERMINE 1104 | 167 | 111180 | 665.7485
CORNING 1101 | 1306 | 239313 | 183.2412
CORNING 1102 | 1634 | 275685 | 168.7179
CORRAL 1101 | 1660 | 273121 | 164.5307
CORRAL 1102 | 4154 | 787595 | 189.5992
CORRAL 1103 | 139 | 5560 | 40
CORRAL SUB | 5722 | 928190 | 162.2143
CORTINA 1101 | 24 | 2592 | 108
COTATI 1102 | 129 | 41802 | 324.0465
COTATI 1103 | 1221 | 108368 | 88.7535
COTATI 1105 | 4038 | 559147 | 138.4713
COTTONWOOD 1101 | 489 | 160148 | 327.501
COTTONWOOD 1102 | 1259 | 537621 | 427.0222
COTTONWOOD 1103 | 971 | 82097 | 84.5489
COVELO 1101 | 3186 | 507556 | 159.3082
CRESCENT MILLS 2101 | 7018 | 402616 | 57.3691
CRESCENT MILLS SUB | 1529 | 153374 | 100.31
CURTIS 1701 | 7178 | 2828256 | 394.0173
CURTIS 1702 | 15774 | 7649312 | 484.9317
CURTIS 1703 | 31623 | 19298848 | 610.2788
CURTIS 1704 | 14852 | 4426837 | 298.0634
CURTIS 1705 | 4506 | 1118370 | 248.1957
CUYAMA 1103 | 291 | 63438 | 218
CUYAMA 2101 | 124 | 31372 | 253
CUYAMA 2102 | 21 | 18396 | 876
DEL MONTE 2104 | 15908 | 1617915 | 101.7045
DESCHUTES 1101 | 3819 | 692550 | 181.3433
DESCHUTES 1104 | 838 | 47358 | 56.5131
DEVILS DEN 1101 | 201 | 64014 | 318.4776
DIAMOND SPRINGS 1103 | 3053 | 1115650 | 365.4274
DIAMOND SPRINGS 1104 | 1121 | 291438 | 259.9804
DIAMOND SPRINGS 1105 | 3329 | 339909 | 102.1054
DIAMOND SPRINGS 1106 | 1832 | 450930 | 246.1408
DIAMOND SPRINGS 1107 | 2793 | 208950 | 74.812
DOBBINS 1101 | 2343 | 321786 | 137.3393
DOLAN ROAD 1101 | 2321 | 218868 | 94.299
DOS PALOS SUB | 2574 | 141666 | 55.0373
DRUM 1101 | 810 | 399042 | 492.6444
DUNBAR 1101 | 6320 | 1136154 | 179.7712
DUNBAR 1102 | 3546 | 831868 | 234.5933
DUNBAR 1103 | 10734 | 1861658 | 173.4356
DUNLAP 1102 | 2661 | 904134 | 339.7723
DUNLAP 1103 | 3850 | 1529757 | 397.3395
EAST MARYSVILLE 1108 | 1003 | 793007 | 790.6351
EAST QUINCY 1101 | 1001 | 163163 | 163
EDENVALE 1102 | 1017 | 192613 | 189.3933
EDENVALE 2105 | 12323 | 1475390 | 119.7265
EEL RIVER 1102 | 221 | 53291 | 241.1357
EL DORADO PH 2101 | 18978 | 4768097 | 251.2434
ELECTRA 1101 | 2545 | 542233 | 213.0582
ELECTRA 1102 | 843 | 76594 | 90.8588
ELECTRA SUB | 1102 | 64294 | 58.343
ELK CREEK 1101 | 4336 | 1465538 | 337.9931
EMERALD LAKE SUB | 624 | 48015 | 76.9471
FAIRVIEW 2207 | 2753 | 265919 | 96.5924
FIREBAUGH SUB | 3659 | 177470 | 48.5023
FITCH MOUNTAIN 1113 | 4310 | 319092 | 74.0353
FOOTHILL 1101 | 404 | 29904 | 74.0198
FORESTHILL 1101 | 11655 | 1927842 | 165.409
FORT BRAGG A 1102 | 1351 | 196050 | 145.1147
FORT ROSS 1121 | 1063 | 93547 | 88.0028
FORT SEWARD 1121 | 563 | 126567 | 224.8082
FORT SEWARD 1122 | 101 | 21630 | 214.1584
FREMONT 1104 | 52 | 12142 | 233.5
FRENCH GULCH 1102 | 34 | 21213 | 623.9118
FROGTOWN 1701 | 30311 | 7464912 | 246.2773
FROGTOWN 1702 | 8210 | 1505638 | 183.3907
FRUITLAND 1141 | 21 | 651 | 31
FRUITLAND 1142 | 1226 | 130165 | 106.1705
FULTON 1107 | 2817 | 302689 | 107.4508
GABILAN 1101 | 1133 | 55106 | 48.6372
GANSNER 1101 | 3682 | 763322 | 207.3118
GARBERVILLE 1101 | 3495 | 475232 | 135.9748
GARBERVILLE 1102 | 5740 | 1554490 | 270.8171
GARBERVILLE SUB | 1820 | 123302 | 67.7484
GARCIA SUB | 9 | 864 | 96
GATES 1106 | 112 | 31136 | 278
GERBER SUB | 1486 | 163460 | 110
GEYSERVILLE 1101 | 3546 | 1389632 | 391.8872
GEYSERVILLE 1102 | 739 | 107773 | 145.8363
GIRVAN 1101 | 4573 | 611742 | 133.7726
GIRVAN 1102 | 1154 | 79710 | 69.0728
GONZALES 1104 | 94 | 102836 | 1094
GRASS VALLEY 1101 | 3579 | 538231 | 150.3859
GRASS VALLEY 1103 | 2581 | 772487 | 299.2976
GRAYS FLAT SUB | 1829 | 229786 | 125.6348
GREEN VALLEY 2101 | 2240 | 421048 | 187.9679
GUALALA 1112 | 9445 | 842325 | 89.1821
GUALALA SUB | 3794 | 364224 | 96
GUSTINE 1102 | 687 | 106316 | 154.754
HALF MOON BAY 1101 | 2941 | 342058 | 116.3067
HALF MOON BAY 1102 | 3270 | 124952 | 38.2116
HALSEY 1101 | 5261 | 607961 | 115.56
HALSEY 1102 | 4265 | 850846 | 199.495
HAMILTON BRANCH 1101 | 206 | 17716 | 86
HARRIS 1109 | 16 | 800 | 50
HARTLEY 1101 | 4227 | 349646 | 82.7173
HARTLEY 1102 | 1844 | 144754 | 78.5
HATTON 1101 | 15197 | 1371760 | 90.2652
HATTON 1102 | 2146 | 480784 | 224.0373
HERDLYN 1102 | 1587 | 309434 | 194.9805
HICKS 2101 | 6619 | 1882887 | 284.467
HICKS 2103 | 417 | 29190 | 70
HIGGINS 1103 | 2927 | 819489 | 279.9757
HIGGINS 1104 | 11237 | 1006009 | 89.5265
HIGGINS 1107 | 1963 | 211762 | 107.8767
HIGGINS 1109 | 1533 | 148816 | 97.075
HIGGINS 1110 | 4589 | 819191 | 178.5119
HIGHLANDS 1102 | 5691 | 384911 | 67.635
HIGHLANDS 1103 | 2261 | 1751321 | 774.5781
HIGHLANDS 1104 | 1150 | 97785 | 85.0304
HOLLISTER 2102 | 285 | 37742 | 132.4281
HOLLISTER 2104 | 180 | 18868 | 104.8222
HOLLISTER 2105 | 253 | 13079 | 51.6957
HOLLISTER 2106 | 55 | 5995 | 109
HONCUT 1102 | 93 | 10788 | 116
HOOPA 1101 | 12218 | 4729263 | 387.0734
HOPLAND 1101 | 424 | 11872 | 28
HORSESHOE 1101 | 444 | 102760 | 231.4414
HORSESHOE 1104 | 388 | 75133 | 193.6418
HUMBOLDT BAY 1102 | 220 | 26806 | 121.8455
IGNACIO 1104 | 293 | 34281 | 117
INDIAN FLAT 1104 | 1260 | 264172 | 209.6603
IONE 1101 | 1332 | 284198 | 213.3619
JAMESON 1105 | 1196 | 155512 | 130.0268
JESSUP 1101 | 6946 | 1648130 | 237.2776
JESSUP 1102 | 1517 | 154149 | 101.6144
JOLON 1102 | 2830 | 504795 | 178.3728
JOLON 1103 | 143 | 21212 | 148.3357
KANAKA 1101 | 58 | 9362 | 161.4138
KERCKHOFF 1101 | 30 | 33870 | 1129
KERN OIL 1106 | 258 | 19414 | 75.2481
KESWICK 1101 | 594 | 89013 | 149.8535
KETTLEMAN HILLS 2104 | 1 | 164 | 164
KING CITY 1102 | 62 | 6343 | 102.3065
KING CITY 1103 | 794 | 45762 | 57.6348
KING CITY 1106 | 124 | 17856 | 144
KIRKER 2104 | 6527 | 752824 | 115.34
KIRKER 2105 | 2201 | 166481 | 75.6388
KONOCTI 1102 | 1048 | 150229 | 143.3483
KONOCTI 1108 | 2825 | 471943 | 167.0595
LAKEVILLE 1102 | 399 | 132140 | 331.1779
LAKEWOOD 1103 | 79 | 7110 | 90
LAKEWOOD 2107 | 3067 | 259796 | 84.7069
LAKEWOOD 2109 | 142 | 31240 | 220
LAKEWOOD 2224 | 323 | 44975 | 139.2415
LAKEWOOD 2227 | 1281 | 165498 | 129.1944
LAMONT 1104 | 315 | 39432 | 125.181
LAS POSITAS 2103 | 3 | 2070 | 690
LAS POSITAS 2108 | 5621 | 1202817 | 213.9863
LAURELES 1111 | 4807 | 2409278 | 501.202
LAURELES 1112 | 3195 | 253681 | 79.3994
LAURELES SUB | 3526 | 1237724 | 351.0278
LAYTONVILLE 1101 | 648 | 372450 | 574.7685
LAYTONVILLE 1102 | 384 | 136302 | 354.9531
LINCOLN 1101 | 1376 | 142154 | 103.3096
LINCOLN 1104 | 1099 | 131024 | 119.2211
LLAGAS 2101 | 1886 | 348297 | 184.675
LOGAN CREEK 2102 | 193 | 24699 | 127.9741
LONE TREE 2105 | 2635 | 477303 | 181.1397
LOS COCHES 1101 | 18 | 10553 | 586.2778
LOS GATOS 1101 | 666 | 128538 | 193
LOS GATOS 1106 | 7929 | 3005130 | 379.0049
LOS GATOS 1107 | 7801 | 1656946 | 212.4017
LOS GATOS 1108 | 789 | 66276 | 84
LOS MOLINOS 1101 | 234 | 15992 | 68.3419
LOS OSITOS 2101 | 920 | 481799 | 523.6946
LOS OSITOS 2102 | 95 | 12635 | 133
LOS OSITOS 2103 | 1006 | 333009 | 331.0229
LOYOLA 1102 | 40 | 3240 | 81
LUCERNE 1103 | 1674 | 156266 | 93.3489
LUCERNE 1106 | 1171 | 78502 | 67.0384
MADISON 2101 | 12084 | 3005529 | 248.7197
MAGUNDEN 1108 | 303 | 29142 | 96.1782
MAPLE CREEK 1101 | 218 | 116080 | 532.4771
MARICOPA 1102 | 765 | 113013 | 147.7294
MARIPOSA 2101 | 10358 | 801793 | 77.4081
MARIPOSA 2102 | 20710 | 2807218 | 135.5489
MARTELL 1101 | 1822 | 241636 | 132.6213
MAXWELL 1102 | 160 | 30560 | 191
MAXWELL 1105 | 224 | 52971 | 236.4777
MC ARTHUR 1101 | 3245 | 742417 | 228.788
MC ARTHUR SUB | 1736 | 608552 | 350.5484
MEADOW LANE 2106 | 9077 | 1200703 | 132.2797
MENDOCINO 1101 | 748 | 47292 | 63.2246
MENLO 1102 | 349 | 102944 | 294.9685
MENLO 1103 | 449 | 103768 | 231.1091
MERCED FALLS 1102 | 1972 | 220533 | 111.8322
MESA 1101 | 1512 | 174284 | 115.2672
MIDDLETOWN 1101 | 6278 | 1187744 | 189.1915
MIDDLETOWN 1102 | 441 | 57227 | 129.7664
MIDDLETOWN SUB | 4692 | 312239 | 66.5471
MILPITAS 1105 | 4122 | 428839 | 104.0366
MILPITAS 1109 | 227 | 150680 | 663.7885
MIRABEL 1101 | 1642 | 534221 | 325.3477
MIRABEL 1102 | 1481 | 239287 | 161.5712
MIWUK 1701 | 4779 | 2203185 | 461.0138
MIWUK 1702 | 19216 | 9961249 | 518.3831
MOLINO 1101 | 751 | 418992 | 557.9121
MOLINO 1102 | 13746 | 3642061 | 264.9542
MOLINO 1104 | 233 | 78557 | 337.1545
MONTE RIO 1111 | 1508 | 234981 | 155.8229
MONTE RIO 1112 | 747 | 387498 | 518.739
MONTE RIO 1113 | 14406 | 3442687 | 238.9759
MONTICELLO 1101 | 4589 | 1335764 | 291.0795
MORAGA 1101 | 2616 | 219975 | 84.0883
MORAGA 1103 | 2366 | 331660 | 140.1775
MORGAN HILL 2104 | 1160 | 189145 | 163.056
MORGAN HILL 2105 | 12983 | 2250710 | 173.3582
MORGAN HILL 2109 | 4190 | 380364 | 90.779
MORGAN HILL 2111 | 4172 | 512249 | 122.7826
MORRO BAY 1102 | 2440 | 108620 | 44.5164
MOUNTAIN QUARRIES 2101 | 7915 | 853423 | 107.8235
NAPA 1112 | 2755 | 179591 | 65.1873
NARROWS 2101 | 1503 | 681570 | 453.4731
NARROWS 2102 | 8040 | 787712 | 97.9741
NARROWS 2105 | 13192 | 3265666 | 247.549
NEWMAN 1105 | 180 | 14046 | 78.0333
NORTH BRANCH 1101 | 45 | 8205 | 182.3333
NORTH DUBLIN 2101 | 5550 | 837549 | 150.9097
NORTH DUBLIN 2103 | 10430 | 1370182 | 131.3693
NORTH TOWER 2101 | 7443 | 2108658 | 283.3075
NOTRE DAME 1103 | 226 | 30397 | 134.5
NOTRE DAME 1104 | 162 | 102431 | 632.2901
OAKHURST 1101 | 6250 | 686031 | 109.765
OAKHURST 1103 | 2755 | 717468 | 260.424
OAKLAND K 1104 | 3268 | 854214 | 261.3874
OAKLAND X 1104 | 609 | 61509 | 101
OAKLAND X 1106 | 1330 | 190180 | 142.9925
OCEANO 1104 | 8956 | 938143 | 104.7502
OILFIELDS 1102 | 46 | 40664 | 884
OILFIELDS 1103 | 26021 | 5193943 | 199.6058
OLEMA 1101 | 132 | 3036 | 23
OLETA 1101 | 3715 | 359277 | 96.7098
OLETA 1102 | 2940 | 695166 | 236.451
OREGON TRAIL 1102 | 2247 | 317371 | 141.2421
OREGON TRAIL 1103 | 1714 | 814604 | 475.2649
OREGON TRAIL 1104 | 1664 | 240206 | 144.3546
ORICK SUB | 348 | 118492 | 340.4943
ORO FINO 1101 | 1044 | 89348 | 85.5824
ORO FINO 1102 | 2912 | 294447 | 101.115
ORO LOMA 1106 | 837 | 80850 | 96.595
ORO LOMA SUB | 632 | 37176 | 58.8228
OROSI 1102 | 1494 | 230330 | 154.17
OROVILLE 1104 | 3312 | 470958 | 142.1975
OTTER 1101 | 378 | 28390 | 75.1058
OTTER SUB | 1114 | 139250 | 125
PANOCHE 1103 | 152 | 58064 | 382
PANORAMA 1101 | 3403 | 235365 | 69.164
PANORAMA 1102 | 10 | 9460 | 946
PARADISE 1103 | 1719 | 109445 | 63.6678
PARADISE 1105 | 1254 | 47762 | 38.0877
PASO ROBLES 1103 | 9708 | 558900 | 57.5711
PASO ROBLES 1104 | 1308 | 384737 | 294.1414
PAUL SWEET 2102 | 1659 | 122766 | 74
PAUL SWEET 2106 | 1348 | 170411 | 126.4177
PEABODY 2113 | 10539 | 1215643 | 115.3471
PENNGROVE 1101 | 335 | 35196 | 105.0627
PENRYN 1103 | 3964 | 378537 | 95.4937
PENRYN 1105 | 3632 | 227708 | 62.6949
PENRYN 1106 | 924 | 36960 | 40
PENRYN 1107 | 11730 | 1470686 | 125.3782
PEORIA 1701 | 5420 | 917912 | 169.3565
PEORIA 1704 | 14543 | 3690116 | 253.7383
PEORIA 1705 | 9695 | 3531842 | 364.2952
PERRY 1101 | 11702 | 1268513 | 108.4014
PETALUMA A SUB | 2519 | 389117 | 154.4728
PETALUMA C 1108 | 4776 | 474304 | 99.3099
PETALUMA C 1109 | 3954 | 367229 | 92.8753
PHILO 1102 | 4313 | 753754 | 174.7633
PHILO SUB | 2222 | 114083 | 51.3425
PIERCY 2110 | 1430 | 126366 | 88.3678
PIKE CITY 1101 | 87 | 24186 | 278
PINE GROVE 1101 | 4906 | 336694 | 68.629
PINE GROVE 1102 | 13746 | 3068573 | 223.2339
PIT NO 3 2101 | 257 | 37744 | 146.8638
PIT NO 5 1101 | 822 | 118156 | 143.7421
PLACER 1103 | 4790 | 1113366 | 232.4355
PLACER 1104 | 992 | 167949 | 169.3034
PLACERVILLE 1111 | 381 | 41529 | 109
PLACERVILLE 1112 | 481 | 37037 | 77
PLACERVILLE 2106 | 34896 | 7334637 | 210.1856
POINT ARENA 1101 | 1136 | 127566 | 112.294
POINT ARENA SUB | 912 | 87552 | 96
POINT MORETTI 1101 | 64 | 8128 | 127
POINT MORETTI SUB | 781 | 163708 | 209.6133
POSO MOUNTAIN 2101 | 1777 | 633233 | 356.3495
POSO MOUNTAIN 2103 | 120 | 104621 | 871.8417
POTTER VALLEY P H 1105 | 987 | 86361 | 87.4985
PRUNEDALE 1110 | 1024 | 139996 | 136.7148
PUEBLO 1104 | 559 | 65140 | 116.5295
PUEBLO 1105 | 282 | 147648 | 523.5745
PUEBLO 2103 | 6834 | 1260627 | 184.464
PUEBLO 2104 | 3060 | 641837 | 209.7507
PURISIMA 1101 | 2659 | 477753 | 179.6739
PUTAH CREEK 1102 | 388 | 32780 | 84.4845
RACETRACK 1703 | 12185 | 3008562 | 246.907
RALSTON 1102 | 232 | 13920 | 60
RAWSON SUB | 2524 | 35336 | 14
RED BLUFF 1101 | 2201 | 285454 | 129.6929
RED BLUFF 1103 | 2941 | 255200 | 86.7732
RED BLUFF 1104 | 724 | 137606 | 190.0635
RED BLUFF 1105 | 2002 | 311245 | 155.467
REDBUD 1101 | 1079 | 173967 | 161.2298
REDBUD 1102 | 7694 | 989473 | 128.6032
REEDLEY 1104 | 104 | 13455 | 129.375
REEDLEY 1112 | 619 | 84697 | 136.8288
RESEARCH 2101 | 406 | 149814 | 369
RESERVATION ROAD 1101 | 8085 | 1010387 | 124.9706
RESERVATION ROAD 1102 | 2765 | 449068 | 162.4116
RESERVATION ROAD SUB | 4547 | 2228403 | 490.082
RIO DELL 1101 | 2860 | 958912 | 335.2839
RIO DELL 1102 | 48 | 6148 | 128.0833
RISING RIVER 1101 | 527 | 59330 | 112.5806
ROB ROY 2104 | 27422 | 2686646 | 97.9741
ROB ROY 2105 | 1054 | 77455 | 73.4867
ROSSMOOR 1101 | 352 | 145777 | 414.1392
ROSSMOOR 1102 | 3095 | 225935 | 73
ROSSMOOR 1106 | 6116 | 544146 | 88.9709
ROSSMOOR 1108 | 12830 | 1452963 | 113.2473
ROSSMOOR 1109 | 870 | 94166 | 108.2368
SALT SPRINGS 2101 | 4730 | 1372456 | 290.1598
SALT SPRINGS 2102 | 2014 | 2108939 | 1047.1395
SAN ARDO 1102 | 902 | 414711 | 459.7683
SAN BENITO 2101 | 36 | 4560 | 126.6667
SAN BENITO 2104 | 10228 | 1193358 | 116.6756
SAN BERNARD 1101 | 17 | 1445 | 85
SAN JOAQUIN #2 1103 | 940 | 209922 | 223.3213
SAN JOAQUIN #3 1101 | 1254 | 59565 | 47.5
SAN JOAQUIN #3 1102 | 262 | 39018 | 148.9237
SAN JOAQUIN #3 1103 | 1377 | 340825 | 247.5127
SAN JUSTO 1101 | 1508 | 194895 | 129.2407
SAN LUIS OBISPO 1101 | 9284 | 836376 | 90.0879
SAN LUIS OBISPO 1103 | 2581 | 346489 | 134.246
SAN LUIS OBISPO 1104 | 5659 | 972832 | 171.9088
SAN LUIS OBISPO 1107 | 6822 | 539870 | 79.1366
SAN MIGUEL 1104 | 241 | 19915 | 82.6349
SAN MIGUEL 1105 | 17 | 884 | 52
SAN MIGUEL 1106 | 90 | 18510 | 205.6667
SAN RAFAEL 1101 | 1300 | 243924 | 187.6338
SAN RAFAEL 1104 | 2818 | 1275213 | 452.5241
SAN RAFAEL 1107 | 5320 | 1428804 | 268.5722
SAN RAFAEL 1108 | 781 | 84447 | 108.1268
SAN RAMON 2107 | 829 | 92019 | 111
SAN RAMON 2108 | 94 | 50860 | 541.0638
SAND CREEK 1103 | 3560 | 873094 | 245.2511
SANTA MARIA 1108 | 445 | 375896 | 844.7101
SANTA NELLA 1101 | 333 | 65237 | 195.9069
SANTA RITA SUB | 972 | 156492 | 161
SANTA ROSA A 1104 | 3282 | 545891 | 166.3288
SANTA YNEZ 1101 | 1852 | 474958 | 256.4568
SANTA YNEZ 1102 | 3749 | 531629 | 141.8055
SANTA YNEZ 1104 | 2156 | 203601 | 94.4346
SARATOGA 1103 | 1322 | 157915 | 119.4516
SARATOGA 1106 | 3303 | 482311 | 146.0221
SARATOGA 1107 | 676 | 57066 | 84.4172
SEACLIFF 0401 | 213 | 17466 | 82
SHADY GLEN 1101 | 1169 | 143221 | 122.5158
SHADY GLEN 1102 | 1158 | 129270 | 111.6321
SHEPHERD 2111 | 560 | 56896 | 101.6
SHINGLE SPRINGS 1103 | 2346 | 163707 | 69.7813
SHINGLE SPRINGS 1104 | 1290 | 188836 | 146.3845
SHINGLE SPRINGS 2108 | 4997 | 1122833 | 224.7014
SHINGLE SPRINGS 2109 | 10272 | 2114478 | 205.8487
SHINGLE SPRINGS 2110 | 3230 | 532771 | 164.9446
SILVERADO 2102 | 1453 | 319290 | 219.7454
SILVERADO 2103 | 154 | 39946 | 259.3896
SILVERADO 2104 | 16807 | 5820900 | 346.3378
SILVERADO 2105 | 904 | 275498 | 304.7544
SISQUOC 1101 | 78 | 32897 | 421.7564
SISQUOC 1102 | 582 | 99261 | 170.5515
SISQUOC 1103 | 389 | 76473 | 196.5887
SMARTVILLE 1101 | 562 | 142097 | 252.8416
SMARTVILLE SUB | 562 | 42150 | 75
SNEATH LANE 1101 | 834 | 162202 | 194.4868
SOBRANTE 1101 | 3224 | 338996 | 105.1476
SOBRANTE 1102 | 580 | 69448 | 119.7379
SOBRANTE 1103 | 4826 | 1523879 | 315.7644
SOLEDAD 2101 | 173 | 63588 | 367.5607
SOLEDAD 2102 | 116 | 25559 | 220.3362
SOLEDAD 2104 | 419 | 64470 | 153.8663
SOLEDAD 2105 | 509 | 67063 | 131.7544
SONOMA 1104 | 2345 | 363056 | 154.8213
SONOMA 1105 | 2875 | 212619 | 73.9544
SPAULDING 1101 | 172 | 21776 | 126.6047
SPENCE 1101 | 168 | 39816 | 237
SPENCE 1104 | 168 | 64008 | 381
SPRING GAP 1702 | 5918 | 1581208 | 267.1862
STAFFORD 1102 | 4365 | 741037 | 169.7679
STANISLAUS 1701 | 17468 | 3714186 | 212.628
STANISLAUS 1702 | 20967 | 2931773 | 139.828
STELLING 1109 | 1471 | 188346 | 128.0394
STELLING 1110 | 43 | 2838 | 66
STILLWATER 1101 | 14 | 140 | 10
STILLWATER 1102 | 2830 | 412961 | 145.9226
STONE CORRAL 1108 | 165 | 30195 | 183
SUMMIT 1101 | 152 | 43374 | 285.3553
SUMMIT 1102 | 208 | 45136 | 217
SUNOL 1101 | 103 | 35277 | 342.4951
SWIFT 2110 | 92 | 34912 | 379.4783
SYCAMORE CREEK 1109 | 886 | 115699 | 130.5858
SYCAMORE CREEK 1111 | 581 | 66218 | 113.9725
TAR FLAT 0401 | 347 | 29514 | 85.0548
TAR FLAT 0402 | 1117 | 339258 | 303.7225
TASSAJARA 2103 | 3712 | 1475519 | 397.4997
TASSAJARA 2104 | 3124 | 250216 | 80.0948
TASSAJARA 2107 | 3846 | 1261490 | 328.0005
TASSAJARA 2108 | 21296 | 5079568 | 238.5222
TASSAJARA 2112 | 1656 | 217484 | 131.3309
TASSAJARA 2113 | 542 | 138752 | 256
TEJON 1102 | 22 | 3784 | 172
TEMBLOR 1104 | 106 | 20200 | 190.566
TEMPLETON 2108 | 3079 | 637270 | 206.973
TEMPLETON 2110 | 5341 | 1131340 | 211.8218
TEMPLETON 2111 | 10778 | 950583 | 88.1966
TEMPLETON 2112 | 12 | 1344 | 112
TEMPLETON 2113 | 29196 | 3541006 | 121.2839
TEMPORARY CARBONA 1101 | 262 | 54627 | 208.5
TIDEWATER 2106 | 7351 | 1378358 | 187.5062
TIGER CREEK 0201 | 14 | 38205 | 2728.9286
TIVY VALLEY 1107 | 5686 | 1911550 | 336.1854
TRES PINOS 1111 | 46 | 7084 | 154
TRINIDAD SUB | 1569 | 276144 | 176
TULUCAY 1101 | 12 | 2352 | 196
TYLER / RAWSON SUB | 6222 | 532984 | 85.6612
TYLER 1105 | 2511 | 366320 | 145.8861
TYLER SUB | 10887 | 742875 | 68.2351
UKIAH 1111 | 1169 | 75608 | 64.6775
UKIAH 1113 | 1209 | 50778 | 42
UKIAH 1114 | 4645 | 439061 | 94.5234
UKIAH 1115 | 1478 | 279072 | 188.8173
UPPER LAKE 1101 | 2750 | 296667 | 107.8789
VACA DIXON 1101 | 1408 | 384384 | 273
VACA DIXON 1105 | 12 | 1944 | 162
VACAVILLE 1104 | 5029 | 457234 | 90.9195
VACAVILLE 1108 | 5685 | 908973 | 159.8897
VACAVILLE 1111 | 2171 | 267668 | 123.2925
Valley Springs 1101 | 6360 | 675368 | 106.1899
VALLEY VIEW 1103 | 23 | 782 | 34
VASCO 1102 | 379 | 148068 | 390.6807
VINEYARD 2107 | 3559 | 1338247 | 376.0177
VINEYARD 2108 | 6092 | 837025 | 137.3974
VINEYARD 2110 | 6914 | 2523610 | 365
VOLTA 1101 | 1262 | 214135 | 169.6791
VOLTA 1102 | 6632 | 1283756 | 193.57
WEIMAR 1101 | 2822 | 449558 | 159.3047
WEIMAR 1102 | 2843 | 282555 | 99.3862
WEST POINT 1101 | 3560 | 418380 | 117.5225
WEST POINT 1102 | 7324 | 540671 | 73.8218
WESTLEY 1101 | 75 | 15900 | 212
WESTLEY 1103 | 40 | 28960 | 724
WHEATLAND 1105 | 213 | 27264 | 128
WHITMORE 1101 | 411 | 172241 | 419.0779
WILDWOOD 1101 | 83 | 11494 | 138.4819
WILLITS 1103 | 2057 | 200024 | 97.2406
WILLITS 1104 | 590 | 86025 | 145.8051
WILLOW CREEK 1101 | 1196 | 111278 | 93.0418
WILLOW CREEK 1102 | 1656 | 1377463 | 831.8013
WILLOW CREEK 1103 | 13044 | 4741895 | 363.5307
WILLOW PASS 2108 | 5654 | 508709 | 89.9733
WINDSOR 1103 | 81 | 8198 | 101.2099
WISE 1102 | 2130 | 278562 | 130.7803
WOODACRE 1101 | 2018 | 297188 | 147.2686
WOODACRE 1102 | 2689 | 500433 | 186.1038
WOODSIDE 1101 | 1345 | 322959 | 240.1182
WOODSIDE 1104 | 2568 | 637594 | 248.2843
WYANDOTTE 1102 | 2114 | 148438 | 70.2167
WYANDOTTE 1103 | 2974 | 506608 | 170.3457
WYANDOTTE 1106 | 182 | 15954 | 87.6593
WYANDOTTE 1107 | 7377 | 1232155 | 167.0266
WYANDOTTE 1109 | 3626 | 294799 | 81.3014
WYANDOTTE 1110 | 4673 | 1328479 | 284.2883
ZACA 1101 | 4879 | 519145 | 106.404
ZACA 1102 | 7444 | 381067 | 51.1912

## YTD EPSS Outages_CESO
Circuit | Sum of CESO
ALHAMBRA 1105 | 1023
ALLEGHANY 1101 | 287
ALLEGHANY 1102 | 164
ALTO 1124 | 898
ALTO 1125 | 2752
ANDERSON 1101 | 228
ANNAPOLIS 1101 | 304
ANNAPOLIS SUB | 229
ANTELOPE 1101 | 45
ANTLER 1101 | 867
APPLE HILL 1104 | 6273
APPLE HILL 2102 | 28293
ARCATA 1121 | 326
ARCATA 1122 | 356
ATASCADERO 1101 | 905
ATASCADERO 1102 | 5385
ATASCADERO 1103 | 7111
AUBERRY 1101 | 4564
AUBERRY 1102 | 665
AUBURN 1102 | 992
AVENA 1702 | 368
AVENAL 2101 | 3349
BALCH NO 1 1101 | 27
BANGOR 1101 | 5251
BAY MEADOWS 2102 | 1160
BAYWOOD 1101 | 588
BEAR VALLEY 2101 | 1035
BEAR VALLEY 2105 | 2015
BELL 1107 | 861
BELL 1108 | 2283
BELLEVUE 2101 | 6092
BEN LOMOND 0401 | 3749
BEN LOMOND 1101 | 2238
BIG BASIN 1101 | 230
BIG BASIN 1102 | 2265
BIG BEND 1102 | 676
BIG MEADOWS 2101 | 1101
BOLINAS 1101 | 1384
BONNIE NOOK 1102 | 1511
BORONDA SUB | 1788
BRENTWOOD 2105 | 2125
BRIDGEVILLE 1101 | 3251
BRIDGEVILLE 1102 | 55
BROWNS VALLEY 1101 | 525
BRUNSWICK 1102 | 3161
BRUNSWICK 1103 | 2560
BRUNSWICK 1104 | 3095
BRUNSWICK 1105 | 18248
BRUNSWICK 1106 | 21276
BRUNSWICK 1107 | 4030
BUCKS CREEK 1103 | 509
BUELLTON 1101 | 2006
BUELLTON 1102 | 2033
BURNEY 1101 | 88
BURNS 2101 | 17400
BUTTE 1105 | 405
CABRILLO 1103 | 2246
CABRILLO 1104 | 2773
CAL WATER 1102 | 54
CALAVERAS CEMENT 1101 | 15839
CALISTOGA 1101 | 3472
CALISTOGA 1102 | 3324
CALPELLA 1101 | 2205
CALPELLA 1102 | 87
CAMBRIA 1102 | 332
CAMP EVERS 2103 | 5954
CAMP EVERS 2104 | 6982
CAMP EVERS 2105 | 13412
CAMP EVERS 2106 | 20288
CANTUA 1103 | 295
CARLOTTA 1121 | 1153
CARNERAS 1103 | 14
CASTRO VALLEY 1108 | 1852
CASTRO VALLEY 1110 | 11992
CASTRO VALLEY 1111 | 86
CAYETANO 2109 | 6283
CAYETANO 2111 | 4176
CAYUCOS 1101 | 660
CAYUCOS 1102 | 155
CEDAR CREEK 1101 | 1455
CHALLENGE 1101 | 1261
CHALLENGE 1102 | 198
CHESTER SUB | 1661
CHOLAME 1101 | 572
CHOLAME 2102 | 1683
CLARK ROAD 1101 | 25
CLARK ROAD 1102 | 6205
CLARKSVILLE 2103 | 755
CLARKSVILLE 2104 | 10062
CLARKSVILLE 2106 | 847
CLARKSVILLE 2110 | 4082
CLAY 1101 | 5385
CLAY 1102 | 3
CLAY 1103 | 4017
CLAYTON 2212 | 4436
CLAYTON 2215 | 18721
CLAYTON 2217 | 5333
CLEAR LAKE 1101 | 3928
CLOVERDALE 1101 | 258
CLOVERDALE 1102 | 4864
COALINGA NO 2 1105 | 322
COARSEGOLD 2102 | 4271
COARSEGOLD 2103 | 3874
COARSEGOLD 2104 | 21905
COLUMBIA HILL 1101 | 37
COPPERMINE 1104 | 167
CORNING 1101 | 1306
CORNING 1102 | 1634
CORRAL 1101 | 1660
CORRAL 1102 | 4154
CORRAL 1103 | 139
CORRAL SUB | 5722
CORTINA 1101 | 24
COTATI 1102 | 129
COTATI 1103 | 1221
COTATI 1105 | 4038
COTTONWOOD 1101 | 489
COTTONWOOD 1102 | 1259
COTTONWOOD 1103 | 971
COVELO 1101 | 3186
CRESCENT MILLS 2101 | 7018
CRESCENT MILLS SUB | 1529
CURTIS 1701 | 7178
CURTIS 1702 | 15774
CURTIS 1703 | 31623
CURTIS 1704 | 14852
CURTIS 1705 | 4506
CUYAMA 1103 | 291
CUYAMA 2101 | 124
CUYAMA 2102 | 21
DEL MONTE 2104 | 15908
DESCHUTES 1101 | 3819
DESCHUTES 1104 | 838
DEVILS DEN 1101 | 201
DIAMOND SPRINGS 1103 | 3053
DIAMOND SPRINGS 1104 | 1121
DIAMOND SPRINGS 1105 | 3329
DIAMOND SPRINGS 1106 | 1832
DIAMOND SPRINGS 1107 | 2793
DOBBINS 1101 | 2343
DOLAN ROAD 1101 | 2321
DOS PALOS SUB | 2574
DRUM 1101 | 810
DUNBAR 1101 | 6320
DUNBAR 1102 | 3546
DUNBAR 1103 | 10734
DUNLAP 1102 | 2661
DUNLAP 1103 | 3850
EAST MARYSVILLE 1108 | 1003
EAST QUINCY 1101 | 1001
EDENVALE 1102 | 1017
EDENVALE 2105 | 12323
EEL RIVER 1102 | 221
EL DORADO PH 2101 | 18978
ELECTRA 1101 | 2545
ELECTRA 1102 | 843
ELECTRA SUB | 1102
ELK CREEK 1101 | 4336
EMERALD LAKE SUB | 624
FAIRVIEW 2207 | 2753
FIREBAUGH SUB | 3659
FITCH MOUNTAIN 1113 | 4310
FOOTHILL 1101 | 404
FORESTHILL 1101 | 11655
FORT BRAGG A 1102 | 1351
FORT ROSS 1121 | 1063
FORT SEWARD 1121 | 563
FORT SEWARD 1122 | 101
FREMONT 1104 | 52
FRENCH GULCH 1102 | 34
FROGTOWN 1701 | 30311
FROGTOWN 1702 | 8210
FRUITLAND 1141 | 21
FRUITLAND 1142 | 1226
FULTON 1107 | 2817
GABILAN 1101 | 1133
GANSNER 1101 | 3682
GARBERVILLE 1101 | 3495
GARBERVILLE 1102 | 5740
GARBERVILLE SUB | 1820
GARCIA SUB | 9
GATES 1106 | 112
GERBER SUB | 1486
GEYSERVILLE 1101 | 3546
GEYSERVILLE 1102 | 739
GIRVAN 1101 | 4573
GIRVAN 1102 | 1154
GONZALES 1104 | 94
GRASS VALLEY 1101 | 3579
GRASS VALLEY 1103 | 2581
GRAYS FLAT SUB | 1829
GREEN VALLEY 2101 | 2240
GUALALA 1112 | 9445
GUALALA SUB | 3794
GUSTINE 1102 | 687
HALF MOON BAY 1101 | 2941
HALF MOON BAY 1102 | 3270
HALSEY 1101 | 5261
HALSEY 1102 | 4265
HAMILTON BRANCH 1101 | 206
HARRIS 1109 | 16
HARTLEY 1101 | 4227
HARTLEY 1102 | 1844
HATTON 1101 | 15197
HATTON 1102 | 2146
HERDLYN 1102 | 1587
HICKS 2101 | 6619
HICKS 2103 | 417
HIGGINS 1103 | 2927
HIGGINS 1104 | 11237
HIGGINS 1107 | 1963
HIGGINS 1109 | 1533
HIGGINS 1110 | 4589
HIGHLANDS 1102 | 5691
HIGHLANDS 1103 | 2261
HIGHLANDS 1104 | 1150
HOLLISTER 2102 | 285
HOLLISTER 2104 | 180
HOLLISTER 2105 | 253
HOLLISTER 2106 | 55
HONCUT 1102 | 93
HOOPA 1101 | 12218
HOPLAND 1101 | 424
HORSESHOE 1101 | 444
HORSESHOE 1104 | 388
HUMBOLDT BAY 1102 | 220
IGNACIO 1104 | 293
INDIAN FLAT 1104 | 1260
IONE 1101 | 1332
JAMESON 1105 | 1196
JESSUP 1101 | 6946
JESSUP 1102 | 1517
JOLON 1102 | 2830
JOLON 1103 | 143
KANAKA 1101 | 58
KERCKHOFF 1101 | 30
KERN OIL 1106 | 258
KESWICK 1101 | 594
KETTLEMAN HILLS 2104 | 1
KING CITY 1102 | 62
KING CITY 1103 | 794
KING CITY 1106 | 124
KIRKER 2104 | 6527
KIRKER 2105 | 2201
KONOCTI 1102 | 1048
KONOCTI 1108 | 2825
LAKEVILLE 1102 | 399
LAKEWOOD 1103 | 79
LAKEWOOD 2107 | 3067
LAKEWOOD 2109 | 142
LAKEWOOD 2224 | 323
LAKEWOOD 2227 | 1281
LAMONT 1104 | 315
LAS POSITAS 2103 | 3
LAS POSITAS 2108 | 5621
LAURELES 1111 | 4807
LAURELES 1112 | 3195
LAURELES SUB | 3526
LAYTONVILLE 1101 | 648
LAYTONVILLE 1102 | 384
LINCOLN 1101 | 1376
LINCOLN 1104 | 1099
LLAGAS 2101 | 1886
LOGAN CREEK 2102 | 193
LONE TREE 2105 | 2635
LOS COCHES 1101 | 18
LOS GATOS 1101 | 666
LOS GATOS 1106 | 7929
LOS GATOS 1107 | 7801
LOS GATOS 1108 | 789
LOS MOLINOS 1101 | 234
LOS OSITOS 2101 | 920
LOS OSITOS 2102 | 95
LOS OSITOS 2103 | 1006
LOYOLA 1102 | 40
LUCERNE 1103 | 1674
LUCERNE 1106 | 1171
MADISON 2101 | 12084
MAGUNDEN 1108 | 303
MAPLE CREEK 1101 | 218
MARICOPA 1102 | 765
MARIPOSA 2101 | 10358
MARIPOSA 2102 | 20710
MARTELL 1101 | 1822
MAXWELL 1102 | 160
MAXWELL 1105 | 224
MC ARTHUR 1101 | 3245
MC ARTHUR SUB | 1736
MEADOW LANE 2106 | 9077
MENDOCINO 1101 | 748
MENLO 1102 | 349
MENLO 1103 | 449
MERCED FALLS 1102 | 1972
MESA 1101 | 1512
MIDDLETOWN 1101 | 6278
MIDDLETOWN 1102 | 441
MIDDLETOWN SUB | 4692
MILPITAS 1105 | 4122
MILPITAS 1109 | 227
MIRABEL 1101 | 1642
MIRABEL 1102 | 1481
MIWUK 1701 | 4779
MIWUK 1702 | 19216
MOLINO 1101 | 751
MOLINO 1102 | 13746
MOLINO 1104 | 233
MONTE RIO 1111 | 1508
MONTE RIO 1112 | 747
MONTE RIO 1113 | 14406
MONTICELLO 1101 | 4589
MORAGA 1101 | 2616
MORAGA 1103 | 2366
MORGAN HILL 2104 | 1160
MORGAN HILL 2105 | 12983
MORGAN HILL 2109 | 4190
MORGAN HILL 2111 | 4172
MORRO BAY 1102 | 2440
MOUNTAIN QUARRIES 2101 | 7915
NAPA 1112 | 2755
NARROWS 2101 | 1503
NARROWS 2102 | 8040
NARROWS 2105 | 13192
NEWMAN 1105 | 180
NORTH BRANCH 1101 | 45
NORTH DUBLIN 2101 | 5550
NORTH DUBLIN 2103 | 10430
NORTH TOWER 2101 | 7443
NOTRE DAME 1103 | 226
NOTRE DAME 1104 | 162
OAKHURST 1101 | 6250
OAKHURST 1103 | 2755
OAKLAND K 1104 | 3268
OAKLAND X 1104 | 609
OAKLAND X 1106 | 1330
OCEANO 1104 | 8956
OILFIELDS 1102 | 46
OILFIELDS 1103 | 26021
OLEMA 1101 | 132
OLETA 1101 | 3715
OLETA 1102 | 2940
OREGON TRAIL 1102 | 2247
OREGON TRAIL 1103 | 1714
OREGON TRAIL 1104 | 1664
ORICK SUB | 348
ORO FINO 1101 | 1044
ORO FINO 1102 | 2912
ORO LOMA 1106 | 837
ORO LOMA SUB | 632
OROSI 1102 | 1494
OROVILLE 1104 | 3312
OTTER 1101 | 378
OTTER SUB | 1114
PANOCHE 1103 | 152
PANORAMA 1101 | 3403
PANORAMA 1102 | 10
PARADISE 1103 | 1719
PARADISE 1105 | 1254
PASO ROBLES 1103 | 9708
PASO ROBLES 1104 | 1308
PAUL SWEET 2102 | 1659
PAUL SWEET 2106 | 1348
PEABODY 2113 | 10539
PENNGROVE 1101 | 335
PENRYN 1103 | 3964
PENRYN 1105 | 3632
PENRYN 1106 | 924
PENRYN 1107 | 11730
PEORIA 1701 | 5420
PEORIA 1704 | 14543
PEORIA 1705 | 9695
PERRY 1101 | 11702
PETALUMA A SUB | 2519
PETALUMA C 1108 | 4776
PETALUMA C 1109 | 3954
PHILO 1102 | 4313
PHILO SUB | 2222
PIERCY 2110 | 1430
PIKE CITY 1101 | 87
PINE GROVE 1101 | 4906
PINE GROVE 1102 | 13746
PIT NO 3 2101 | 257
PIT NO 5 1101 | 822
PLACER 1103 | 4790
PLACER 1104 | 992
PLACERVILLE 1111 | 381
PLACERVILLE 1112 | 481
PLACERVILLE 2106 | 34896
POINT ARENA 1101 | 1136
POINT ARENA SUB | 912
POINT MORETTI 1101 | 64
POINT MORETTI SUB | 781
POSO MOUNTAIN 2101 | 1777
POSO MOUNTAIN 2103 | 120
POTTER VALLEY P H 1105 | 987
PRUNEDALE 1110 | 1024
PUEBLO 1104 | 559
PUEBLO 1105 | 282
PUEBLO 2103 | 6834
PUEBLO 2104 | 3060
PURISIMA 1101 | 2659
PUTAH CREEK 1102 | 388
RACETRACK 1703 | 12185
RALSTON 1102 | 232
RAWSON SUB | 2524
RED BLUFF 1101 | 2201
RED BLUFF 1103 | 2941
RED BLUFF 1104 | 724
RED BLUFF 1105 | 2002
REDBUD 1101 | 1079
REDBUD 1102 | 7694
REEDLEY 1104 | 104
REEDLEY 1112 | 619
RESEARCH 2101 | 406
RESERVATION ROAD 1101 | 8085
RESERVATION ROAD 1102 | 2765
RESERVATION ROAD SUB | 4547
RIO DELL 1101 | 2860
RIO DELL 1102 | 48
RISING RIVER 1101 | 527
ROB ROY 2104 | 27422
ROB ROY 2105 | 1054
ROSSMOOR 1101 | 352
ROSSMOOR 1102 | 3095
ROSSMOOR 1106 | 6116
ROSSMOOR 1108 | 12830
ROSSMOOR 1109 | 870
SALT SPRINGS 2101 | 4730
SALT SPRINGS 2102 | 2014
SAN ARDO 1102 | 902
SAN BENITO 2101 | 36
SAN BENITO 2104 | 10228
SAN BERNARD 1101 | 17
SAN JOAQUIN #2 1103 | 940
SAN JOAQUIN #3 1101 | 1254
SAN JOAQUIN #3 1102 | 262
SAN JOAQUIN #3 1103 | 1377
SAN JUSTO 1101 | 1508
SAN LUIS OBISPO 1101 | 9284
SAN LUIS OBISPO 1103 | 2581
SAN LUIS OBISPO 1104 | 5659
SAN LUIS OBISPO 1107 | 6822
SAN MIGUEL 1104 | 241
SAN MIGUEL 1105 | 17
SAN MIGUEL 1106 | 90
SAN RAFAEL 1101 | 1300
SAN RAFAEL 1104 | 2818
SAN RAFAEL 1107 | 5320
SAN RAFAEL 1108 | 781
SAN RAMON 2107 | 829
SAN RAMON 2108 | 94
SAND CREEK 1103 | 3560
SANTA MARIA 1108 | 445
SANTA NELLA 1101 | 333
SANTA RITA SUB | 972
SANTA ROSA A 1104 | 3282
SANTA YNEZ 1101 | 1852
SANTA YNEZ 1102 | 3749
SANTA YNEZ 1104 | 2156
SARATOGA 1103 | 1322
SARATOGA 1106 | 3303
SARATOGA 1107 | 676
SEACLIFF 0401 | 213
SHADY GLEN 1101 | 1169
SHADY GLEN 1102 | 1158
SHEPHERD 2111 | 560
SHINGLE SPRINGS 1103 | 2346
SHINGLE SPRINGS 1104 | 1290
SHINGLE SPRINGS 2108 | 4997
SHINGLE SPRINGS 2109 | 10272
SHINGLE SPRINGS 2110 | 3230
SILVERADO 2102 | 1453
SILVERADO 2103 | 154
SILVERADO 2104 | 16807
SILVERADO 2105 | 904
SISQUOC 1101 | 78
SISQUOC 1102 | 582
SISQUOC 1103 | 389
SMARTVILLE 1101 | 562
SMARTVILLE SUB | 562
SNEATH LANE 1101 | 834
SOBRANTE 1101 | 3224
SOBRANTE 1102 | 580
SOBRANTE 1103 | 4826
SOLEDAD 2101 | 173
SOLEDAD 2102 | 116
SOLEDAD 2104 | 419
SOLEDAD 2105 | 509
SONOMA 1104 | 2345
SONOMA 1105 | 2875
SPAULDING 1101 | 172
SPENCE 1101 | 168
SPENCE 1104 | 168
SPRING GAP 1702 | 5918
STAFFORD 1102 | 4365
STANISLAUS 1701 | 17468
STANISLAUS 1702 | 20967
STELLING 1109 | 1471
STELLING 1110 | 43
STILLWATER 1101 | 14
STILLWATER 1102 | 2830
STONE CORRAL 1108 | 165
SUMMIT 1101 | 152
SUMMIT 1102 | 208
SUNOL 1101 | 103
SWIFT 2110 | 92
SYCAMORE CREEK 1109 | 886
SYCAMORE CREEK 1111 | 581
TAR FLAT 0401 | 347
TAR FLAT 0402 | 1117
TASSAJARA 2103 | 3712
TASSAJARA 2104 | 3124
TASSAJARA 2107 | 3846
TASSAJARA 2108 | 21296
TASSAJARA 2112 | 1656
TASSAJARA 2113 | 542
TEJON 1102 | 22
TEMBLOR 1104 | 106
TEMPLETON 2108 | 3079
TEMPLETON 2110 | 5341
TEMPLETON 2111 | 10778
TEMPLETON 2112 | 12
TEMPLETON 2113 | 29196
TEMPORARY CARBONA 1101 | 262
TIDEWATER 2106 | 7351
TIGER CREEK 0201 | 14
TIVY VALLEY 1107 | 5686
TRES PINOS 1111 | 46
TRINIDAD SUB | 1569
TULUCAY 1101 | 12
TYLER / RAWSON SUB | 6222
TYLER 1105 | 2511
TYLER SUB | 10887
UKIAH 1111 | 1169
UKIAH 1113 | 1209
UKIAH 1114 | 4645
UKIAH 1115 | 1478
UPPER LAKE 1101 | 2750
VACA DIXON 1101 | 1408
VACA DIXON 1105 | 12
VACAVILLE 1104 | 5029
VACAVILLE 1108 | 5685
VACAVILLE 1111 | 2171
Valley Springs 1101 | 6360
VALLEY VIEW 1103 | 23
VASCO 1102 | 379
VINEYARD 2107 | 3559
VINEYARD 2108 | 6092
VINEYARD 2110 | 6914
VOLTA 1101 | 1262
VOLTA 1102 | 6632
WEIMAR 1101 | 2822
WEIMAR 1102 | 2843
WEST POINT 1101 | 3560
WEST POINT 1102 | 7324
WESTLEY 1101 | 75
WESTLEY 1103 | 40
WHEATLAND 1105 | 213
WHITMORE 1101 | 411
WILDWOOD 1101 | 83
WILLITS 1103 | 2057
WILLITS 1104 | 590
WILLOW CREEK 1101 | 1196
WILLOW CREEK 1102 | 1656
WILLOW CREEK 1103 | 13044
WILLOW PASS 2108 | 5654
WINDSOR 1103 | 81
WISE 1102 | 2130
WOODACRE 1101 | 2018
WOODACRE 1102 | 2689
WOODSIDE 1101 | 1345
WOODSIDE 1104 | 2568
WYANDOTTE 1102 | 2114
WYANDOTTE 1103 | 2974
WYANDOTTE 1106 | 182
WYANDOTTE 1107 | 7377
WYANDOTTE 1109 | 3626
WYANDOTTE 1110 | 4673
ZACA 1101 | 4879
ZACA 1102 | 7444
Grand Total | 1972285

## YTD EPSS Outages_CPZ
CPZ | Count of Outages
ALHAMBRA 110582622 | 3
ALLEGHANY 1101806 | 2
ALLEGHANY 1101978 | 1
ALLEGHANY 1102CB | 1
ALTO 1124432 | 1
ALTO 1124870444 | 1
ALTO 11251158 | 1
ALTO 1125296476 | 1
ANDERSON 11011390 | 1
ANNAPOLIS 1101528344 | 2
ANTELOPE 11013609 | 1
ANTLER 11011378 | 2
ANTLER 1101718316 | 2
APPLE HILL 110412832 | 2
APPLE HILL 110412842 | 2
APPLE HILL 110413512 | 4
APPLE HILL 21021532 | 5
APPLE HILL 2102186912 | 5
APPLE HILL 2102501650 | 1
APPLE HILL 210251792 | 6
APPLE HILL 2102836878 | 1
ARCATA 1121716954 | 2
ARCATA 11225384 | 1
ATASCADERO 1101A50 | 2
ATASCADERO 1102A28 | 2
ATASCADERO 1102A88 | 1
ATASCADERO 1103492068 | 2
ATASCADERO 1103A06 | 3
ATASCADERO 1103A16 | 2
ATASCADERO 1103A46 | 1
ATASCADERO 1103A80 | 1
AUBERRY 110137536 | 3
AUBERRY 1101R2845 | 1
AUBERRY 1101R314 | 2
AUBERRY 1101R324 | 1
AUBERRY 110237466 | 1
AUBERRY 1102R2850 | 1
AUBURN 1102251946 | 2
AVENA 17025494 | 1
AVENAL 21019070 | 6
AVENAL 21019810 | 1
BALCH NO 1 1101105414 | 1
BANGOR 11011806 | 1
BANGOR 11011958 | 2
BANGOR 110131502 | 2
BANGOR 1101614048 | 1
BANGOR 11017446 | 1
BANGOR 110182350 | 1
BANGOR 1101870548 | 1
BANGOR 1101CB | 1
BAY MEADOWS 210257886 | 1
BAYWOOD 1101CB | 2
BAYWOOD 1101V102 | 1
BEAR VALLEY 210110000 | 4
BEAR VALLEY 210513430 | 1
BEAR VALLEY 210521160 | 2
BEAR VALLEY 210576694 | 2
BEAR VALLEY 2105916436 | 1
BEAR VALLEY 21059480 | 1
BELL 11072400 | 1
BELL 110750172 | 1
BELL 1108127062 | 1
BELL 11082202 | 2
BELL 11082226 | 1
BELL 1108339792 | 1
BELLEVUE 2101335190 | 1
BELLEVUE 2101648 | 2
BELLEVUE 2101CB | 1
BEN LOMOND 040116010 | 2
BEN LOMOND 04015144 | 3
BEN LOMOND 0401944178 | 3
BEN LOMOND 1101BL 1101 | 3
BIG BASIN 1101136050 | 1
BIG BASIN 110195690 | 1
BIG BASIN 110210254 | 1
BIG BASIN 110212124 | 3
BIG BASIN 110212992 | 1
BIG BEND 1102CB | 2
BOLINAS 11011064 | 2
BOLINAS 1101528 | 1
BONNIE NOOK 1102542186 | 2
BONNIE NOOK 1102CB | 2
BRENTWOOD 210519062 | 1
BRENTWOOD 2105502672 | 2
BRENTWOOD 210596324 | 1
BRENTWOOD 210598606 | 1
BRENTWOOD 2105B534R | 1
BRIDGEVILLE 110169866 | 2
BRIDGEVILLE 1101CB | 2
BRIDGEVILLE 110255612 | 1
BROWNS VALLEY 110193870 | 1
BRUNSWICK 11021010 | 3
BRUNSWICK 1102940 | 1
BRUNSWICK 11032784 | 2
BRUNSWICK 11042112 | 1
BRUNSWICK 1104CB | 1
BRUNSWICK 11051030 | 1
BRUNSWICK 11052100 | 4
BRUNSWICK 11052130 | 3
BRUNSWICK 11052140 | 6
BRUNSWICK 11052204 | 1
BRUNSWICK 11052210 | 1
BRUNSWICK 110532536 | 1
BRUNSWICK 11062104 | 4
BRUNSWICK 11062392 | 4
BRUNSWICK 11062796 | 2
BRUNSWICK 110651484 | 4
BRUNSWICK 110651486 | 2
BRUNSWICK 1107357568 | 1
BRUNSWICK 1107CB | 1
BUCKS CREEK 1103338520 | 2
BUELLTON 1101Y06 | 2
BUELLTON 1101Y26 | 1
BUELLTON 1101Y36 | 4
BUELLTON 1102CB | 1
BURNEY 11011322 | 1
BURNEY 1101519432 | 1
BURNS 210136516 | 2
BURNS 210139126 | 2
BURNS 2101CB | 2
BUTTE 1105612016 | 2
CABRILLO 1103CB | 2
CABRILLO 1103Y46 | 1
CABRILLO 1104597930 | 1
CABRILLO 1104838078 | 1
CABRILLO 1104Y24 | 2
CAL WATER 1102920714 | 1
CALAVERAS CEMENT 110111236 | 3
CALAVERAS CEMENT 1101191544 | 1
CALAVERAS CEMENT 11012646 | 1
CALAVERAS CEMENT 1101502 | 3
CALAVERAS CEMENT 110180930 | 2
CALAVERAS CEMENT 1101CB | 2
CALISTOGA 1101122350 | 1
CALISTOGA 1101242919 | 5
CALISTOGA 1101257964 | 1
CALISTOGA 110143924 | 2
CALISTOGA 11015934 | 3
CALISTOGA 1101727772 | 1
CALISTOGA 1101890 | 3
CALISTOGA 1102131531 | 1
CALISTOGA 1102141073 | 1
CALISTOGA 1102279135 | 1
CALISTOGA 1102634 | 1
CALISTOGA 110266730 | 1
CALISTOGA 1102706 | 2
CALISTOGA 1102769230 | 1
CALPELLA 1101372366 | 1
CALPELLA 1101CB | 1
CALPELLA 1102421412 | 1
CAMP EVERS 210311046 | 3
CAMP EVERS 210311056 | 2
CAMP EVERS 210312990 | 2
CAMP EVERS 21035402 | 1
CAMP EVERS 21035404 | 1
CAMP EVERS 210411048 | 2
CAMP EVERS 2104CB | 1
CAMP EVERS 210510214 | 1
CAMP EVERS 210510728 | 1
CAMP EVERS 210533542 | 1
CAMP EVERS 2105370732 | 1
CAMP EVERS 21055232 | 1
CAMP EVERS 2105922576 | 1
CAMP EVERS 210595050 | 2
CAMP EVERS 2105CB | 1
CAMP EVERS 210611006 | 2
CAMP EVERS 210612760 | 3
CAMP EVERS 2106257600 | 1
CAMP EVERS 210660124 | 1
CAMP EVERS 2106737512 | 1
CAMP EVERS 210694770 | 3
CANTUA 11039900 | 1
CARLOTTA 112144150 | 1
CARLOTTA 11214914 | 1
CARNERAS 1103430670 | 1
CASTRO VALLEY 1108343456 | 1
CASTRO VALLEY 1110560528 | 5
CASTRO VALLEY 1110610800 | 2
CASTRO VALLEY 1110MR243 | 1
CASTRO VALLEY 1111227862 | 1
CAYETANO 2109884904 | 2
CAYETANO 2109MR186 | 3
CAYETANO 2109MR572 | 1
CAYETANO 2111CB | 2
CAYETANO 2111MR444 | 1
CAYUCOS 1101W58 | 2
CAYUCOS 1102317156 | 1
CAYUCOS 1102613456 | 1
CEDAR CREEK 11011664 | 1
CEDAR CREEK 1101451856 | 1
CEDAR CREEK 1101CB | 2
CHALLENGE 11015460 | 2
CHALLENGE 1101CB | 1
CHALLENGE 11021064 | 1
CHOLAME 1101X14 | 1
CHOLAME 2102796386 | 2
CHOLAME 2102867686 | 2
CHOLAME 2102X06 | 3
CHOLAME 2102X08 | 2
CHOLAME 2102X16 | 2
CHOLAME 2102X22 | 1
CLARK ROAD 1101CB | 1
CLARK ROAD 11022044 | 1
CLARK ROAD 1102212118 | 3
CLARK ROAD 1102272950 | 1
CLARK ROAD 1102514690 | 1
CLARK ROAD 110281296 | 3
CLARK ROAD 110290548 | 1
CLARK ROAD 110292622 | 1
CLARKSVILLE 210319572 | 1
CLARKSVILLE 2103593454 | 1
CLARKSVILLE 210413352 | 7
CLARKSVILLE 210419772 | 1
CLARKSVILLE 2104CB | 1
CLARKSVILLE 210619642 | 1
CLARKSVILLE 211019692 | 1
CLAY 110113442 | 4
CLAY 110113450 | 1
CLAY 1101CB | 1
CLAY 1102CB | 1
CLAY 11037124 | 2
CLAY 11037142 | 2
CLAY 1103CB | 1
CLAYTON 2212614950 | 1
CLAYTON 2212681608 | 1
CLAYTON 221296224 | 2
CLAYTON 2212CB | 1
CLAYTON 2215184604 | 1
CLAYTON 2215880066 | 1
CLAYTON 2215CB | 3
CLAYTON 2215W573R | 1
CLAYTON 2217CB | 1
CLEAR LAKE 11011302 | 2
CLEAR LAKE 1101740076 | 1
CLEAR LAKE 110192870 | 4
CLOVERDALE 110184088 | 1
CLOVERDALE 1101964556 | 1
CLOVERDALE 1102156 | 2
CLOVERDALE 1102262 | 2
CLOVERDALE 1102654084 | 1
CLOVERDALE 1102672 | 1
CLOVERDALE 1102CB | 1
COALINGA NO 2 110541954 | 2
COARSEGOLD 210210330 | 1
COARSEGOLD 2102383092 | 2
COARSEGOLD 21035020 | 1
COARSEGOLD 21036110 | 3
COARSEGOLD 2103CB | 1
COARSEGOLD 210410400 | 4
COARSEGOLD 2104570682 | 3
COARSEGOLD 2104828842 | 2
COARSEGOLD 2104905960 | 3
COLUMBIA HILL 1101CB | 1
COPPERMINE 1104556430 | 1
COPPERMINE 1104613086 | 1
CORNING 110182846 | 3
CORNING 1101972454 | 1
CORNING 11021900 | 4
CORNING 110253184 | 1
CORRAL 110112606 | 2
CORRAL 1101173174 | 1
CORRAL 110136652 | 1
CORRAL 110175204 | 3
CORRAL 1102CB | 1
CORRAL 1103CB | 1
CORTINA 110130262 | 1
COTATI 1102282 | 1
COTATI 110361736 | 1
COTATI 110379140 | 1
COTATI 1105328 | 3
COTATI 110536536 | 2
COTATI 1105616 | 1
COTTONWOOD 1101384360 | 1
COTTONWOOD 110168190 | 1
COTTONWOOD 11021578 | 2
COTTONWOOD 11029026 | 1
COTTONWOOD 11031616 | 3
COTTONWOOD 1103389928 | 1
COTTONWOOD 1103957942 | 1
COVELO 110137328 | 1
COVELO 1101562360 | 4
CRESCENT MILLS 21012056 | 2
CRESCENT MILLS 21012230 | 3
CRESCENT MILLS 21012232 | 2
CRESCENT MILLS 21012562 | 1
CRESCENT MILLS 2101CB | 2
CURTIS 17019230 | 2
CURTIS 1701CB | 1
CURTIS 170210940 | 4
CURTIS 1702278740 | 2
CURTIS 1702295684 | 1
CURTIS 170247488 | 1
CURTIS 17026008 | 10
CURTIS 17028000 | 2
CURTIS 1703258550 | 1
CURTIS 17036064 | 3
CURTIS 170384944 | 6
CURTIS 170390320 | 1
CURTIS 17039240 | 1
CURTIS 17039330 | 1
CURTIS 1703CB | 1
CURTIS 170411290 | 3
CURTIS 17046060 | 4
CURTIS 17048140 | 5
CURTIS 170539256 | 2
CURTIS 170565908 | 3
CURTIS 17058110 | 1
CURTIS 17058170 | 2
CUYAMA 1103282557 | 1
CUYAMA 1103622728 | 1
CUYAMA 1103684566 | 1
CUYAMA 21013542 | 1
CUYAMA 21021000 | 1
DEL MONTE 21042624 | 2
DEL MONTE 21042762 | 4
DEL MONTE 21049096 | 1
DEL MONTE 21049500 | 1
DESCHUTES 11011380 | 4
DESCHUTES 1104421598 | 1
DESCHUTES 1104622260 | 3
DEVILS DEN 1101CB | 3
DIAMOND SPRINGS 11039432 | 1
DIAMOND SPRINGS 1103CB | 1
DIAMOND SPRINGS 1104705100 | 1
DIAMOND SPRINGS 1104CB | 1
DIAMOND SPRINGS 11057722 | 3
DIAMOND SPRINGS 11062100 | 1
DIAMOND SPRINGS 110656026 | 1
DIAMOND SPRINGS 110676088 | 1
DIAMOND SPRINGS 11071402 | 1
DIAMOND SPRINGS 1107CB | 1
DOBBINS 11011264 | 1
DOBBINS 11015202 | 1
DOBBINS 110169722 | 1
DOBBINS 1101CB | 1
DOLAN ROAD 110122158 | 1
DOLAN ROAD 110169466 | 1
DOLAN ROAD 1101CB | 2
DRUM 1101CB | 4
DUNBAR 1101440 | 1
DUNBAR 1101534 | 1
DUNBAR 1101872066 | 1
DUNBAR 1101904852 | 2
DUNBAR 1102246 | 1
DUNBAR 1102386158 | 2
DUNBAR 1102448 | 3
DUNBAR 1102694641 | 1
DUNBAR 1103234 | 3
DUNBAR 1103CB | 1
DUNLAP 11027050 | 29
DUNLAP 11037080 | 5
DUNLAP 11037170 | 5
DUNLAP 11037220 | 1
DUNLAP 1103CB | 1
EAST MARYSVILLE 1108900690 | 1
EAST QUINCY 11012452 | 1
EDENVALE 1102XR064 | 1
EDENVALE 2105469810 | 1
EDENVALE 2105CB | 2
EEL RIVER 11021902 | 2
EEL RIVER 110249130 | 1
EL DORADO PH 210119612 | 1
EL DORADO PH 210119752 | 1
EL DORADO PH 210152456 | 2
EL DORADO PH 21016852 | 7
ELECTRA 11011238 | 1
ELECTRA 110161816 | 2
ELECTRA 11017104 | 3
ELECTRA 11026014 | 1
ELK CREEK 11012002 | 5
ELK CREEK 11012004 | 1
ELK CREEK 11012008 | 2
ELK CREEK 110137334 | 1
EMERALD LAKE 0401CB | 1
FAIRVIEW 2207M501R | 2
FAIRVIEW 2207P148 | 1
FITCH MOUNTAIN 1113154 | 1
FITCH MOUNTAIN 111349826 | 2
FITCH MOUNTAIN 1113775992 | 1
FOOTHILL 1101549904 | 1
FOOTHILL 1101CB | 1
FORESTHILL 11011802 | 4
FORESTHILL 110150486 | 2
FORESTHILL 1101CB | 1
FORT BRAGG A 1102265870 | 1
FORT BRAGG A 110231304 | 2
FORT BRAGG A 110233064 | 1
FORT BRAGG A 1102416218 | 1
FORT BRAGG A 1102418 | 1
FORT ROSS 1121134 | 3
FORT ROSS 1121204 | 4
FORT ROSS 1121560 | 1
FORT ROSS 1121612266 | 1
FORT SEWARD 1121CB | 4
FORT SEWARD 1122CB | 1
FREMONT 1104645342 | 2
FRENCH GULCH 11021462 | 1
FRENCH GULCH 11022902 | 1
FROGTOWN 170113412 | 13
FROGTOWN 1701CB | 1
FROGTOWN 170236870 | 1
FROGTOWN 17027134 | 3
FROGTOWN 1702737236 | 2
FROGTOWN 170275252 | 1
FROGTOWN 17028482 | 2
FROGTOWN 1702CB | 1
FRUITLAND 1141200856 | 1
FRUITLAND 1141866852 | 2
FRUITLAND 1142899734 | 2
FULTON 1107126742 | 3
GABILAN 11013034 | 2
GABILAN 1101460414 | 1
GABILAN 1101566352 | 1
GANSNER 1101372132 | 1
GANSNER 110152664 | 2
GANSNER 110199388 | 1
GARBERVILLE 11011750 | 2
GARBERVILLE 110139524 | 1
GARBERVILLE 11016014 | 2
GARBERVILLE 110197300 | 1
GARBERVILLE 1101CB | 2
GARBERVILLE 11021510 | 5
GARBERVILLE 11022124 | 2
GARBERVILLE 11022540 | 1
GARBERVILLE 11028652 | 1
GARBERVILLE 1102CB | 1
GATES 110699914 | 1
GEYSERVILLE 1101166 | 3
GEYSERVILLE 110137454 | 2
GEYSERVILLE 1101406798 | 1
GEYSERVILLE 1101480 | 1
GEYSERVILLE 1102350 | 1
GEYSERVILLE 1102429530 | 1
GEYSERVILLE 1102537096 | 1
GEYSERVILLE 1102776178 | 1
GEYSERVILLE 1102904170 | 1
GIRVAN 11011636 | 2
GIRVAN 1101323094 | 1
GIRVAN 1101409530 | 2
GIRVAN 11019732 | 1
GIRVAN 1102296428 | 1
GIRVAN 110280726 | 1
GONZALES 110422418 | 1
GRASS VALLEY 11012208 | 1
GRASS VALLEY 1101CB | 3
GRASS VALLEY 11032180 | 5
GREEN VALLEY 210111054 | 5
GREEN VALLEY 2101135762 | 2
GREEN VALLEY 210136820 | 3
GREEN VALLEY 2101454176 | 1
GREEN VALLEY 210190860 | 2
GUALALA 111135562 | 2
GUALALA 1111402866 | 1
GUALALA 11121294 | 1
GUALALA 1112CB | 2
GUSTINE 11029100 | 1
GUSTINE 1102999258 | 1
HALF MOON BAY 11012500 | 1
HALF MOON BAY 1101CB | 1
HALF MOON BAY 11022032 | 1
HALSEY 11011704 | 1
HALSEY 1101CB | 2
HALSEY 1102164068 | 1
HALSEY 110239104 | 1
HALSEY 1102676064 | 1
HALSEY 1102CB | 1
HAMILTON BRANCH 11012046 | 1
HARRIS 1109700 | 1
HARTLEY 1101658 | 4
HARTLEY 1101738 | 2
HARTLEY 1101871312 | 1
HARTLEY 1102841676 | 2
HATTON 11012026 | 2
HATTON 110137088 | 2
HATTON 1101399900 | 1
HATTON 110175304 | 1
HATTON 1101CB | 1
HATTON 1102CB | 1
HERDLYN 1102608254 | 1
HERDLYN 1102CB | 1
HICKS 2101CB | 1
HICKS 2101XR250 | 2
HICKS 2103XR248 | 1
HIGGINS 110332120 | 1
HIGGINS 110350072 | 2
HIGGINS 1103995672 | 1
HIGGINS 11041006 | 6
HIGGINS 11071070 | 1
HIGGINS 1107CB | 1
HIGGINS 1109594 | 3
HIGGINS 1110166282 | 1
HIGGINS 11102408 | 1
HIGGINS 1110861610 | 2
HIGGINS 1110CB | 1
HIGHLANDS 1102230414 | 1
HIGHLANDS 1102556 | 1
HIGHLANDS 1102604702 | 1
HIGHLANDS 110275140 | 1
HIGHLANDS 1102914918 | 1
HIGHLANDS 1103520 | 1
HIGHLANDS 1103828 | 1
HIGHLANDS 1103917328 | 1
HIGHLANDS 110439458 | 1
HIGHLANDS 110448262 | 1
HIGHLANDS 110476156 | 1
HOLLISTER 2102113634 | 2
HOLLISTER 2102855412 | 1
HOLLISTER 21044403 | 1
HOLLISTER 210491424 | 1
HOLLISTER 21054048 | 1
HOLLISTER 2105475946 | 1
HOLLISTER 21064004 | 1
HONCUT 1102301886 | 1
HOOPA 11013174 | 4
HOOPA 11013304 | 2
HOOPA 110137202 | 2
HOOPA 1101405280 | 3
HOOPA 110182542 | 2
HOOPA 110193038 | 3
HOPLAND 1101154790 | 1
HORSESHOE 11012714 | 1
HORSESHOE 110151538 | 1
HORSESHOE 110450142 | 1
HUMBOLDT BAY 1102104220 | 1
IGNACIO 1104469764 | 1
INDIAN FLAT 1104CB | 2
IONE 1101510200 | 3
IONE 1101CB | 1
JAMESON 1105466348 | 3
JAMESON 110560052 | 1
JESSUP 11011496 | 4
JESSUP 110141356 | 1
JESSUP 110168362 | 1
JESSUP 11019002 | 1
JESSUP 1102158468 | 1
JOLON 11027002 | 5
JOLON 11027004 | 1
JOLON 11027070 | 3
JOLON 1102CB | 2
JOLON 1103549180 | 7
JOLON 1103CB | 4
KANAKA 1101733624 | 1
KERCKHOFF 1101R308 | 1
KERN OIL 11063301 | 1
KERN OIL 110646960 | 2
KESWICK 11011590 | 11
KESWICK 1101417066 | 2
KETTLEMAN HILLS 2104358094 | 1
KING CITY 1102728782 | 1
KING CITY 11037038 | 1
KING CITY 1106944510 | 1
KIRKER 210475648 | 1
KIRKER 2104CB | 1
KIRKER 2105A536R | 1
KONOCTI 1102354890 | 1
KONOCTI 110275382 | 1
KONOCTI 11081278 | 4
KONOCTI 1108950 | 1
LAKEVILLE 1102280 | 1
LAKEVILLE 1102347280 | 2
LAKEVILLE 1102367100 | 1
LAKEVILLE 110287432 | 2
LAKEWOOD 2107396264 | 1
LAKEWOOD 210769586 | 2
LAKEWOOD 2109432198 | 1
LAKEWOOD 2224568670 | 1
LAKEWOOD 2227W503R | 1
LAMONT 11043855 | 2
LAMONT 11044113 | 4
LAS POSITAS 2108MR190 | 3
LAURELES 1111198478 | 2
LAURELES 11112020 | 3
LAURELES 11112028 | 2
LAURELES 1111432 | 5
LAURELES 11122142 | 2
LAURELES 1112438 | 1
LAURELES 1112779322 | 1
LAURELES 1112CB | 1
LAYTONVILLE 1101518 | 3
LAYTONVILLE 110237586 | 1
LAYTONVILLE 1102572 | 1
LINCOLN 1101210168 | 1
LINCOLN 1101881364 | 3
LINCOLN 110195756 | 4
LINCOLN 11042070 | 2
LINCOLN 1104693294 | 1
LINCOLN 1104818790 | 1
LLAGAS 2101984552 | 1
LLAGAS 2101XR244 | 2
LLAGAS 2101XR586 | 3
LOGAN CREEK 21022428 | 1
LOGAN CREEK 2102767046 | 1
LONE TREE 2105CB | 1
LOS COCHES 1101625902 | 1
LOS GATOS 1101LB40 | 1
LOS GATOS 110660116 | 2
LOS GATOS 1106697500 | 2
LOS GATOS 1106LA64 | 1
LOS GATOS 1106LB44 | 2
LOS GATOS 110760092 | 2
LOS GATOS 110760114 | 2
LOS GATOS 1107781232 | 1
LOS GATOS 1107CB | 2
LOS GATOS 1108590544 | 1
LOS MOLINOS 11011308 | 1
LOS OSITOS 21011132 | 4
LOS OSITOS 21017014 | 2
LOS OSITOS 21027592 | 1
LOS OSITOS 2103258688 | 1
LOS OSITOS 21033010 | 2
LOS OSITOS 21037062 | 2
LOYOLA 1102CB | 1
LUCERNE 1103245134 | 1
LUCERNE 110327932 | 2
LUCERNE 11034200 | 1
LUCERNE 1103630 | 1
LUCERNE 1106664 | 1
MADISON 21011606 | 2
MADISON 2101274974 | 3
MADISON 2101760730 | 3
MADISON 21017702 | 2
MADISON 210189332 | 5
MADISON 21019512 | 1
MADISON 2101CB | 2
MAGUNDEN 1108250674 | 3
MAPLE CREEK 11016906 | 2
MARICOPA 11023558 | 1
MARICOPA 1102CB | 1
MARIPOSA 210110070 | 1
MARIPOSA 210110170 | 3
MARIPOSA 210110990 | 2
MARIPOSA 2101929360 | 2
MARIPOSA 210210880 | 3
MARIPOSA 21021960 | 2
MARIPOSA 210237282 | 1
MARIPOSA 210237288 | 1
MARIPOSA 2102527766 | 1
MARIPOSA 2102851902 | 4
MARIPOSA 21029590 | 1
MARIPOSA 2102CB | 1
MARTELL 110111244 | 3
MARTELL 110191216 | 1
MAXWELL 11023306 | 1
MAXWELL 11053008 | 2
MAXWELL 1105910362 | 1
MC ARTHUR 11011488 | 1
MC ARTHUR 11011544 | 2
MC ARTHUR 11011546 | 2
MC ARTHUR 110138998 | 1
MC ARTHUR 110153120 | 1
MC ARTHUR 1101648698 | 5
MEADOW LANE 2106C558R | 3
MENDOCINO 1101856020 | 1
MENLO 1102154024 | 2
MENLO 1102628458 | 2
MENLO 11029152 | 1
MENLO 1103866118 | 2
MERCED FALLS 11029460 | 1
MERCED FALLS 11029470 | 1
MESA 1101M86 | 2
MIDDLETOWN 1101548 | 2
MIDDLETOWN 1101644756 | 2
MIDDLETOWN 1101829164 | 2
MIDDLETOWN 1102414 | 1
MILPITAS 1105CB | 1
MILPITAS 1109903328 | 1
MILPITAS 1109XR374 | 1
MIRABEL 1101116 | 1
MIRABEL 1101228 | 3
MIRABEL 1101298 | 2
MIRABEL 1101774276 | 1
MIRABEL 1102332 | 1
MIRABEL 1102503294 | 1
MIWUK 170110600 | 1
MIWUK 1701767890 | 1
MIWUK 1701953336 | 3
MIWUK 1702667248 | 6
MIWUK 17028130 | 1
MIWUK 17029270 | 2
MOLINO 1101322 | 2
MOLINO 1102104 | 3
MOLINO 1102178 | 4
MOLINO 1102381468 | 1
MOLINO 1102485246 | 1
MOLINO 1102495692 | 1
MOLINO 1102658 | 2
MOLINO 1104368158 | 1
MONTE RIO 1111292 | 1
MONTE RIO 1111969182 | 2
MONTE RIO 1112212 | 1
MONTE RIO 11125040 | 1
MONTE RIO 111264682 | 1
MONTE RIO 1112938174 | 1
MONTE RIO 1113202 | 1
MONTE RIO 1113320 | 1
MONTE RIO 11133970 | 5
MONTE RIO 1113524 | 1
MONTICELLO 110137384 | 4
MONTICELLO 110152910 | 3
MONTICELLO 1101630 | 1
MONTICELLO 110165454 | 2
MONTICELLO 1101666 | 1
MONTICELLO 1101718 | 1
MORAGA 1101772406 | 1
MORAGA 1101CB | 1
MORAGA 1102161484 | 1
MORAGA 110381146 | 1
MORGAN HILL 2104152774 | 3
MORGAN HILL 210542348 | 1
MORGAN HILL 2105XR070 | 1
MORGAN HILL 2105XR152 | 1
MORGAN HILL 2105XR176 | 1
MORGAN HILL 2105XR268 | 1
MORGAN HILL 2105XR494 | 2
MORGAN HILL 2109XR246 | 1
MORGAN HILL 2111919856 | 1
MORGAN HILL 2111997000 | 2
MORGAN HILL 2111XR292 | 2
MORGAN HILL 2111XR398 | 5
MORRO BAY 1102V84 | 1
MOUNTAIN QUARRIES 21011102 | 1
MOUNTAIN QUARRIES 21011346 | 1
MOUNTAIN QUARRIES 21011350 | 1
MOUNTAIN QUARRIES 21012422 | 2
MOUNTAIN QUARRIES 210151584 | 6
N/A | 31
NAPA 11121302 | 4
NAPA 1112850068 | 1
NARROWS 21011202 | 3
NARROWS 21022728 | 1
NARROWS 210248484 | 2
NARROWS 210276952 | 2
NARROWS 21052228 | 2
NARROWS 21052426 | 5
NARROWS 21052748 | 3
NARROWS 2105CB | 1
NEWMAN 110590430 | 1
NORTH BRANCH 1101CB | 1
NORTH DUBLIN 2101CB | 1
NORTH DUBLIN 2103248212 | 3
NORTH DUBLIN 2103CB | 2
NORTH TOWER 2101CB | 4
NOTRE DAME 1103317782 | 2
NOTRE DAME 11042028 | 2
OAKHURST 1101352740 | 3
OAKHURST 11015490 | 1
OAKHURST 1101618380 | 1
OAKHURST 110311900 | 1
OAKHURST 11035480 | 1
OAKHURST 110377384 | 1
OAKLAND K 1104432850 | 1
OAKLAND K 1104CB | 1
OAKLAND X 1104CR101 | 1
OAKLAND X 1106CR008 | 1
OCEANO 1104Q08 | 1
OCEANO 1104Q10 | 2
OCEANO 1104Q12 | 1
OCEANO 1104V38 | 4
OILFIELDS 110241992 | 1
OILFIELDS 1103451760 | 1
OILFIELDS 11037006 | 5
OILFIELDS 110383158 | 1
OILFIELDS 110387034 | 6
OILFIELDS 1103N04 | 1
OILFIELDS 1103N40 | 1
OILFIELDS 1103N42 | 5
OILFIELDS 1103N44 | 3
OILFIELDS 1103N48 | 2
OLEMA 11011200 | 1
OLETA 1101296804 | 3
OLETA 1101928252 | 1
OLETA 1102186326 | 4
OREGON TRAIL 11021382 | 1
OREGON TRAIL 11021584 | 1
OREGON TRAIL 1102CB | 2
OREGON TRAIL 110335002 | 1
OREGON TRAIL 110346860 | 1
OREGON TRAIL 11041634 | 2
ORO FINO 11012022 | 1
ORO FINO 110265932 | 2
ORO FINO 110276008 | 1
ORO FINO 1102787504 | 1
ORO LOMA 11063650 | 1
ORO LOMA 11069790 | 3
OROSI 1102CB | 4
OROVILLE 11042588 | 2
OTTER 1101440 | 1
PALMER 1101M82 | 1
PALMER 1101M88 | 2
PANOCHE 1103107270 | 1
PANORAMA 1101713592 | 2
PANORAMA 11021632 | 1
PARADISE 11032486 | 2
PARADISE 1105878870 | 1
PASO ROBLES 1103351084 | 2
PASO ROBLES 1103540954 | 1
PASO ROBLES 110355374 | 1
PASO ROBLES 1103N58 | 2
PASO ROBLES 1104R12 | 1
PASO ROBLES 1104R56 | 3
PAUL SWEET 2102777828 | 1
PAUL SWEET 210612828 | 1
PAUL SWEET 2106974130 | 4
PAUL SWEET 2106CB | 1
PEABODY 2113CB | 2
PENNGROVE 1101554 | 1
PENNGROVE 1101950828 | 1
PENRYN 11032198 | 1
PENRYN 110351658 | 2
PENRYN 1103604 | 1
PENRYN 1103660 | 4
PENRYN 1105168616 | 2
PENRYN 11052406 | 2
PENRYN 110550548 | 1
PENRYN 110551676 | 1
PENRYN 110651674 | 1
PENRYN 11072410 | 1
PENRYN 11072706 | 3
PENRYN 11072708 | 1
PENRYN 1107CB | 3
PEORIA 1701169700 | 1
PEORIA 17013186 | 2
PEORIA 170176030 | 1
PEORIA 170190090 | 1
PEORIA 170411232 | 1
PEORIA 170413494 | 1
PEORIA 170459596 | 4
PEORIA 17046090 | 1
PEORIA 17048040 | 1
PEORIA 1704CB | 2
PEORIA 170567898 | 4
PEORIA 170570198 | 1
PEORIA 1705CB | 1
PERRY 1101618168 | 1
PERRY 110179696 | 1
PERRY 110185870 | 1
PERRY 1101925053 | 1
PERRY 1101986322 | 1
PERRY 1101V74 | 1
PERRY 1101V88 | 2
PETALUMA C 1108233646 | 3
PETALUMA C 1108296 | 1
PETALUMA C 1108618 | 5
PETALUMA C 1108636 | 2
PETALUMA C 1109259100 | 2
PETALUMA C 110948000 | 3
PETALUMA C 1109820458 | 1
PETALUMA C 1109857148 | 1
PHILO 1102920 | 5
PHILO 1102928 | 1
PIERCY 2110XR258 | 2
PIKE CITY 1101935730 | 1
PINE GROVE 11013166 | 1
PINE GROVE 11013170 | 5
PINE GROVE 110152088 | 1
PINE GROVE 11023168 | 4
PINE GROVE 11023172 | 3
PINE GROVE 110235576 | 1
PINE GROVE 11026080 | 1
PINE GROVE 110283098 | 1
PIT NO 3 21011480 | 2
PIT NO 5 11011658 | 4
PIT NO 5 11011660 | 1
PIT NO 5 110190846 | 1
PLACER 1103284874 | 1
PLACER 1103CB | 2
PLACERVILLE 11118582 | 1
PLACERVILLE 111219712 | 1
PLACERVILLE 21061104 | 3
PLACERVILLE 210611132 | 2
PLACERVILLE 210619552 | 1
PLACERVILLE 21062224 | 3
PLACERVILLE 210623190 | 1
PLACERVILLE 21067522 | 5
PLACERVILLE 21069712 | 2
PLACERVILLE 2106CB | 2
POINT ARENA 11013702 | 2
POINT ARENA 1101476 | 4
POINT MORETTI 110112122 | 1
POSO MOUNTAIN 21011703 | 3
POSO MOUNTAIN 21012181 | 6
POSO MOUNTAIN 21013990 | 1
POSO MOUNTAIN 2101720132 | 10
POSO MOUNTAIN 2101730862 | 3
POSO MOUNTAIN 2101CB | 1
POSO MOUNTAIN 2103388671 | 2
POSO MOUNTAIN 2103CB | 5
POTTER VALLEY P H 11051904 | 2
POTTER VALLEY P H 1105640888 | 2
POTTER VALLEY P H 110564118 | 1
PRUNEDALE 1110557716 | 2
PRUNEDALE 1110826224 | 1
PUEBLO 1104105708 | 1
PUEBLO 1105684564 | 1
PUEBLO 2102279478 | 1
PUEBLO 2102391312 | 1
PUEBLO 2102618 | 2
PUEBLO 2102656 | 2
PUEBLO 2102698 | 1
PUEBLO 21031970 | 1
PUEBLO 210378504 | 3
PUEBLO 210398394 | 2
PURISIMA 110149394 | 1
PURISIMA 1101Y44 | 3
PUTAH CREEK 1102202158 | 2
PUTAH CREEK 110264044 | 1
RACETRACK 170310870 | 1
RACETRACK 170311270 | 2
RACETRACK 17036014 | 11
RACETRACK 1703CB | 2
RACETRACK 170455798 | 1
RALSTON 1102CB | 2
RED BLUFF 11011556 | 4
RED BLUFF 110176020 | 1
RED BLUFF 11031702 | 1
RED BLUFF 1103CB | 1
RED BLUFF 110451238 | 2
RED BLUFF 110585632 | 2
REDBUD 1101323962 | 1
REDBUD 1101558812 | 2
REDBUD 1101754544 | 1
REDBUD 1102432 | 1
REDBUD 1102523244 | 2
REEDLEY 1104887932 | 4
REEDLEY 1112477952 | 1
REEDLEY 11127240 | 2
RESEARCH 2101D576R | 1
RESERVATION ROAD 1101370948 | 3
RESERVATION ROAD 1101383718 | 1
RESERVATION ROAD 1101586340 | 1
RESERVATION ROAD 1101975548 | 2
RESERVATION ROAD 11023032 | 1
RESERVATION ROAD 1102CB | 1
RIO DELL 11011504 | 2
RIO DELL 11018768 | 5
RIO DELL 110275970 | 1
RISING RIVER 11011530 | 1
ROB ROY 210410960 | 3
ROB ROY 210412596 | 2
ROB ROY 210467520 | 7
ROB ROY 2104974520 | 1
ROB ROY 21055090 | 2
ROSSMOOR 110181770 | 1
ROSSMOOR 1102457174 | 1
ROSSMOOR 1106CB | 2
ROSSMOOR 1106L522R | 1
ROSSMOOR 1107857172 | 1
ROSSMOOR 110845268 | 7
ROSSMOOR 1109724062 | 3
ROSSMOOR 110982962 | 1
ROSSMOOR 1109847274 | 1
SALT SPRINGS 210110416 | 2
SALT SPRINGS 21011232 | 4
SALT SPRINGS 21013116 | 1
SALT SPRINGS 21023118 | 1
SAN ARDO 11027030 | 3
SAN ARDO 11027066 | 2
SAN BENITO 2101295566 | 1
SAN BENITO 2104785888 | 5
SAN BENITO 210488772 | 3
SAN BERNARD 1101641042 | 1
SAN JOAQUIN #2 110310320 | 1
SAN JOAQUIN #2 1103CB | 1
SAN JOAQUIN #3 1101CB | 2
SAN JOAQUIN #3 1102CB | 1
SAN JOAQUIN #3 1103CB | 1
SAN JUSTO 11014002 | 9
SAN LUIS OBISPO 1101483444 | 3
SAN LUIS OBISPO 1101V12 | 2
SAN LUIS OBISPO 1103V82 | 2
SAN LUIS OBISPO 1104236895 | 2
SAN LUIS OBISPO 1104350030 | 1
SAN LUIS OBISPO 1104721823 | 1
SAN LUIS OBISPO 1104982992 | 1
SAN LUIS OBISPO 1104CB | 1
SAN LUIS OBISPO 1104V40 | 1
SAN LUIS OBISPO 1104V46 | 5
SAN LUIS OBISPO 1107V02 | 2
SAN LUIS OBISPO 1107V58 | 1
SAN MIGUEL 1104R88 | 1
SAN MIGUEL 1105CB | 1
SAN MIGUEL 1106605393 | 1
SAN RAFAEL 110139156 | 1
SAN RAFAEL 1104802 | 2
SAN RAFAEL 11071166 | 2
SAN RAFAEL 11071276 | 1
SAN RAFAEL 11081262 | 1
SAN RAMON 2107824562 | 1
SAN RAMON 210853732 | 1
SAND CREEK 11037110 | 4
SAND CREEK 11037140 | 3
SAND CREEK 1103799118 | 1
SAND CREEK 1103818064 | 1
SANTA MARIA 1108M80 | 1
SANTA NELLA 11037200 | 3
SANTA ROSA A 1104210 | 2
SANTA YNEZ 1101277014 | 4
SANTA YNEZ 1101673618 | 1
SANTA YNEZ 1101Y52 | 2
SANTA YNEZ 1102320270 | 4
SANTA YNEZ 1102CB | 1
SANTA YNEZ 1102Y18 | 1
SANTA YNEZ 1104Y04 | 4
SARATOGA 1103LC16 | 2
SARATOGA 1106340986 | 5
SARATOGA 1107413816 | 2
SEACLIFF 040112946 | 1
SHADY GLEN 11012768 | 1
SHADY GLEN 110151696 | 1
SHADY GLEN 11022232 | 3
SHEPHERD 2111537008 | 1
SHINGLE SPRINGS 1103CB | 2
SHINGLE SPRINGS 1104556218 | 2
SHINGLE SPRINGS 210819622 | 1
SHINGLE SPRINGS 2108294550 | 3
SHINGLE SPRINGS 210911092 | 1
SHINGLE SPRINGS 210912392 | 3
SHINGLE SPRINGS 210961892 | 2
SHINGLE SPRINGS 210985766 | 2
SHINGLE SPRINGS 21099372 | 3
SHINGLE SPRINGS 211051790 | 1
SHINGLE SPRINGS 211051800 | 3
SILVERADO 2102285782 | 3
SILVERADO 210234959 | 2
SILVERADO 210258626 | 1
SILVERADO 210298998 | 1
SILVERADO 2103507513 | 1
SILVERADO 2104209359 | 2
SILVERADO 210437632 | 3
SILVERADO 2104632 | 3
SILVERADO 2104633600 | 1
SILVERADO 2104722 | 4
SILVERADO 210478268 | 2
SILVERADO 2104806500 | 2
SILVERADO 2105131568 | 1
SILVERADO 2105247660 | 1
SILVERADO 2105658898 | 2
SILVERADO 2105768606 | 3
SISQUOC 1102M52 | 2
SISQUOC 1102M54 | 4
SISQUOC 1103858898 | 2
SISQUOC 1103M98 | 2
SMARTVILLE 1101CB | 1
SNEATH LANE 11016525 | 1
SOBRANTE 1101CB | 4
SOBRANTE 1102690098 | 1
SOBRANTE 11033342 | 1
SOBRANTE 1103CB | 1
SOBRANTE 1103LA401R | 1
SOLEDAD 2101107872 | 2
SOLEDAD 21017048 | 1
SOLEDAD 2101823854 | 2
SOLEDAD 21027008 | 3
SOLEDAD 2102858388 | 2
SOLEDAD 2104413916 | 1
SOLEDAD 2105526864 | 1
SONOMA 1104414 | 1
SONOMA 1104914376 | 3
SONOMA 1105138 | 3
SONOMA 1105229588 | 1
SPAULDING 1101578852 | 1
SPENCE 1101965598 | 1
SPENCE 1104965598 | 1
SPRING GAP 170210720 | 1
SPRING GAP 17029280 | 2
SPRING GAP 17029690 | 2
STAFFORD 11021202 | 2
STAFFORD 11021258 | 1
STAFFORD 1102524 | 2
STANISLAUS 17011812 | 2
STANISLAUS 17017144 | 12
STANISLAUS 170179826 | 2
STANISLAUS 1701CB | 1
STANISLAUS 17021850 | 4
STANISLAUS 17021888 | 3
STANISLAUS 170275348 | 1
STELLING 110913228 | 2
STELLING 1110396595 | 1
STILLWATER 1101747294 | 1
STILLWATER 1102CB | 2
STONE CORRAL 1108255186 | 3
SUMMIT 1101742 | 1
SUMMIT 1102CB | 1
SUNOL 1101605520 | 1
SWIFT 2110XR332 | 1
SYCAMORE CREEK 1109CB | 1
SYCAMORE CREEK 11112014 | 1
SYCAMORE CREEK 11112602 | 1
TAR FLAT 0401922858 | 1
TAR FLAT 04023144 | 5
TASSAJARA 2103883664 | 1
TASSAJARA 2103CB | 1
TASSAJARA 2104CB | 3
TASSAJARA 210883368 | 1
TASSAJARA 2108CB | 3
TASSAJARA 2112D514R | 1
TASSAJARA 2112D569R | 1
TASSAJARA 2113MR276 | 1
TEJON 11024525 | 1
TEMBLOR 1104CB | 2
TEMPLETON 2108A64 | 1
TEMPLETON 2110307832 | 1
TEMPLETON 2110317796 | 1
TEMPLETON 2110N30 | 1
TEMPLETON 2110R06 | 1
TEMPLETON 2111514592 | 1
TEMPLETON 2111A66 | 5
TEMPLETON 2111R86 | 1
TEMPLETON 2112238418 | 1
TEMPLETON 2113205874 | 1
TEMPLETON 2113587564 | 1
TEMPLETON 2113A10 | 1
TEMPLETON 2113A20 | 1
TEMPLETON 2113A32 | 2
TEMPLETON 2113A70 | 3
TEMPLETON 2113CB | 2
TEMPLETON 2113R82 | 2
TEMPORARY CARBONA 110145186 | 2
TIDEWATER 210657926 | 4
TIDEWATER 210695842 | 1
TIGER CREEK 0201CB | 1
TIVY VALLEY 110737522 | 1
TIVY VALLEY 1107584840 | 1
TIVY VALLEY 11077380 | 2
TIVY VALLEY 1107822606 | 4
TIVY VALLEY 1107869946 | 2
TRES PINOS 1111203126 | 1
TULUCAY 1101504524 | 1
TYLER 11051704 | 3
UKIAH 1111433984 | 1
UKIAH 1113CB | 1
UKIAH 1114408 | 4
UKIAH 1114822 | 3
UKIAH 1114943840 | 1
UKIAH 11151216 | 1
UPPER LAKE 1101412 | 2
UPPER LAKE 110142378 | 2
UPPER LAKE 1101CB | 1
VACA DIXON 110118292 | 1
VACA DIXON 11059792 | 1
VACAVILLE 1104CB | 2
VACAVILLE 1108CB | 2
VACAVILLE 1111CB | 1
Valley Springs 110111158 | 5
Valley Springs 1101207256 | 3
VALLEY VIEW 1106P176 | 1
VASCO 1102546328 | 1
VASCO 1102886522 | 1
VINEYARD 2107CB | 1
VINEYARD 2108MR172 | 2
VINEYARD 2110CB | 1
VOLTA 11011596 | 1
VOLTA 1101507876 | 2
VOLTA 110165764 | 3
VOLTA 1101914816 | 1
VOLTA 11021502 | 3
VOLTA 11021504 | 1
VOLTA 11021646 | 2
WEIMAR 11012058 | 4
WEIMAR 11012740 | 1
WEIMAR 11022038 | 1
WEST POINT 110112256 | 2
WEST POINT 11024788 | 1
WEST POINT 11024790 | 1
WEST POINT 110293116 | 1
WEST POINT 1102CB | 1
WESTLEY 110111730 | 1
WESTLEY 1103237522 | 1
WHEATLAND 1105248490 | 1
WHITMORE 11011594 | 1
WHITMORE 110145262 | 1
WHITMORE 1101589578 | 1
WILDWOOD 11011576 | 1
WILLITS 11032506 | 1
WILLITS 1103409216 | 3
WILLITS 1103564506 | 3
WILLITS 1103696 | 2
WILLITS 110391948 | 1
WILLITS 1104341020 | 1
WILLITS 1104627552 | 1
WILLOW CREEK 11015002 | 3
WILLOW CREEK 11032936 | 2
WILLOW CREEK 110347966 | 3
WILLOW CREEK 11037514 | 3
WILLOW CREEK 1103CB | 4
WILLOW PASS 2108CB | 1
WINDSOR 1103701650 | 1
WISE 11022054 | 1
WISE 11022230 | 1
WISE 11022234 | 1
WISE 1102307494 | 2
WISE 1102697216 | 1
WOODACRE 1101404 | 2
WOODACRE 110196844 | 2
WOODACRE 11021280 | 1
WOODACRE 1102137662 | 1
WOODSIDE 11018522 | 1
WOODSIDE 11018884 | 1
WOODSIDE 11018912 | 2
WOODSIDE 11049116 | 1
WYANDOTTE 110213916 | 1
WYANDOTTE 11031504 | 1
WYANDOTTE 11031508 | 2
WYANDOTTE 110641650 | 1
WYANDOTTE 11071026 | 3
WYANDOTTE 110737472 | 1
WYANDOTTE 110777578 | 2
WYANDOTTE 1107CB | 1
WYANDOTTE 110913052 | 1
WYANDOTTE 1109759354 | 2
WYANDOTTE 1110747922 | 3
ZACA 1101CB | 4
ZACA 1102CB | 1
ZACA 1102Y02 | 5
ZACA 1102Y48 | 4
Grand Total | 2263

## CPZs
CPZ | EPSS Device Global ID
ALHAMBRA 1101CB | {8AE2EF2A-3822-4BB8-8505-AA1FB37F605D}
ALHAMBRA 110213333 | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
ALHAMBRA 110281034 | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
ALHAMBRA 1102CB | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
ALHAMBRA 1105295792 | {8C6CE5F6-5F2A-4876-BD0D-A2DA021CCAD3}
ALHAMBRA 110581514 | {AC26085C-F280-4A6A-A0D9-361E1E9983F9}
ALHAMBRA 110582622 | {43B3FCFC-E570-42A3-9958-1934EF46169A}
ALHAMBRA 110582622 | {2DD5AD9E-82A0-40E3-9440-AC94C1A7128E}
ALHAMBRA 11058302 | {EAE1D7B0-E463-4F79-B04B-CDCA7EEEF36C}
ALHAMBRA 110595016 | {9A4542AE-EE8F-4BB7-BE2E-76002D6DCF25}
ALHAMBRA 1105CB | {36DDF29F-B22D-4B8A-AF4A-BB933D5333CF}
ALLEGHANY 1101183068 | {F078E4AC-B64C-461C-A921-5985B3E5BCBB}
ALLEGHANY 1101804 | {B02385C8-6373-4D81-ABD4-7C98960F9245}
ALLEGHANY 1101806 | {A90B9AA9-7F37-4154-B2B2-B43A5EF8D800}
ALLEGHANY 1101808 | {FD2262BF-C160-4434-8E95-55FF0A0B15F6}
ALLEGHANY 1101978 | {3479738B-50FC-4140-94A7-E159A76AE25B}
ALLEGHANY 1101CB | {326E3BAE-F690-4463-8FFC-C774FBAA59CE}
ALLEGHANY 1101DV 1101/2 | {C2CC1D79-89DB-4ECE-9478-5BA20AA53E99}
ALLEGHANY 1101SC 1101/2 | {0AD4AD2D-1FA2-436E-8047-FAB2722F7DE2}
ALLEGHANY 1101VR816 | {C309DB72-5D9A-4AC9-886D-5F718B64DFF4}
ALLEGHANY 1102CB | {303E53EF-22EF-468F-BD54-C029D47A56AA}
ALLEGHANY 1102WC 1101/2 | {144A1C59-970C-4C0B-893E-5971B69F35AA}
ALPINE 1101CB | {147B95CE-2512-4395-8036-5E41FB98DF5E}
ALTO 11201214 | {B3DBF89F-E691-4A93-8B05-2E162DB10E10}
ALTO 1120500 | {E6E93162-4459-4248-A579-2775F57735F8}
ALTO 112081716 | {AB366F07-2039-406C-B0DB-849A899ADA0E}
ALTO 112087204 | {D4FBBC03-A778-4C54-9456-3A890F4850F6}
ALTO 112088190 | {FB7430F5-69AD-42E3-8B5B-42F0E8A7B1F0}
ALTO 1120CB | {D4FBBC03-A778-4C54-9456-3A890F4850F6}
ALTO 1121508 | {987386B4-3AF7-40EE-94AC-C1508EDFA8F3}
ALTO 112191428 | {987386B4-3AF7-40EE-94AC-C1508EDFA8F3}
ALTO 1121CB | {AC60738C-EEA0-4867-B6FF-D969AE620995}
ALTO 11221212 | {480E1BDA-E928-4338-A7BA-DDA1B7A106EF}
ALTO 11221260 | {7808A995-1603-4DBC-94EF-C3DF7EAAE7DD}
ALTO 1122591122 | {E26D9B6D-6B45-4494-94E9-E5BD7162DD89}
ALTO 112265474 | {C2F314B0-1B7A-4CC5-862B-042BD22A1A33}
ALTO 112278672 | {792237E5-EE75-4319-AAE8-4FDB93CD8345}
ALTO 1122CB | {F8F75874-EBBE-4BAE-AEB7-B4201B2B809B}
ALTO 11231222 | {52729A7B-7BFA-4980-A850-5BD8CF10E4D2}
ALTO 112332448 | {C469F866-3A91-4B43-94B4-8116C5F6A5C8}
ALTO 1123CB | {727BD7F2-BE7C-4A08-9D75-7C070423C0FA}
ALTO 1123CB | {C4F18DDE-7DF7-43C4-9D20-1B47C5ED6CA4}
ALTO 1124246034 | {7D95830D-A648-4B7C-9FF3-8B171C1CA56A}
ALTO 11243121 | {5B9950E9-6C0C-44EE-B414-F2773560C367}
ALTO 11243745 | {5A7E1969-E475-4A2E-A5C6-85EFB5802FE4}
ALTO 1124428 | {27199B13-B86B-4E3B-B3CA-CB9918D6CC38}
ALTO 1124428 | {84CE664B-0611-4200-83BA-04B0E42A1B56}
ALTO 1124430 | {5B9950E9-6C0C-44EE-B414-F2773560C367}
ALTO 1124432 | {5A7E1969-E475-4A2E-A5C6-85EFB5802FE4}
ALTO 1124635972 | {09E5B2C8-C5E7-4FCA-92E9-55DF7D2FE60B}
ALTO 1124703432 | {60AD6E98-4C8E-4B03-A21E-57588A85616E}
ALTO 1124810594 | {D958A2D4-CE6E-4B3C-AC0F-6AE22C6D92E7}
ALTO 1124870444 | {856EAD72-BC3F-4C54-B04F-3629A4B87A87}
ALTO 1124CB | {2C543D7C-5902-4DC9-BE9B-719A66315791}
ALTO 1124CB | {B1454119-63A8-48AF-9377-F24B23472EF9}
ALTO 1124CB | {5017D9D5-0257-4525-9036-FC54DCC8E2D0}
ALTO 11251158 | {896F1F1F-796C-403D-AE33-2C5D4126F620}
ALTO 11251158 | {230CA050-BA1E-4373-AB59-B01CD2906F80}
ALTO 11251158 | {DC93F2BF-1FFD-4AAB-B042-E35ACAAAB3A8}
ALTO 11251158 | {1354222E-2584-48AC-B05D-15ACC6FB1CCF}
ALTO 11251226 | {E82C2F97-5C09-4976-BD47-A486EC875FA4}
ALTO 11251256 | {68422AE1-2121-4A4F-B961-26CF0C3DA27B}
ALTO 1125296476 | {0ECD6D03-E99B-4280-9CB5-4AEDBF369158}
ALTO 1125510 | {3D1372A7-8F04-4F4C-824F-7EEDAB15603F}
ALTO 1125530664 | {DA893851-A239-41E8-8E7B-70F066561313}
ALTO 11256405 | {DA893851-A239-41E8-8E7B-70F066561313}
ALTO 1125902 | {A0846B72-320F-48B2-9E0D-A5F9C3A78393}
ALTO 1125CB | {F6FBF85B-F199-40F3-8A70-868561B74EE6}
ANDERSON 11011390 | {F53F100A-A47D-4F77-AE95-9A2266045C73}
ANDERSON 11011752 | {ABE6F062-1CE8-44B2-8445-67D100174B10}
ANDERSON 1101514412 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
ANDERSON 1101583708 | {C1AE4ED5-9E2B-4787-958E-F3CEA46DF77D}
ANDERSON 1101810804 | {5720837F-AF3C-4D19-9FD1-A4D55662D2CC}
ANDERSON 1101CB | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
ANDERSON 1101CB | {A21FB6E2-C2EE-4D2F-B401-72361201D9F9}
ANDERSON 11029792 | {F240E67E-FE6C-498C-BF9F-54CAA8C204DD}
ANDERSON 110299392 | {82EAFCF1-F1E6-41E8-A0B3-25F73ADE0F7A}
ANDERSON 1102CB | {4CF4EB85-76D9-4518-B772-23773872AF10}
ANDERSON 11031600 | {38F7B678-11EB-498C-AD48-774BD4B8786F}
ANDERSON 1103193378 | {00748604-4E7C-487B-992B-00C51AC005AF}
ANDERSON 1103226050 | {F12B9CD1-046D-40CE-8D1D-9858A5F6226D}
ANDERSON 1103721690 | {53A9B8B1-BFDE-47C9-97AE-1322DE96BE54}
ANDERSON 1103CB | {87B1630C-320C-4426-9018-625251B99E73}
ANITA 11052572 | {BD567EF6-1FB2-4D01-8EA9-A26EEF378E91}
ANITA 11062074 | {F3D6F39A-52C7-4EF2-B536-42290D3060B9}
ANITA 11062418 | {BF1D640B-1AB6-49FB-AB3D-0A09BCB77224}
ANITA 11062462 | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
ANITA 11062496 | {CA64925E-CB77-4A47-8864-C246E9A1F937}
ANITA 110648098 | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
ANITA 1106552724 | {66BDFA7D-F7B6-403B-BF76-C55BF0419221}
ANITA 1106CB | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
ANNAPOLIS 1101202158 | {0B0F8D7C-2C4F-4CBA-AE85-A14338AA03E0}
ANNAPOLIS 1101528344 | {7D61C9A3-0A8E-455B-9684-CECD384B35D0}
ANNAPOLIS 110176842 | {2E3AB06D-E271-44D1-BCDE-8DE501692F34}
ANNAPOLIS 1101CB | {26E5272A-CBC3-4332-B0D6-5C00B9086880}
ANTELOPE 11012656 | {0223D8A4-0FAE-4E90-8B93-4043739FD071}
ANTELOPE 1101318686 | {946AC549-8FBD-4BEB-87DA-8E29BFBBE9D4}
ANTELOPE 11013609 | {F610032A-F2E0-4366-8F75-D3F075E51CA8}
ANTELOPE 1102CB | {C3268251-FFC0-4729-94B8-55800124A207}
ANTLER 11011376 | {96A0A843-7251-461B-B57C-57ECCA82B23A}
ANTLER 11011378 | {06D2F196-2635-44B3-B616-380DADBEF83C}
ANTLER 11011378 | {8E148904-632C-4897-8A4C-68D035CA5B54}
ANTLER 11011378 | {C885D848-026E-4C6E-A0E7-D886450B2EC9}
ANTLER 11011384 | {C5E3EE8D-D562-41BA-8596-EEF5987F2F11}
ANTLER 11011520 | {F81A30D4-0CE7-4E7B-A7EB-CF369AB53D11}
ANTLER 11011612 | {EAAD5F12-9AE3-4341-A497-B18C1046E2B5}
ANTLER 1101484276 | {EE25C3E5-291C-49B5-AB87-572752CC4B0A}
ANTLER 1101718316 | {4413B493-DE83-49E8-BEE8-12AA31A465DE}
ANTLER 1101CB | {5E7DC64A-0B4A-4299-87CB-EE1D39916B3F}
APPLE HILL 110313312 | {4D62B52A-6FFC-40E3-9CBB-F053155CEAAC}
APPLE HILL 11038412 | {07722CD6-14E4-4447-AD94-AC55195AC8E1}
APPLE HILL 1103CB | {DD461B3A-397C-4A3A-A4DD-6F0A05715903}
APPLE HILL 110412832 | {0010E3CC-5B34-4785-98D9-D2D98BC731B3}
APPLE HILL 110412842 | {04FA73EB-B797-476B-86A7-C1CFAD605BCA}
APPLE HILL 110413512 | {C961DA87-D3C6-40FA-87BC-1A5AB7DF3FCD}
APPLE HILL 1104236062 | {78CB65A8-D5F1-4141-9775-453719688C2B}
APPLE HILL 1104275024 | {60D1E266-474C-4944-877D-C3B4C2A1D233}
APPLE HILL 110497086 | {E9B2D551-2CAF-489B-9D1C-4D1BCFDB0559}
APPLE HILL 1104CB | {C95685B7-B649-4BB7-AFD8-6C20EE89F893}
APPLE HILL 21021532 | {9C4905F1-5CAF-4EA3-AEC8-7E33B8AB07B0}
APPLE HILL 21021532 | {4A1B7FA4-9EA2-489A-952B-02F0D69E191E}
APPLE HILL 2102186912 | {FB182C0F-B71E-4B89-801E-E64DB8A5CDBB}
APPLE HILL 210239544 | {67403348-AD5A-4D81-B973-25AED6358693}
APPLE HILL 2102501650 | {4047ABE5-181C-4DB3-9DBB-212375DDD70B}
APPLE HILL 210251792 | {60540539-B6BA-4E80-BC6C-988DA579218B}
APPLE HILL 21026552 | {4065F493-7B96-40A7-8EE5-29CF10B90CA4}
APPLE HILL 21027502 | {730CDBAB-B217-4D30-9612-715B7140F38A}
APPLE HILL 210277546 | {71852C93-FB23-454D-AA22-159ABBF0F364}
APPLE HILL 2102836878 | {CB359284-0736-45D2-B59D-DFB4E12FD162}
APPLE HILL 21028372 | {87934A6A-C9D7-420E-9278-5C4F8DB79DED}
APPLE HILL 210289934 | {94D1A3AD-4895-43D5-80BA-F27D9B67BD20}
APPLE HILL 21029722 | {CD700C3D-374F-40E3-8624-DAD7800FADA7}
APPLE HILL 210297982 | {1FCD571D-957E-4FF9-863E-0126FD4A401D}
APPLE HILL 2102CB | {5DC9E720-795B-432E-BA68-667FD0BD630A}
ARBUCKLE 110194064 | {B2E83566-334B-4D06-8145-C26AD63C12BB}
ARBUCKLE 110447282 | {44D6ED2F-777A-4FEB-A593-3F9A2FF8D4A7}
ARBUCKLE 1104656592 | {20D0259F-0F20-437E-ADAA-0E44C8DDA743}
ARBUCKLE 1104669720 | {4F1CDC69-EA0B-4135-93B4-1C48EA3748CD}
ARBUCKLE 1104969486 | {09231E8B-9807-445C-B8AC-5325493AFFCC}
ARCATA 11211206 | {AF459D89-AFC9-4CD3-8D0B-AF684DED3FA0}
ARCATA 11216004 | {7105441B-4177-4883-821E-B79840B9E771}
ARCATA 1121716954 | {FF12024C-319B-45A6-9F88-A7BDDD085162}
ARCATA 1121716954 | {6E3AE2B4-F135-43F0-832F-E39BC5035CBC}
ARCATA 1121716954 | {2938B984-F7EB-4FD2-BCCA-0E89F66CB086}
ARCATA 1121CB | {B9FFA3B9-62B6-4B90-9671-6A7AB6EDF708}
ARCATA 11220664 | {82E30D47-3E2A-4E87-8D66-B620821B7943}
ARCATA 1122328150 | {8FD0CF2A-B76A-4A6B-BC5A-684C3A58EA8B}
ARCATA 112233060 | {21ADCA93-F696-42D2-B9AB-0580CBDEB386}
ARCATA 112233062 | {B31BB8D7-E9FC-4E78-862F-0335ED33A574}
ARCATA 11225384 | {367A2503-D1F3-412A-9C31-B8346F988B1A}
ARCATA 11225384 | {F8ACD64A-30F6-4E37-A172-24BA9176BE45}
ARCATA 112293912 | {B31BB8D7-E9FC-4E78-862F-0335ED33A574}
ARCATA 1122CB | {4D343D95-65B7-4F09-8335-963B7DE7388B}
ARLINGTON 0401404226 | {B073565E-E5DC-4302-BADE-27F696E6F580}
ARLINGTON 0401CB | {B0F9DF73-E5FE-4D63-9A97-F698C647DBAA}
ARVIN 110115909 | {2B1BA581-45FA-4D2D-868E-E1CB0E681EBA}
ARVIN 110169618 | {2B1BA581-45FA-4D2D-868E-E1CB0E681EBA}
ARVIN 110194892 | {2B1BA581-45FA-4D2D-868E-E1CB0E681EBA}
ATASCADERO 1101A02 | {F4592309-FF5C-4AE7-B40E-CF8D73FD01E6}
ATASCADERO 1101A22 | {1A2AEC20-7798-471E-990E-3BD9D80801FA}
ATASCADERO 1101A50 | {CC1F4643-49D2-4B99-B353-84FF1B6CAA23}
ATASCADERO 1101A50 | {C74334F6-C157-4384-BFB7-ED7E4C2B59D6}
ATASCADERO 1101CB | {98F44516-A7DA-4F88-98E1-7BF277BBBD67}
ATASCADERO 1102A26 | {C057EF7E-9D13-4CEE-8644-90B6E434EFC2}
ATASCADERO 1102A26 | {DA2C7B5E-6C7B-401F-B35E-CA8BB5D3B738}
ATASCADERO 1102A28 | {7017AD32-E07A-4554-A2AD-C732D91DBE2C}
ATASCADERO 1102A88 | {553C693F-FB0A-403F-AF7B-DFD04F0B4035}
ATASCADERO 1102CB | {E22A44CE-34F2-45EB-BA42-C88A6CDC3537}
ATASCADERO 1103440856 | {CE1B4F1D-0818-4F54-96A6-5CB8D8BF7895}
ATASCADERO 1103492068 | {BDD83B1C-28F8-4B09-B7CE-E948BFB7D564}
ATASCADERO 1103635958 | {F5631237-9E9F-4E89-82C9-2C77B3AF73EC}
ATASCADERO 1103A06 | {850B41E6-E885-4F34-842C-9B877CC07C7A}
ATASCADERO 1103A16 | {DCD0DC19-914F-4CFB-A070-C04552F2A497}
ATASCADERO 1103A18 | {1D2DA1C9-B2A9-4713-BA25-DD6CA0F657BB}
ATASCADERO 1103A46 | {614AFF73-1972-445B-AB78-45C825B90AEF}
ATASCADERO 1103A80 | {01E75A4D-5E59-4C31-876B-BB494E0AE408}
ATASCADERO 1103CB | {80C03548-09A3-4516-9CD7-A85242729AF9}
AUBERRY 1101233716 | {4B373C79-EE2B-4490-BA99-503E66D60707}
AUBERRY 1101323028 | {90ABCC1D-5DD8-43C1-9AC0-715DCF2D275E}
AUBERRY 110137536 | {45D15552-78D5-442B-BA6F-9416A2388C3B}
AUBERRY 110149122 | {6985CB9B-1F8C-4CB7-A5AE-AEFA2BA7C828}
AUBERRY 110149122 | {BA3893C1-711D-4BF6-9767-7C0EC1B0CA4D}
AUBERRY 1101CB | {50F15232-B267-496F-ACCD-C66670CD5E1D}
AUBERRY 1101D4982 | {90ABCC1D-5DD8-43C1-9AC0-715DCF2D275E}
AUBERRY 1101R2578 | {E7B58C7C-DEE3-44AF-9DC1-540E49CB1676}
AUBERRY 1101R2579 | {1328D5B4-6BC6-4A19-8B7D-C1E2266894DF}
AUBERRY 1101R2838 | {48B8D134-2217-4EE4-BD7C-3270CBBFB37D}
AUBERRY 1101R2839 | {1D410A42-CC20-42CD-9AF0-41D38F1027D3}
AUBERRY 1101R2845 | {AF3C9CC3-4B67-4003-BBC4-2AADCCAC2E66}
AUBERRY 1101R314 | {4F5EBE36-6D68-4A47-AF49-0D6F0830F1BC}
AUBERRY 1101R324 | {E1E5839C-1351-4866-AD70-89FE7DE5E158}
AUBERRY 110237466 | {72B3FD6E-4E00-4CD9-8668-70733AC266B2}
AUBERRY 1102CB | {004C66A4-EFD9-4F4F-AA71-77719D3D9AC9}
AUBERRY 1102R1013 | {71E8F95F-8504-4520-9C3B-8AB71CD7CDDD}
AUBERRY 1102R2850 | {CFE5622E-640A-4701-B25A-30E645D814D9}
AUBERRY 1102R309 | {6CB8407B-8DEC-4DDB-A06C-70CFC4C2C27B}
AUBERRY 1102R902 | {5ED2B13E-98E4-45F9-A6A0-57DA496030DD}
AUBURN 1101173014 | {ACC7CE4E-E9FD-4F32-956F-F6FB27435C5C}
AUBURN 1101CB | {0654A595-233E-4128-BBD6-123F6D88D1DE}
AUBURN 1102251946 | {F47804CC-754A-4FCA-B217-8CAF682A164E}
AUBURN 11028611 | {F47804CC-754A-4FCA-B217-8CAF682A164E}
AUBURN 1102CB | {8B190E99-2FFD-4283-B3F1-C9A94DD8C8D7}
AVENA 170212876 | {3E1C42BA-A837-4BE0-A8EE-C29428358DD7}
AVENA 17025494 | {3E1C42BA-A837-4BE0-A8EE-C29428358DD7}
AVENAL 210144778 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
AVENAL 2101602496 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
AVENAL 21019070 | {BA67822C-2303-4723-983B-9142A9A0088D}
AVENAL 21019810 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
BALCH NO 1 1101105414 | {AE86CCC0-9A32-4ECB-B70D-2CCE4DDF5F1F}
BALCH NO 1 1101406582 | {F32CC135-97A4-4BFA-A01E-518E8F21967F}
BALCH NO 1 1101R372 | {A73833CF-1AF8-4A38-AFD0-B16A74E1496D}
BANGOR 11011804 | {F430F9BA-4822-49EF-972E-D271E55910BA}
BANGOR 11011806 | {ABE5C26B-A76B-46B8-A04C-0EC15FF8F909}
BANGOR 11011958 | {4EADDDA4-9026-4CB9-B9C4-03D97B5E8FF0}
BANGOR 11011958 | {11F38EC3-5F35-4498-B01A-5E1A27124E84}
BANGOR 110131502 | {6925CBA3-93E0-44A7-B2DC-50805D93ECF4}
BANGOR 1101498380 | {B3637D02-5D81-4552-9104-06FFEBB0B445}
BANGOR 1101537672 | {50071A42-1669-4AE7-A593-9FFF3A6A09B5}
BANGOR 1101614048 | {5063F2C6-9AF9-45AF-BA98-1D8C5E52CC95}
BANGOR 1101614048 | {808B9A32-C42D-445B-9979-179B0B7A37BE}
BANGOR 1101626862 | {9C69B9F4-7C5C-4BD0-9159-FF9477A29E57}
BANGOR 11017446 | {37FE066D-28CF-4140-A2D0-4ABC1EA8F8E8}
BANGOR 11017446 | {1FB07492-7817-4281-B458-54D457C1DE65}
BANGOR 110182350 | {61206052-9537-4FFD-A305-D8F681D781BF}
BANGOR 1101870548 | {16EDAC9B-8C49-4185-9FE4-CF4748324FBE}
BANGOR 1101CB | {CB9FA698-E2B3-4923-A1DA-DA7C548C122C}
BANGOR 1101CB | {C9648835-EB5A-442A-856F-5456F572C3DC}
BANGOR 1101CB | {95A6A954-1179-44FA-AE45-DBA914F6C1CE}
BASALT 110138824 | {848BC58D-4F0A-4BE8-A349-0A623ECC18C6}
BASALT 110175886 | {0FAE99A3-272C-4D4D-AE6A-B1955441A366}
BASALT 1101860318 | {36CB0205-94DA-45AD-B087-D2736F00D26A}
BASALT 1101CB | {36CB0205-94DA-45AD-B087-D2736F00D26A}
BASALT 1104CB | {1D69793B-6513-4BDE-BB21-BAE25C357436}
BASALT 1105CB | {6CFDCF11-C002-42A5-AACA-1A265A50033F}
BASALT 11061781 | {230E7534-26E2-46DC-BF08-6106FB749B89}
BASALT 11062103 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
BASALT 1106267462 | {B44FE367-DC69-440D-96D5-5E7D077FB65E}
BASALT 1106316302 | {4B4F529E-61C9-4763-88C9-BA9E643D6014}
BASALT 110635550 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
BASALT 11065030 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
BASALT 1106657038 | {0C9DEF06-9AAB-4128-9810-85E010FF7C1A}
BASALT 1106724 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
BASALT 1106783176 | {0C9DEF06-9AAB-4128-9810-85E010FF7C1A}
BASALT 1106CB | {230E7534-26E2-46DC-BF08-6106FB749B89}
BASALT 1106CUS167 | {4B4F529E-61C9-4763-88C9-BA9E643D6014}
BAY MEADOWS 110565187 | {4460A2C3-E57A-4228-8E6E-BAA1830E8AC4}
BAY MEADOWS 210248770 | {89242FEE-8748-42BC-8EA8-CDD97EA44EAD}
BAY MEADOWS 210257886 | {D73C61C6-F360-40B2-9388-D54915745260}
BAY MEADOWS 21029062 | {89242FEE-8748-42BC-8EA8-CDD97EA44EAD}
BAY MEADOWS 21029162 | {7B48B738-B738-4F2B-B0D7-4D191D860D4E}
BAY MEADOWS 2102CB | {7B48B738-B738-4F2B-B0D7-4D191D860D4E}
BAYWOOD 1101CB | {82D72170-020E-4DD7-9C9F-960EDB0862CE}
BAYWOOD 1101V102 | {6A94C75C-2B9D-417A-8946-7997EE49AE89}
BEAR VALLEY 210110000 | {0D159A34-F101-472F-9F8B-631446B0CF4C}
BEAR VALLEY 210110019 | {01E04AB3-4BC7-461C-86D6-3A3D5CD166F9}
BEAR VALLEY 21014160 | {853E569F-DA3D-4A9C-B01E-E103347AC121}
BEAR VALLEY 21014500 | {D468A32E-4500-4D2C-80DA-85F74A9A6EF3}
BEAR VALLEY 210190550 | {CE2E0286-475F-4451-81F2-51329124240C}
BEAR VALLEY 2101CB | {01E04AB3-4BC7-461C-86D6-3A3D5CD166F9}
BEAR VALLEY 210513430 | {F76AEDBB-91E0-4407-A41D-F6794405D1E1}
BEAR VALLEY 210521160 | {BAB6581B-1DEF-4E8B-AEF9-096FA24A0638}
BEAR VALLEY 2105293732 | {ABB0CC40-D4C3-4C01-9BEA-4570C6C0972F}
BEAR VALLEY 21054170 | {ABA71BA3-C71D-490E-AEB5-C37239F168A1}
BEAR VALLEY 2105454432 | {11DB8C84-C8EE-401C-AB12-1A2E81A02CED}
BEAR VALLEY 210576694 | {DBF29453-0B03-42AD-A97A-1CA961543977}
BEAR VALLEY 2105916436 | {C5D51BCC-B370-48A3-8349-FB710857EC4B}
BEAR VALLEY 21059480 | {83E15892-C159-48B2-98C7-95188F40B517}
BEAR VALLEY 21059570 | {C6F77565-3ECF-49F4-A49E-50D716B67BE9}
BEAR VALLEY 2105CB | {3A07F3B8-E9B8-45C5-8744-6792C16A4186}
BELL 11072400 | {DB8C8898-F3FD-4C6D-9D99-FE8F56C2485D}
BELL 110750172 | {6BF0E854-A546-4347-BF88-873ABBCE7D58}
BELL 1107643778 | {B62CEF1F-B5AF-4B96-9E64-FF58A6B33C79}
BELL 1107CB | {49E80940-99B4-47A0-948C-E1482C4F88F1}
BELL 1107CB | {CD565697-14B6-4AA0-954C-46CA84031737}
BELL 1108127062 | {EA7A922D-E9BD-484D-B6ED-929B9EBF7C80}
BELL 11082202 | {C705CC3B-4CE7-4574-9451-1595DBBA258B}
BELL 11082226 | {FF6B966D-B6C9-448E-9EAD-BA4CD433B469}
BELL 1108339792 | {C5B6945A-DE5A-4681-9AEF-7B6CF23C0D53}
BELL 1108351852 | {50A19D76-23E4-4194-A546-FA4EB9B67EC9}
BELL 1108533042 | {3E1C7211-235E-420D-A32C-57DAE88986D6}
BELL 110880680 | {3A2A466A-E07F-43BB-BFCA-7454C5908F19}
BELL 1108CB | {35B30399-E588-44B0-B481-56F6CD9688B5}
BELL 110950506 | {085B8A15-383C-4AC7-8C00-A9FA8BED6EBE}
BELL 110950520 | {C66EE736-987A-4FEF-A8AF-F6DA5647068C}
BELL 1109724884 | {C6312B9E-C10C-4771-B9EE-B7179EF46C16}
BELL 1109CB | {4EF25014-B554-454F-9BE5-F3AB9DDDB6E9}
BELL 111050182 | {6B9F0345-026B-4979-BA83-3B077A617109}
BELL 111050522 | {E670C03E-CA4E-48A0-8E3D-40CC604AC7DD}
BELL 111056214 | {AAA117DC-6FD5-43B8-AB6A-D4EAC9CEEA32}
BELL 1110CB | {451291E3-291B-4A82-B036-A633A631A6D2}
BELLEVUE 1102182 | {2902212F-4C02-4AB4-BB89-DFDC181B544C}
BELLEVUE 1102463316 | {D29926DB-AE31-4DF0-BAC8-C7164572C130}
BELLEVUE 2101335190 | {91F5D445-CCB5-4AE4-9883-27CF7A3A57E6}
BELLEVUE 2101646 | {BEA97E4E-CFBB-4EAF-9EAB-B9D9096C26BD}
BELLEVUE 2101648 | {BB094C57-2223-469C-ABF0-9ADC89223899}
BELLEVUE 2101CB | {09987E11-E541-4564-AE03-05F03FAC13CB}
BELLEVUE 2103388 | {018227D6-38CC-4EE9-BD26-7E3FF5AE9B25}
BELLEVUE 210342412 | {AB1749CC-E955-4627-948C-09860E609DAF}
BELLEVUE 2103940234 | {018227D6-38CC-4EE9-BD26-7E3FF5AE9B25}
BELLEVUE 2103CB | {D7E9D0AF-E912-4093-ACB1-C01E71ABC496}
BELMONT 110268446 | {E797AB19-3600-4F18-89F8-9B9F590AAC2A}
BELMONT 11028918 | {8299BD19-90A4-4D64-8B9E-E4A475CD494E}
BELMONT 110347804 | {84C88409-8465-4D6B-B014-0E4B9C728457}
BELMONT 1103543076 | {84C88409-8465-4D6B-B014-0E4B9C728457}
BELMONT 11038956 | {1467F520-572F-46EC-93E0-707DAECC5FB0}
BELMONT 11038958 | {B68C4BA8-94F5-4FA3-9062-8EFAD0B4F95D}
BELMONT 1110330790 | {E5D2E9A8-3F25-4DA6-AD92-5C753B714148}
BELMONT 111039182 | {2B049CE5-6DAC-4065-B555-915EF340A6E9}
BELMONT 11103975 | {650AE2A0-8481-4167-A199-68E796B3390A}
BELMONT 11104845 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
BELMONT 11104946 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
BELMONT 11109088 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
BELMONT 11109090 | {650AE2A0-8481-4167-A199-68E796B3390A}
BEN LOMOND 040116010 | {52BA473C-1BA5-4952-86A7-343CF045CF65}
BEN LOMOND 04015144 | {8CE26437-AB3D-4CA1-B3DD-136FBC93120B}
BEN LOMOND 04015400 | {81F477DE-A079-435A-9F55-2410FEC944BA}
BEN LOMOND 0401698634 | {84DC7993-D314-489B-A9D8-96434904B6FE}
BEN LOMOND 0401944178 | {EB10C4EE-4491-4EBB-BF92-473E5065B27C}
BEN LOMOND 110196738 | {EA87785F-FD13-47C1-AD0C-AE56EB6FAE60}
BEN LOMOND 1101BL 1101 | {97243609-0190-4CA4-910D-8656166A7529}
BERESFORD 0403435168 | {9E0ECC0E-D080-43C9-A87B-75BDCB2E0E91}
BERESFORD 0403855954 | {D4A9962C-7929-42D6-9791-5B60C706E999}
BERESFORD 04039154 | {59262E1A-A9BD-4C08-8147-3EF20A86F7EA}
BERKELEY F 0402502466 | {5BAFA9F8-CA96-406F-9803-715FC721E178}
BERKELEY F 1103162952 | {0AD46168-2B6E-4761-82AD-462845B00603}
BERKELEY F 1103620294 | {A3A50FD3-D864-4F5A-8B1F-9F554249643F}
BERKELEY F 1103813976 | {8BB0C622-0BA1-48A6-BC5B-DC08A0DC776B}
BERKELEY F 1103BR110 | {C6EF6B66-22B5-4479-8720-12455A79DA2B}
BERKELEY F 1105189500 | {5B19BE61-6886-4FC7-B0FB-4DA13CF3F560}
BERKELEY F 1105BR100 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BERKELEY F 1105BR106 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BERKELEY F 1105BR166 | {ABB7B77D-2EF2-4B3C-9B77-BF1774A4BD64}
BERKELEY F 1105BR168 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BERKELEY F 1105CB | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BERRENDA A 1101CB | {FD8A5294-9952-41B0-9949-0D7EF73FF10D}
BIG BASIN 110110720 | {1594C1F1-1EBD-4EB0-9A76-086953E0C574}
BIG BASIN 110112838 | {CC60F8EB-8583-4463-B38C-D2F869F171F0}
BIG BASIN 1101136050 | {EC6DAEAE-4663-4197-A593-D4839F2AF80A}
BIG BASIN 1101136050 | {D289407A-D347-4D80-AEB6-2C2B754CD8EC}
BIG BASIN 1101393582 | {498E3237-3BEA-4CD5-BBB3-313CDEBA801E}
BIG BASIN 1101595388 | {BF396B32-BD22-486B-867E-90456CF37674}
BIG BASIN 1101654386 | {AFA25227-DFA1-4EA5-A377-3B377C42257E}
BIG BASIN 1101654386 | {AE056BEF-ECED-4EBC-BAE2-8A81892BDAAF}
BIG BASIN 110165444 | {E247FC6E-157B-4272-AEDD-8C777FFAAD92}
BIG BASIN 110169550 | {6AB8FDF6-DF60-4669-94F5-76C04F7F5767}
BIG BASIN 110169550 | {0BA1101B-99F3-4D87-946C-F832D0B52AF5}
BIG BASIN 110195690 | {0F585841-A965-44FC-98CB-5C72CA920770}
BIG BASIN 1101CB | {94CF54F7-C6CD-4453-B5AE-8C10C6BEE2CA}
BIG BASIN 110210254 | {15D4C8BA-CC0A-4EB2-8B2F-A8AED4A99003}
BIG BASIN 110212124 | {5E67FDC7-6621-4E4B-BC49-469EB29666B6}
BIG BASIN 110212758 | {99A79B5B-089E-4FC6-A0B0-CC4BF6257CED}
BIG BASIN 110212992 | {1695E978-9BD4-42EE-A017-6DD99E4F027F}
BIG BASIN 11022253 | {634E25F6-7941-40E8-9E1F-430E935AA77A}
BIG BASIN 1102243760 | {634E25F6-7941-40E8-9E1F-430E935AA77A}
BIG BASIN 1102307348 | {684496E5-6AA8-4CE0-BD15-F571AD20F865}
BIG BASIN 1102351054 | {2DB85505-B58C-4180-BE1F-5ECE90BED242}
BIG BASIN 11025066 | {A725B58B-37EB-4147-83B3-63635BC09A1B}
BIG BASIN 110276752 | {7395FFA4-03E8-4D80-A8FA-546880E8DDC7}
BIG BASIN 11028403 | {1695E978-9BD4-42EE-A017-6DD99E4F027F}
BIG BASIN 110296986 | {87B7E394-3606-4372-9564-36FE0E57DA45}
BIG BASIN 1102CB | {7DF78B7A-3D58-4011-B365-74BA17A842F7}
BIG BEND 1101180398 | {8A0E1297-B2C6-4E29-9AF9-DF1E115646B0}
BIG BEND 1101641808 | {5A96A91D-9C08-4D36-BEF1-A7C7B5FBE746}
BIG BEND 1101641808 | {A3F84BA5-8D5A-4B0D-AFE9-3E2A03521912}
BIG BEND 1101CB | {25C4070D-0704-4FE8-B250-876F6C426225}
BIG BEND 1102884340 | {DF76653F-9A84-406D-B399-26AC3048352B}
BIG BEND 1102CB | {05EF3BA2-F04A-49CF-AF87-10424EDE6926}
BIG MEADOWS 21012016 | {6B2D5F4D-4DFC-49DF-85DE-2AF9D30D36A6}
BIG MEADOWS 21012246 | {FF704EC9-7B07-4166-A0E1-5C891877A473}
BIG MEADOWS 21012248 | {1667C171-4E6E-402D-B45F-3BA2B8FB113A}
BIG MEADOWS 21012260 | {18489341-7942-4EE1-95D9-22D6837A669D}
BIG MEADOWS 21012474 | {CAAE778D-9C35-4E23-898C-4B832CDD3B89}
BIG MEADOWS 21012476 | {A5EA53CA-65A7-43BC-BB3E-43041FB8E51A}
BIG MEADOWS 21012510 | {2FDD93D7-D61D-44CD-93DA-C1ACCE10D2C0}
BIG MEADOWS 21012586 | {70718D9A-2BF1-4C9C-AEE6-9A1119246050}
BIG MEADOWS 2101CB | {48DFC761-81AC-4E6E-A815-DEA2190E6576}
BIG RIVER 11011052 | {774F8E82-5627-4004-BA65-1CFB3311B274}
BIG RIVER 11011286 | {DFBBBB18-D02D-419D-977F-28C5BC8837E8}
BIG RIVER 11012183 | {A36BE560-E1CB-4559-8E7E-01132EBA1D0A}
BIG RIVER 11012989 | {2D8E8FC7-3A5C-40AE-8F67-02A91CEAEC16}
BIG RIVER 11013002 | {E6F8FC53-7441-41DA-90B5-FEDD62BCC4B4}
BIG RIVER 11013002 | {D95A7C0C-0AF4-4CEB-8EB2-04C841B078C9}
BIG RIVER 110155402 | {2D8E8FC7-3A5C-40AE-8F67-02A91CEAEC16}
BIG RIVER 110169032 | {B18E180C-39A4-4EFB-8DCB-B1B629947F6E}
BIG RIVER 110179628 | {82A21CBC-843C-4ABE-B864-8FD58FD45315}
BIG RIVER 110179628 | {20E18CC8-D4A7-4B74-B6A8-456036AC47A2}
BIG RIVER 1101952 | {1DB69746-E909-4FD7-90E8-E346F8AB657A}
BIG RIVER 1101954 | {A36BE560-E1CB-4559-8E7E-01132EBA1D0A}
BIG RIVER 1101CB | {BCC029FE-B790-4D1A-9B12-5D2C7AA3930D}
BLUE LAKE 11013578 | {2B080883-3F89-467A-86D3-526324676232}
BLUE LAKE 1101CB | {E31E0DBD-FA9C-4715-8BFA-E451681E5B43}
BLUE LAKE 11021024 | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
BLUE LAKE 11024624 | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
BLUE LAKE 110256630 | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
BLUE LAKE 110266454 | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
BLUE LAKE 110294240 | {6705332E-2929-4E9F-8E1A-9444B006678B}
BLUE LAKE 1102CB | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
BOGARD 1101CB | {4D0F6AF0-AE59-447B-B052-BCC3C8B2DAA2}
BOLINAS 11011064 | {196072E3-9BAD-4649-BDA0-FE3AF88F88C8}
BOLINAS 11011232 | {6FB5348B-5DA9-49B1-98A7-B3620A483016}
BOLINAS 11011236 | {6AEEBA49-CC4B-431B-92AA-34EB4CB9F64F}
BOLINAS 110137034 | {92DF57CB-130C-4B97-B59B-998A6C49E6E1}
BOLINAS 110146152 | {14035AAB-B6A7-4C8F-9B08-2EC08FB0B5E9}
BOLINAS 1101504 | {24FD9F9F-3AE5-44A3-85E5-C29F5C852455}
BOLINAS 1101528 | {E52E3AA8-626F-4DCF-BFEC-F21E6141C71E}
BOLINAS 1101530 | {E368881D-C918-4559-9B53-61F2E5E1FBD8}
BOLINAS 1101806 | {52879B9D-A33B-4D4E-99FA-0487B37405B8}
BOLINAS 1101CB | {86BA3963-96A5-4181-83CD-FA7B5EC47222}
BONNIE NOOK 1101CB | {9FFB5CDC-505F-4B8E-9B6D-E79E68D9EC60}
BONNIE NOOK 1102542186 | {297BF28C-8BC3-41EA-8E65-D92643DE031D}
BONNIE NOOK 1102CB | {3EE03E8E-7174-416B-B7B0-D49DC8F3C48B}
BONNIE NOOK 1103CB | {C90BDB25-C8EE-44ED-88EB-56C4AFDDB087}
BRENTWOOD 210519062 | {05E5BF7A-7308-4C97-B511-1A2E6E9E6D92}
BRENTWOOD 2105219013 | {73088D62-3A1B-4094-930F-67E177B3F8E6}
BRENTWOOD 2105500796 | {20554200-5340-4600-A74E-4043866C22E6}
BRENTWOOD 2105502672 | {B557525E-C955-4555-A43D-602C62B6D5B3}
BRENTWOOD 21056512 | {DA007DA4-760F-4151-A582-C98D9C468550}
BRENTWOOD 210596324 | {8B109078-C964-45C9-BF00-4904308EBFAE}
BRENTWOOD 210598606 | {659CB7C9-DF34-4927-8487-32FE0AC742E7}
BRENTWOOD 2105B504R | {9A8233B7-234B-46CF-8EEF-6B74776F9D38}
BRENTWOOD 2105B534R | {9C413BEB-102E-4BE4-83F6-909D0B4AB75B}
BRENTWOOD 2110CB | {656225FC-E476-48B0-B77B-181188E8D8F8}
BRENTWOOD 211199210 | {E5AF8736-114E-4C01-9F04-EE6BE2C6FDFA}
BRENTWOOD 2111CB | {E5AF8736-114E-4C01-9F04-EE6BE2C6FDFA}
BRIDGEVILLE 110137484 | {24C71D6A-46DB-4BB7-8807-9800CAD347CE}
BRIDGEVILLE 110169866 | {3BB5B038-4064-4F43-B944-1BDE53135960}
BRIDGEVILLE 1101CB | {FC8DA5F1-E256-452E-840A-DB2CC55A41C4}
BRIDGEVILLE 1102353222 | {7337F134-7FAF-4975-B99D-C63324850B37}
BRIDGEVILLE 110237486 | {DC0A7D01-2EED-443F-A8C6-2C05CEB2611C}
BRIDGEVILLE 110255612 | {16121076-8F7B-4A07-9991-9C360FE94AC6}
BRIDGEVILLE 1102839652 | {6A116841-A841-40C3-9B48-86C4D5331427}
BRIDGEVILLE 1102CB | {5393CBB1-CE75-4399-B6C7-25EB732D48AF}
BROWNS VALLEY 11011268 | {868A573A-DC6D-45C3-92E0-27ABE99A6BF7}
BROWNS VALLEY 110136622 | {EF947682-77F0-46FF-B597-C974CCFEC84A}
BROWNS VALLEY 110193870 | {77D006A2-E276-4C22-A5B0-EE84D8EA3177}
BROWNS VALLEY 110197188 | {D76845FE-B268-426A-A73C-E770602E73F9}
BROWNS VALLEY 1101CB | {3F3AA0D2-CD3D-432D-9160-6EFA10A51D9D}
BRUNSWICK 11021010 | {CA5C38FD-CE12-4872-96AA-D926F4220C4F}
BRUNSWICK 1102940 | {8A1F3383-8C42-4458-990C-2355B321D3F3}
BRUNSWICK 1102CB | {0BF84A9F-DBEC-4CA7-98FB-695194286708}
BRUNSWICK 1103164092 | {58929914-99C2-4C8E-B85B-CC617974C9CA}
BRUNSWICK 1103173934 | {4D42C841-B88C-453F-8358-63D2C1E45D9F}
BRUNSWICK 1103173934 | {04D37AC0-1325-4EC9-B6FB-C903BA33F6BD}
BRUNSWICK 11032200 | {8832E15C-A8F3-49CE-9AF2-19EADE479033}
BRUNSWICK 1103234378 | {69E159D4-B5BB-47CF-962F-03601F5F22F3}
BRUNSWICK 1103262343 | {8DEE04BC-1F93-42B1-9D32-1482C9BA3DA3}
BRUNSWICK 11032784 | {A034BC39-5C36-44F2-830F-5D5EFC9DEDAA}
BRUNSWICK 110350070 | {DB1F9D2B-D359-4F2E-9F3F-F43B886E9D0B}
BRUNSWICK 1103639148 | {F18B8210-FBEC-4E04-A79C-5C0A5F7DDB09}
BRUNSWICK 110378862 | {B83D09DE-3D47-4840-BFDB-F992D85178B8}
BRUNSWICK 1103851116 | {32013278-E652-4636-8622-02EE3E5AF946}
BRUNSWICK 1103852240 | {D2CFCF41-58C5-4503-B8F1-FDC586F0302A}
BRUNSWICK 11038918 | {D34CE8D2-4E63-4899-B49E-7C6D0FD502F0}
BRUNSWICK 1103904574 | {1762E3E3-DCB4-41D0-A815-060A5A457F0D}
BRUNSWICK 1103956424 | {3FB24E68-4827-4A80-90A1-2EAF2EBC79EB}
BRUNSWICK 1103CB | {D972EC75-3864-4C3E-9FB0-5B538887AB46}
BRUNSWICK 11041020 | {DBDF15C5-1C5A-46A1-9C80-FCF08A12927F}
BRUNSWICK 11042112 | {1C515CF3-FCCE-4095-B61A-ED44FA9AA5B1}
BRUNSWICK 11042112 | {5D7A1019-73A7-4921-AA73-859EBCF0FBCE}
BRUNSWICK 1104285704 | {252458C9-C847-447C-8725-6EE8EF8017F8}
BRUNSWICK 110456468 | {A316ED50-5AA1-4ED8-AC7C-24B23FF6CC3D}
BRUNSWICK 1104761310 | {3AE21CFF-B1F8-4F68-931E-FCCDD52142DD}
BRUNSWICK 1104789062 | {9C94BAE7-5392-4BE2-B54A-A9765B78E00E}
BRUNSWICK 1104CB | {4DC4BD40-BC56-400F-B12D-56D1E0B91D5C}
BRUNSWICK 1104CB | {BEA0A501-B4D2-4CC0-BAE4-F7EC8C1D8A1B}
BRUNSWICK 1104CB | {1075F189-27AE-463D-9A6F-C9AFE8205A68}
BRUNSWICK 11051030 | {B6CCA276-60FE-4AA5-8337-7F4B8BC06A51}
BRUNSWICK 11052100 | {EB9602B6-3B78-44B7-9264-163222D3097C}
BRUNSWICK 11052130 | {12398A09-47B6-4618-B7A8-07F9B9DF4D2E}
BRUNSWICK 11052140 | {F48F30DF-84CD-4C48-AE91-CC0DFAC8DA65}
BRUNSWICK 11052140 | {B6A93F55-534E-4C9A-8EB8-6367DF5FB505}
BRUNSWICK 11052140 | {64937DAF-546B-4775-B18A-D5EDC1A6AA5C}
BRUNSWICK 11052204 | {EDC3C6AA-B200-49D0-AFDA-73B9844EB8E4}
BRUNSWICK 11052210 | {061B0891-9632-4691-9CF7-EFB012B2AC41}
BRUNSWICK 1105271012 | {D095B28C-4EC2-41A1-AFB1-E86B21ED4434}
BRUNSWICK 1105272286 | {8A44AA74-ACDA-4D97-B1DB-12F78C555BFA}
BRUNSWICK 1105297538 | {CDF4D9B0-F952-4777-9AE7-DE3DFB888FF5}
BRUNSWICK 110532536 | {547CB5AE-3FC8-46F0-9836-780E7F4C0AE3}
BRUNSWICK 1105452800 | {628DA938-A810-4C8C-8B30-4F78074FCDBC}
BRUNSWICK 110584480 | {BE84EF6E-6642-4AA6-9D64-6402D1C22F4F}
BRUNSWICK 1105875388 | {EFB7F521-2C9B-4778-952B-B2078E131A97}
BRUNSWICK 1105963830 | {291237EB-DE0C-4195-81B9-D045DCC5ABD7}
BRUNSWICK 1105CB | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
BRUNSWICK 1106114670 | {79D77B1C-2CE6-4D9C-82D3-8EC01871EFD8}
BRUNSWICK 11062104 | {BDBA1A41-9235-4F2C-87B2-104E0BB64232}
BRUNSWICK 11062392 | {F0B6C592-2F67-4F88-A13D-794768FAAAF8}
BRUNSWICK 11062416 | {EDF4431E-F5AF-4806-91E5-400DCB7DFCFA}
BRUNSWICK 11062790 | {C10441DE-4140-4067-AC0A-82D10F063DBA}
BRUNSWICK 11062796 | {EF5B06D7-E629-41B9-B306-6C2CC9919130}
BRUNSWICK 110651484 | {EFD00C80-B08F-4DD1-B4BC-20FE90F89DC3}
BRUNSWICK 110651484 | {F211ADF4-31F0-466B-8F59-DF90345ABDCC}
BRUNSWICK 110651486 | {20D517CB-EFEF-4E5D-A065-4994CEAE6929}
BRUNSWICK 110663124 | {C847E025-6E0A-40C2-B74F-54E4CBC5EB88}
BRUNSWICK 1106657600 | {DC0239AF-D0E3-47FA-B41B-85E9605567D4}
BRUNSWICK 1106CB | {05FDE184-0042-4792-8C58-B7C18CC19C9C}
BRUNSWICK 1107357568 | {D067704F-EA17-4E88-B020-8A7104433E44}
BRUNSWICK 110750008 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
BRUNSWICK 110750010 | {5FEB44CD-F1A7-4044-A3E4-77CA9BA8E902}
BRUNSWICK 110756240 | {0B71C1B2-A29B-4BB9-A4C4-B904DD28EC13}
BRUNSWICK 110765574 | {7CD5E23A-1FEF-4DD4-B696-6D5E8A5A222C}
BRUNSWICK 110767218 | {01EA3047-6C3D-48CC-8F03-375E6D507A0F}
BRUNSWICK 1107969778 | {0FA0D6AA-C395-48A8-ADF0-FA394B369CF5}
BRUNSWICK 1107CB | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
BRUNSWICK 11102664 | {52CBF115-6640-4F98-9743-613A61123F02}
BRUNSWICK 1110528196 | {91E6440A-FA7C-462D-9F90-13D6AE94C094}
BRUNSWICK 111061602 | {A298B0D8-C9B9-4411-92EE-D00915B8BD24}
BRUNSWICK 111063100 | {F62664EC-2775-4F42-885E-6C5354881CBF}
BRUNSWICK 1110832231 | {4FDE05D2-6E18-49FB-9864-F184CF9B6861}
BRUNSWICK 111094368 | {BCC579AC-C459-46FE-9298-10C2B7376879}
BRUNSWICK 111095576 | {21D4FC8E-0338-4F5F-A1A4-BA17C75094F0}
BRUNSWICK 1110CB | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
BUCKS CREEK 1102CB | {777DE2C4-ED25-41C9-82DD-E42386BC34EE}
BUCKS CREEK 1103338520 | {788A24F0-B95A-4429-91A6-A78EF0DB40D4}
BUCKS CREEK 1103CB | {2C93052B-CAB6-4039-91C2-ECB9C837F00A}
BUELLTON 1101CB | {3DA79F67-E6AE-44CC-8D0A-A38C65F29240}
BUELLTON 1101Y06 | {B215B9B7-F7F3-4553-8BC7-ED531B03358B}
BUELLTON 1101Y26 | {4514D6A6-77B8-4164-AACC-ADDF4E8C95FD}
BUELLTON 1101Y34 | {9919F67F-7D4E-4CC7-938A-6CB755805F83}
BUELLTON 1101Y36 | {9CBEE47E-1598-4921-97C7-5CC747F89863}
BUELLTON 1102CB | {2D7A19FE-1388-4016-A42B-7364F42C4D40}
BUELLTON 1102Y20 | {2A274649-29BE-484B-9512-4089BA59299F}
BUELLTON 1102Y50 | {BE22BF5B-77AE-4173-893E-2D7D15CAA658}
BURLINGAME 04049066 | {585506C1-ED3B-4FB3-84DA-FABB2641F074}
BURLINGAME 0404CB | {585506C1-ED3B-4FB3-84DA-FABB2641F074}
BURNEY 11011322 | {A45048C4-5E06-4803-9C40-C46808E3753F}
BURNEY 11011340 | {9FEEDD46-3D3C-44E2-AC09-40EF72D10F0B}
BURNEY 11011358 | {2A928B3F-2AFB-4E95-9D5F-1D4611A31405}
BURNEY 11012402 | {2E555E2F-D45B-427A-941D-A906BDE558FE}
BURNEY 110145984 | {1877F2B7-68C6-4031-8C15-9D4F18F07556}
BURNEY 1101519432 | {343AC60B-63D0-4E19-ACE7-2943E5C1D0F7}
BURNEY 11019042 | {76D3EBDD-5C29-47DF-9912-445D8BE3DBA6}
BURNEY 1101CB | {DD5BA261-28C3-4395-8BF5-3D293075C1EE}
BURNEY 110237284 | {B2408DFF-DEFE-41B8-ADEE-8F62D90930D1}
BURNEY 110257046 | {2AA24801-8300-4851-B080-261023387F10}
BURNEY 110297318 | {C4DDB13D-8C8F-4D3D-860D-833D982C6826}
BURNEY 1102CB | {36A5A14C-2F20-494D-A5FC-CDF9488C4EA1}
BURNS 210110912 | {62DB6A1E-C643-412E-AD78-478695BE02E4}
BURNS 210136516 | {6763B940-A4FC-4294-830C-EA07CE726C5F}
BURNS 210139126 | {1E00CF74-EEE2-4457-A6AF-F5C49F5CE48D}
BURNS 210190678 | {153A6026-D323-4954-B25F-4B63C2678A6D}
BURNS 210191034 | {B62417A2-05A9-4D8F-8000-7D56F072966D}
BURNS 2101BL 2101 | {096C1652-B7E1-4420-B7F5-3A29C5C5F06A}
BURNS 2101CB | {77124F72-2A10-485B-AF25-5FB9845AECBA}
BUTTE 11032104 | {FB7A2293-9439-48C4-B179-5F6C84D82D44}
BUTTE 11032208 | {F6CF6B5A-1E51-4A8D-BE96-2DD1B8FF14FE}
BUTTE 11032422 | {F6CF6B5A-1E51-4A8D-BE96-2DD1B8FF14FE}
BUTTE 1105134600 | {5CCEBBD0-8D8E-4DD0-87AF-C021A43051F6}
BUTTE 11052224 | {99D60B56-5961-4789-A3E0-D520C3413381}
BUTTE 1105235788 | {E9B89DB3-0831-46EE-9118-671FF72DAA2A}
BUTTE 11052576 | {9A0BA931-124F-4B29-B938-98D870112FD7}
BUTTE 1105518014 | {EA7C07F2-4273-40BB-B6F5-36B0C70D1D31}
BUTTE 1105612016 | {B2540AD5-03FB-488F-9579-CE16933A52B5}
BUTTE 1105CB | {99D60B56-5961-4789-A3E0-D520C3413381}
CABRILLO 11031437 | {02264660-E3C6-4806-AC6E-28401EBDA58A}
CABRILLO 1103CB | {F3B21B24-5FCC-4918-B9AB-A8B8CD51F711}
CABRILLO 1103Y10 | {133D318F-822E-44D3-9638-08188E1B8D58}
CABRILLO 1103Y12 | {723FB00A-7C12-42CB-85FE-70F2D7BE445E}
CABRILLO 1103Y46 | {02264660-E3C6-4806-AC6E-28401EBDA58A}
CABRILLO 1104431976 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
CABRILLO 1104497036 | {27DCEC24-FA17-48AC-A20B-BD915C784084}
CABRILLO 1104597930 | {DB4CB1A3-78E1-4EA1-92B3-6161B305FA89}
CABRILLO 1104765792 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
CABRILLO 1104838078 | {27DCEC24-FA17-48AC-A20B-BD915C784084}
CABRILLO 1104Y08 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
CABRILLO 1104Y24 | {A2EAD6B1-6208-4216-A913-DC206F2BE25D}
CAL WATER 1102329532 | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
CAL WATER 11023428 | {66B5382A-A6B4-4150-9067-49730EEFBF01}
CAL WATER 11023802 | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
CAL WATER 1102690954 | {F35BC96C-F1E1-4513-95B9-90DB5E55FEE2}
CAL WATER 1102920714 | {75FA50A9-2878-4633-B714-48E51CCA6E1E}
CAL WATER 1102CB | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
CALAVERAS CEMENT 110111188 | {B3717E2C-44BF-4A63-A354-45BBFC0B5253}
CALAVERAS CEMENT 110111236 | {765E2074-110B-4FD6-8019-AD09D7431DAB}
CALAVERAS CEMENT 110113424 | {B1720971-4842-488B-929E-F65E96985B19}
CALAVERAS CEMENT 11011419 | {31F34B0C-04AD-46C5-88A1-857D16F62C5A}
CALAVERAS CEMENT 1101191544 | {207C6256-DB81-41B8-B8E9-FF1EC6E289A9}
CALAVERAS CEMENT 11012646 | {3FB47D58-B406-4320-8238-19B8B73E9349}
CALAVERAS CEMENT 110136880 | {2CE7DA92-EEC1-4680-BEC4-A1E05BA2B50C}
CALAVERAS CEMENT 11014786 | {CF62E6C3-07CA-4DD5-8099-332BF3F2B85C}
CALAVERAS CEMENT 110147968 | {AFAF5A37-E0AD-4142-ABDE-E616F0022060}
CALAVERAS CEMENT 1101502 | {1D87D320-3344-47D1-AB52-86F36B13B2E4}
CALAVERAS CEMENT 1101544800 | {B4FC0E10-1DBC-4446-A2DE-836BB2DB31D0}
CALAVERAS CEMENT 1101585 | {765E2074-110B-4FD6-8019-AD09D7431DAB}
CALAVERAS CEMENT 110180930 | {31F34B0C-04AD-46C5-88A1-857D16F62C5A}
CALAVERAS CEMENT 1101CB | {16B948B9-B372-45A4-B29D-56B8F2A70B74}
CALISTOGA 1101122350 | {EF1FA2C3-57EE-4BD3-91A2-9186818DE5AD}
CALISTOGA 1101134232 | {C06D7D77-648B-4C10-B65E-6012FCEC9841}
CALISTOGA 1101134232 | {E817A6B1-B5A9-480F-BE4E-060F6D3D012F}
CALISTOGA 1101157668 | {6BBCCA3D-69FC-4060-8327-3D48C3973D5D}
CALISTOGA 1101217982 | {CD3F0C5B-3CFB-463F-84A3-D2D5913DA9C2}
CALISTOGA 1101242919 | {A2E97EA6-1CE8-40C8-917B-02BFB4DB75BC}
CALISTOGA 1101257964 | {0D63E34E-7108-465F-BC13-5DF2F623AD72}
CALISTOGA 1101267806 | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
CALISTOGA 110135588 | {027DEE93-00CD-47B3-9E09-CCA2A54DDEE2}
CALISTOGA 110143924 | {452F0E63-4DD0-460D-9F3F-8DAD64266857}
CALISTOGA 1101537148 | {950B7723-A5B4-41CD-A0A5-13F29B883B0B}
CALISTOGA 11015934 | {39A37840-00F8-46CB-8218-BB0855552677}
CALISTOGA 1101727772 | {15B270FB-A708-4F25-A097-2249C81A7EB5}
CALISTOGA 1101730666 | {FA49F960-6509-4068-B228-484102BD4152}
CALISTOGA 110178734 | {6508E901-1F5A-48C3-8B34-5971800F66D8}
CALISTOGA 1101843761 | {0B54DF53-2082-4B6F-9020-553C5C7EBC03}
CALISTOGA 1101881110 | {0E3098B8-1D79-4775-90EE-1CA04AC01E07}
CALISTOGA 1101886282 | {22798A75-B031-4EAD-AEE6-E26CAD1C77A1}
CALISTOGA 1101890 | {37250BD0-D9D0-484F-9AA1-8C286761C77F}
CALISTOGA 1101894 | {D294E12F-4C7C-4C89-818B-50A112502FCB}
CALISTOGA 1101894220 | {7EC3F9B5-28CF-42D9-B7F8-DA19D0A08EE2}
CALISTOGA 1101959538 | {592CEFBC-9961-4F1D-B002-F87443B77673}
CALISTOGA 1101CB | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
CALISTOGA 1102131531 | {9728A510-4796-446C-AFFA-E71EAF88F06E}
CALISTOGA 1102141073 | {418B82F8-6C32-40A7-BAFC-4E4E4E20312E}
CALISTOGA 1102177784 | {854EA7F2-5906-4478-AEB7-CF15AD49AC3F}
CALISTOGA 1102270153 | {5E03CEC5-E2EB-42D8-9EED-F70D1DF93EB6}
CALISTOGA 1102279135 | {0AB6C849-088B-4982-95AE-9F5B40F2ED13}
CALISTOGA 1102447865 | {256C107E-DF69-4B49-8315-E416EEEC567C}
CALISTOGA 1102634 | {71406629-30F8-4B6B-8A17-26183BADDC66}
CALISTOGA 1102634 | {1FCE58DF-672D-489A-B6FD-E3E4E442C0A2}
CALISTOGA 1102640833 | {8A508CC4-F811-46AA-A430-C9F69A63B403}
CALISTOGA 110266730 | {2FC93923-0AF8-4A4D-9F96-EF0ED8AF2245}
CALISTOGA 1102706 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
CALISTOGA 1102714556 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
CALISTOGA 1102769230 | {2E19A9CF-57F8-4CF7-B698-92E35CE7A12C}
CALISTOGA 1102892348 | {5967EFD1-F9A6-454F-AA55-1486E49A0BFC}
CALISTOGA 1102929461 | {54FC9C79-A744-48AC-829D-6AD9866F8972}
CALISTOGA 1102960240 | {41CC5656-0DD4-454D-8539-FF84073137C6}
CALISTOGA 1102963232 | {F6B6C2A6-F266-4776-97CA-32630CA07BDE}
CALISTOGA 1102CB | {B6480B23-3B7E-4A3F-9C7B-82F910A25330}
CALPELLA 1101345230 | {CE47E68B-6431-42EF-95CF-00E7CF465463}
CALPELLA 1101372366 | {94071028-8C5B-457B-A3F8-E4BBBDF8AD63}
CALPELLA 1101542 | {C7347FC3-B613-4AAE-82AC-3F7111D01C04}
CALPELLA 1101619542 | {979C5268-1F54-4BBC-B316-05EF7B718423}
CALPELLA 1101753000 | {E12D2ABA-05E0-44D9-A574-E03478B74646}
CALPELLA 1101908688 | {12A38B89-AFC7-458E-AF14-8B6F24C74831}
CALPELLA 1101931142 | {634C24C9-E71D-4215-AF41-8A5F9990674C}
CALPELLA 1101CB | {C851DF07-17A8-4945-A053-68AC77422563}
CALPELLA 1102421412 | {3A9F2D9A-7433-47D8-8578-46D205BA61B6}
CALPELLA 1102CB | {2993BF9E-90A5-4634-AB04-8D39B8C96792}
CALPELLA 1102CB | {E4FB8FF1-A25E-4BCC-BD7D-820FE1EF6169}
CAMBRIA 1101175422 | {90731576-6ADC-4169-86FA-CAE47F468CEA}
CAMBRIA 1101858200 | {1CB4B3DE-6FA2-40BE-AA6D-BEA2EDAB4893}
CAMBRIA 1101CB | {5CB94E28-BCD0-4946-A0EA-D8080443F8CB}
CAMBRIA 1102CB | {A36DF7B8-003C-42F6-A33B-327B9F3DECA5}
CAMBRIA 1102W50 | {98891E8E-A196-4377-815F-B850671211F6}
CAMP EVERS 210310946 | {A1366627-BA9B-4DAB-8067-98E47F041CB9}
CAMP EVERS 210311046 | {DC46DF0C-E79C-47C3-8E88-AF56F3C9F267}
CAMP EVERS 210311056 | {C4E0B9E0-CB11-4C51-9BF2-0A1F8C067741}
CAMP EVERS 210312990 | {EA67021F-EC51-4B91-B55C-AC9EF715A21B}
CAMP EVERS 2103449218 | {AD962272-DFC9-4006-90BE-E42CBF343716}
CAMP EVERS 21035402 | {CEB97A6E-057E-4617-8BF5-91D85F0FC1F8}
CAMP EVERS 21035404 | {08861202-71CD-43A7-A4E9-A7647717C791}
CAMP EVERS 210355638 | {4C9A65DC-55B1-4CE2-AD64-FA340511DC8F}
CAMP EVERS 210392582 | {FE8FB0E1-1FAA-49D9-87B9-90771C18AB33}
CAMP EVERS 2103CB | {22D220C5-2768-4212-BADC-DEEFF16BE912}
CAMP EVERS 210410442 | {51C72ADA-5E33-425F-A574-21BEA172A863}
CAMP EVERS 210411048 | {3BCDAF7C-1C90-48AD-8ECA-3702D1B4C97A}
CAMP EVERS 2104189010 | {CE6EDBCF-B1D7-4C02-8D27-0FDA223000E1}
CAMP EVERS 2104CB | {84EE2558-0006-42C6-8836-08F2D7F2DAA3}
CAMP EVERS 2104CB | {D8B5F10C-1F36-4DDF-ADD9-C8CA172CCAC3}
CAMP EVERS 210510214 | {F835FBEC-BE60-4F27-B7FA-FBF03B1492E9}
CAMP EVERS 210510294 | {9A213A9A-1023-49F7-ABDF-C909666FFA23}
CAMP EVERS 210510728 | {61BEE218-5ECD-4073-AA08-F1DB60558A8D}
CAMP EVERS 210510996 | {9C524D92-A5C3-4391-A08F-2E5640BEA3EC}
CAMP EVERS 210511004 | {91583C6E-961C-4B38-9535-F88F266F69EA}
CAMP EVERS 210511384 | {8B06F25F-237B-4FE8-8F99-17C1FF96A7BD}
CAMP EVERS 210512590 | {9C7B2B92-FC22-48B4-B1A3-9DC57E45ACA3}
CAMP EVERS 210533542 | {AA5C701E-0F96-4151-A44F-2E6809287FB2}
CAMP EVERS 2105370732 | {F3D8BF5C-D197-44D8-98A9-531A4D374A53}
CAMP EVERS 2105426822 | {B7A521A6-441C-41FF-9BF3-E1AC07BB086B}
CAMP EVERS 21055146 | {592F5AE1-0E6F-42C9-A6FF-0D40652C51A7}
CAMP EVERS 21055188 | {8C44BEAB-509E-4818-A7FB-FBD552205E02}
CAMP EVERS 21055232 | {7121682A-B3AC-4974-A685-FFAEF4CE6C69}
CAMP EVERS 2105534190 | {AA599654-FFB2-4492-998F-E0F44B671B73}
CAMP EVERS 2105601610 | {C60D85EC-3384-4B7F-924F-0F013DD5EB4A}
CAMP EVERS 210584166 | {C18F23CB-C77B-45AF-AE28-F27A00E5C8FB}
CAMP EVERS 2105922576 | {113167BA-CCDF-4634-B6F8-AB10EDD459D5}
CAMP EVERS 210595050 | {CA99B367-8DC7-4E82-BCC3-DFC89B2C9160}
CAMP EVERS 2105CB | {EE077F7F-8175-4265-8512-03731CF3E11C}
CAMP EVERS 210611006 | {386E8549-812B-4BD5-AF30-4B8F8F3211D4}
CAMP EVERS 210611044 | {90D97D29-641D-4D44-ABC6-DEB499FDF2DF}
CAMP EVERS 210612518 | {8A35F12A-0761-4DDF-88CA-C8A70AB35338}
CAMP EVERS 210612760 | {77218484-2483-4A3A-8ACC-0336A0ABECA8}
CAMP EVERS 210612840 | {F761DD80-845B-4F29-ADA0-4CE9C4A1F615}
CAMP EVERS 2106130936 | {B2374312-6A96-4C62-9249-47729A4C1D06}
CAMP EVERS 210616000 | {1BABBDF2-DCB6-4552-BE33-67EDAC391159}
CAMP EVERS 2106255706 | {B9907868-2016-4A65-8566-DE5DBA7654A2}
CAMP EVERS 2106257600 | {A9948C64-0DE8-41DB-BAB3-440E2282849B}
CAMP EVERS 2106287578 | {8E63B9EB-959B-406C-95DE-C4CA49EAA042}
CAMP EVERS 210637210 | {4EC0C5CA-D3E9-47E9-809A-55A51CA9C021}
CAMP EVERS 210637210 | {968E49EC-DA99-4694-8469-77DF22F8452B}
CAMP EVERS 2106478670 | {2A12FE05-29C7-4A7E-ADD1-ADDA9E49ED27}
CAMP EVERS 2106478670 | {F294860C-7C31-40F4-A41B-D8135E8E175E}
CAMP EVERS 21065020 | {D340DCCD-95D6-4317-9003-DD8DEDE9B1C0}
CAMP EVERS 21065300 | {30210CF9-C9B7-4E0D-B350-23AD99A7DA9C}
CAMP EVERS 210660120 | {CCDF3A25-AE56-4EB7-B245-ECC2A1643713}
CAMP EVERS 210660124 | {DA7C8872-7711-476B-9F5C-23C6F7D102DC}
CAMP EVERS 2106737512 | {38594324-B008-4F93-A718-0D73EA72DED9}
CAMP EVERS 21067603 | {4EC0C5CA-D3E9-47E9-809A-55A51CA9C021}
CAMP EVERS 210694770 | {58DC126F-C9E2-47DB-AFA1-8FE0FF5A0DFD}
CAMP EVERS 2106CB | {F50933AC-5B82-417B-BA6F-799563320ECE}
CAMPHORA 110122412 | {3C98E34E-9E87-4EA2-902E-6CB817DB7650}
CAMPHORA 1101613562 | {C4E21E20-1077-4DDF-9A14-C3E5D8A4A595}
CAMPHORA 110177978 | {31472151-05E0-42A0-B884-E32FC8EACB46}
CANTUA 11019880 | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
CANTUA 11019890 | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
CANTUA 1101CB | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
CANTUA 11029310 | {47A2D34B-B373-4F5E-9E14-A9EF32FD99D4}
CANTUA 1102CB | {593FAF9F-F993-4666-8339-2025B1146F35}
CANTUA 11039900 | {ADBA8581-1EDE-4FED-96B1-1470CDDF965C}
CARBONA 110114204 | {03E03B20-8D28-451C-9701-95F4851E85CE}
CARBONA 110145186 | {D5A2A0ED-5854-48FF-9353-DEF3C343CB3C}
CARBONA 1101975330 | {33A7055F-6DBB-40BD-9D42-63496DE4F455}
CARBONA 1101CB | {03E03B20-8D28-451C-9701-95F4851E85CE}
CARLOTTA 112142896 | {98A83A4A-2877-4301-8F63-D1E33C62F68A}
CARLOTTA 112144150 | {47D7E27E-F1F2-4AFA-B2C6-25B11F5B475A}
CARLOTTA 11214914 | {A5C24938-2037-405D-99A3-0ABBFC2B130E}
CARLOTTA 1121686774 | {B05654BB-E8D8-4BA7-B923-D4499F5C765C}
CARLOTTA 1121CB | {3CA4A42E-51F1-49B1-95E4-11CB39229D26}
CARNERAS 1103430670 | {4F63DE1D-7CBF-4AAC-B035-BBB7D4E5B891}
CAROLANDS 04018506 | {41914C65-46E2-4B82-9AFC-5A738FB74209}
CAROLANDS 04018886 | {029D0D55-2BAE-4088-B646-F2DDA198BF80}
CAROLANDS 04018888 | {8A7276CB-0C27-49CE-BD2E-58CE1319B4D3}
CAROLANDS 040197209 | {542C89B5-8855-4F9C-96E0-4B73D5C44BAD}
CAROLANDS 0401CB | {AFAFA564-C801-46B9-B877-3979D8BE4904}
CAROLANDS 0402CB | {6CB7829C-D7F4-4692-906A-EB06183783C1}
CAROLANDS 0403CB | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
CAROLANDS 040484797 | {D7BC6FC3-0984-4223-925A-00CF07B371A2}
CAROLANDS 04049024 | {ADC13D99-F0AF-402E-9F6C-0B91201427B3}
CAROLANDS 04049026 | {EE04BD96-5787-4D66-B00B-BC1201689111}
CAROLANDS 0404CB | {F73FE32B-0064-4963-BD0F-96E252B7B701}
CARRIZO PLAINS 11013527 | {DF118858-83A9-4B97-BE1A-B9801D7678FF}
CARRIZO PLAINS 1101384116 | {6983F117-CF1B-49D2-BCC1-D1CF76202FAE}
CARRIZO PLAINS 1101384116 | {DF118858-83A9-4B97-BE1A-B9801D7678FF}
CARRIZO PLAINS 1101711854 | {412EB69B-2273-4C1E-A820-027827AE03FC}
CASTRO VALLEY 1102837904 | {D1EA05C6-0F55-455A-AD0C-597319479076}
CASTRO VALLEY 1102840916 | {B3742266-0A6B-41B7-BDF6-4E4FF8E74B2F}
CASTRO VALLEY 1102960346 | {2E3992ED-F001-40B5-B77A-1BD22BF80B0A}
CASTRO VALLEY 1102CB | {4C70CAF0-3BFD-4092-B38C-A567700FFBF5}
CASTRO VALLEY 1102MR204 | {B72D11A7-A3E3-4487-9B62-E0B9199739E9}
CASTRO VALLEY 1102MR248 | {30E66223-084D-4B40-9C14-1E91EC3B3A23}
CASTRO VALLEY 1102MR359 | {F23FD02C-15E0-46F5-9C74-B690AB0C4482}
CASTRO VALLEY 1102MR518 | {BF555005-32AC-49E5-8E9E-ED1476EE192C}
CASTRO VALLEY 1105132304 | {DF750B9C-4007-427B-BA49-F0504B484D45}
CASTRO VALLEY 11057406 | {8FB1C60E-7F21-427D-AC07-FBC0BD1C61E8}
CASTRO VALLEY 1105805238 | {9FA4DC7A-6448-41DD-AE90-39B3A5BE7830}
CASTRO VALLEY 1105853216 | {D3473D96-EE5A-4DC3-BCCA-A509A72B1AB7}
CASTRO VALLEY 1105MR201 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
CASTRO VALLEY 1105MR215 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
CASTRO VALLEY 1105MR236 | {C255CD66-4CFB-4E6F-AE78-6A76CA6EB0AA}
CASTRO VALLEY 1105MR579 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
CASTRO VALLEY 1105MR585 | {8FB1C60E-7F21-427D-AC07-FBC0BD1C61E8}
CASTRO VALLEY 1107MR235 | {35AEE05C-849F-43E6-A066-12B4CE5002B2}
CASTRO VALLEY 1107MR336 | {AD5F876C-C0A5-47C7-B722-6D39867E5D84}
CASTRO VALLEY 1107MR586 | {6E95A290-884A-4661-ABDD-3867B3A651A0}
CASTRO VALLEY 1107MR587 | {F17715EC-9622-4357-8B6D-1CE6C6C47591}
CASTRO VALLEY 1108343456 | {FC94D279-1737-41C3-B252-F362937CE45D}
CASTRO VALLEY 11088971 | {D8E4C9CA-7EEB-49BA-880B-C873380BC8EB}
CASTRO VALLEY 1108MR205 | {E6DE5FA6-EF94-448F-BB17-EE24C05283D8}
CASTRO VALLEY 1108MR233 | {D8E4C9CA-7EEB-49BA-880B-C873380BC8EB}
CASTRO VALLEY 1108MR337 | {750917F9-85DB-4340-A453-D5DEEA818A9B}
CASTRO VALLEY 1108MR578 | {DE9C2D91-5A65-4F2B-B56E-B99E45AB3C86}
CASTRO VALLEY 1108MR580 | {750917F9-85DB-4340-A453-D5DEEA818A9B}
CASTRO VALLEY 111010315 | {4396A44C-BE29-48A2-B592-2211E388C99B}
CASTRO VALLEY 1110264914 | {0238934D-AD84-4436-8033-E87CEB6334C8}
CASTRO VALLEY 1110560528 | {A99DCE6F-B545-4120-B017-A9E82834DFD0}
CASTRO VALLEY 1110610800 | {217855BB-2EFA-4F5A-897E-1A1792604994}
CASTRO VALLEY 1110CB | {FFE0EC6C-F31E-4ACF-B207-C8795D8C3898}
CASTRO VALLEY 1110MR243 | {58409F43-908C-4F7B-B13E-65AE96367D27}
CASTRO VALLEY 1110MR273 | {C6807FEA-40B3-41BE-80F1-095A0F67FBA5}
CASTRO VALLEY 1110MR379 | {8CF3EAE2-3D5E-46D8-99A9-0040E44D6238}
CASTRO VALLEY 1110MR525 | {DDE57A1E-80D5-431E-961E-F1D86837BDD0}
CASTRO VALLEY 1110MR748 | {4396A44C-BE29-48A2-B592-2211E388C99B}
CASTRO VALLEY 1111227862 | {24288AD2-A665-4D6B-A149-2AC7913C77E7}
CASTRO VALLEY 1111CB | {75D298E6-3FF1-47B6-9B91-A2291860E391}
CASTRO VALLEY 1111MR334 | {144B3CD2-37D4-4FA9-8973-1F3A9C9CD174}
CASTROVILLE 210436922 | {5DE92B6D-4604-444B-8D65-AB7A469C1FE2}
CAYETANO 2109884904 | {FCFE254C-7C9E-488B-BFF8-A6B5C0DABDF8}
CAYETANO 2109884904 | {4B1B4811-B2BF-45DA-954C-55F605B422B6}
CAYETANO 2109884904 | {D6285326-2FFA-4A2D-BFE1-B6ED404A2994}
CAYETANO 2109CB | {6B3AA927-69EC-4F4F-A5CE-660E716543CD}
CAYETANO 2109CB | {CB1F79C6-162B-44E7-BDF1-619119F35335}
CAYETANO 2109MR186 | {96E83343-B1D6-4373-84A9-0E60E5A945BA}
CAYETANO 2109MR198 | {DE685544-4F9C-41AF-85C6-DB5D3F282705}
CAYETANO 2109MR572 | {12F27C0D-5A90-400E-AE30-47886559E780}
CAYETANO 2109MR572 | {DE968837-AFA5-4F15-89D0-BA934A29FE50}
CAYETANO 2111CB | {C40E7CD7-2111-4F6E-9C4C-C85455B7EAD0}
CAYETANO 2111CB | {439ED568-0BDE-4626-B59A-7C48F17E3B78}
CAYETANO 2111CB | {0098F2B1-286E-480D-B861-BA704D93D774}
CAYETANO 2111MR329 | {439ED568-0BDE-4626-B59A-7C48F17E3B78}
CAYETANO 2111MR444 | {9023C050-E4CF-4D3E-B644-63B7AF1F7B04}
CAYUCOS 11014701 | {5CFEA468-EAFA-49AC-B046-6E19D81021D8}
CAYUCOS 1101CB | {E8519C3F-CC2F-4A8E-BB1B-BC611BF917C3}
CAYUCOS 1101W14 | {978A144F-73B7-480C-94FC-939745BD7BEE}
CAYUCOS 1101W58 | {5CFEA468-EAFA-49AC-B046-6E19D81021D8}
CAYUCOS 1102317156 | {BC053071-09B8-414B-AB18-6F0D45277D55}
CAYUCOS 1102613456 | {6A688077-C692-4875-BCC4-AA060549E3B3}
CAYUCOS 1102CB | {80B87962-AD85-4936-A71D-968069A54623}
CAYUCOS 1102W16 | {27A305FA-41EE-4706-9CA1-3C6F18524B78}
CAYUCOS 1102W18 | {3F253D0A-A8E6-4C2E-92EB-89E0F265E7C4}
CEDAR CREEK 11011656 | {383E38F1-9CAC-409E-B20B-DAC5E1331447}
CEDAR CREEK 11011664 | {81F58F11-9F6E-4CC2-A527-0CBBB670DE91}
CEDAR CREEK 1101451856 | {1E7F5746-1B26-4A75-989E-3A819FF5E822}
CEDAR CREEK 1101CB | {4A950894-EB8D-4B95-B3B2-200DB270C21B}
CEDAR CREEK 1101CB | {578FE3D8-350C-4FA5-8070-C7453CE4838E}
CHALLENGE 11015460 | {B23B77B2-F3D5-42C7-AB2B-D58C03818E3A}
CHALLENGE 11015460 | {CC6E361B-CB3E-4B40-BF58-ADB4E431D8DD}
CHALLENGE 11015460 | {F0D31826-5D50-4D47-B81B-BCAAA769528E}
CHALLENGE 1101CB | {6A653745-C5CA-4E78-9C62-82F0E53CCD59}
CHALLENGE 11021064 | {B35DE979-0877-4DCD-A99D-B482E8F19A15}
CHALLENGE 11021902 | {1446E22C-05D8-4F82-9637-10F46D2B1E35}
CHALLENGE 11025462 | {9343C558-C255-4E56-87AF-7724333414B9}
CHALLENGE 1102CB | {C71A58EE-DA31-4CE3-8F9B-4D615671BE3A}
CHESTER 1101CB | {F5B87947-B1CF-4B32-AB2B-95DA61D92836}
CHESTER 11022564 | {C8BA9CFD-3C7E-444F-AD17-DFDE1ACC00EB}
CHESTER 11022614 | {C8BA9CFD-3C7E-444F-AD17-DFDE1ACC00EB}
CHESTER 1102CB | {655104DB-DE28-4723-9C66-99BF732C7F54}
CHOLAME 11015939 | {47231439-CE13-4A31-BF86-1A2379821F62}
CHOLAME 1101CB | {35294033-F688-4422-9C73-F70641476C8E}
CHOLAME 1101R22 | {7FDC77D6-0D2A-45F5-A1E8-7D8DC458C0F0}
CHOLAME 1101R96 | {0F26305A-B95B-48BC-93DA-531056D0E973}
CHOLAME 1101X12 | {B37DAD9A-6324-4833-89D5-DCF19FFFD67A}
CHOLAME 1101X14 | {47231439-CE13-4A31-BF86-1A2379821F62}
CHOLAME 210210264 | {DCDC17BE-E1B5-4238-9F74-2FA47A2B0257}
CHOLAME 2102127926 | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
CHOLAME 210249414 | {946E7382-BCE9-4876-B322-206F92E831CA}
CHOLAME 21025597 | {C3648DC1-A8A4-411C-BC09-DF15A6A8CCC0}
CHOLAME 2102796386 | {C3648DC1-A8A4-411C-BC09-DF15A6A8CCC0}
CHOLAME 2102867686 | {97118B4A-2A8C-456A-94EA-FB99937C6D68}
CHOLAME 2102CB | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
CHOLAME 2102X06 | {2CD93861-C1D5-4471-A09B-75955F723957}
CHOLAME 2102X08 | {7DB68BFD-2EE5-4737-904D-3F4AB911B6ED}
CHOLAME 2102X10 | {DC85B463-1C28-4036-85F0-A9C121ABE158}
CHOLAME 2102X16 | {90DAAFCD-8A40-42C4-A489-C7D86439D101}
CHOLAME 2102X18 | {D9DC2012-D30B-464F-B310-3196684B5ECE}
CHOLAME 2102X20 | {3EDA206D-0CFD-4058-8D33-8D070063612D}
CHOLAME 2102X22 | {8576EB3F-3AE6-4C28-B63E-BF3A9FDC680A}
CLARK ROAD 1101CB | {F673F67C-7B92-4672-819A-41DD2FB01076}
CLARK ROAD 11022044 | {62022298-C96E-4026-AE43-0F12DB277F1C}
CLARK ROAD 11022068 | {31C399B4-B5E1-4797-80CF-566E803A98B5}
CLARK ROAD 11022070 | {DBD4B653-AFBF-40EB-8724-1790AF913C8C}
CLARK ROAD 1102212118 | {1264D9D2-8375-4858-AD32-A3365D0B100E}
CLARK ROAD 11022582 | {E681E40E-5ECE-4E9E-921D-C13E15C00CCA}
CLARK ROAD 1102272950 | {8416EEC9-E95D-4731-9C74-10E801D32C56}
CLARK ROAD 1102272950 | {242A0DDF-2969-4CDF-89E1-CB12AA379A9D}
CLARK ROAD 1102407706 | {2CB09E0C-64E6-4F21-99AA-BAB6BE3DC5D0}
CLARK ROAD 110247006 | {6FBCFF19-8461-4946-AD7D-C380516CF011}
CLARK ROAD 1102514690 | {680899C8-622A-4D07-B62D-BFF41E670A32}
CLARK ROAD 110281296 | {154C476C-5A31-47D9-B01B-5C020A5462D1}
CLARK ROAD 110290548 | {1DE99E4E-7765-44B0-9832-275F1EB7F7A4}
CLARK ROAD 110292622 | {4AC0D11C-BCBB-44BA-9487-96EC262DE746}
CLARK ROAD 110292622 | {381D7853-5A02-4486-A50E-C31E33DE4E4C}
CLARK ROAD 1102CB | {E6C812B7-52C7-47F0-B595-32AF66AB7A9D}
CLARKSVILLE 210319572 | {AE109701-21ED-44EA-AA47-DDDDD6EEFB68}
CLARKSVILLE 210351564 | {1D188BFE-6402-4FA3-8FCB-922AC5F45D03}
CLARKSVILLE 2103547420 | {9DEE0693-2AD3-4794-A608-F547DC530CB5}
CLARKSVILLE 2103593454 | {1F682AD1-C38A-4DAB-9AB0-5C203E1BC633}
CLARKSVILLE 21036842 | {74B1A787-27C8-4482-8395-8E75B6FF6455}
CLARKSVILLE 2103CB | {582D525E-AEFD-49AD-B483-1141532B60A7}
CLARKSVILLE 210413352 | {76CF34A1-3FD0-4E72-BAFC-6CFED61FA5FB}
CLARKSVILLE 210419632 | {E10F57CA-31E3-4642-897F-6FA410857C1A}
CLARKSVILLE 210419662 | {A9104265-B4F6-48EE-93C6-57B36F6C317A}
CLARKSVILLE 210419772 | {484A22B9-C40C-4E37-BA87-C46E298525CF}
CLARKSVILLE 2104432966 | {9975CD68-B64D-4E58-9676-D1AE007E2CB9}
CLARKSVILLE 2104CB | {52B8BBE5-F562-4FC9-B2FE-B4B9BC5E3665}
CLARKSVILLE 2104CB | {24BA7214-EA0E-4940-8D9A-B12BFFD010BB}
CLARKSVILLE 2104CB | {B8AE2828-B8F3-4AD5-B0DD-60A11E80CAD2}
CLARKSVILLE 2105385236 | {760BF466-E4DF-4A5C-B2C4-51F0ABE15277}
CLARKSVILLE 210551478 | {0F59AF2F-5869-40D3-A6B5-13E6D7B47101}
CLARKSVILLE 210575884 | {398A55C4-A233-41E8-986A-9CEE99885341}
CLARKSVILLE 2105CB | {9208AF25-E3F3-4F0D-8CE3-550040B29414}
CLARKSVILLE 210619642 | {6458AB58-DA5E-4D0A-95E1-69BD6C7E0EA2}
CLARKSVILLE 21066832 | {C549AB23-FF4D-4476-A6BB-298E3FC3CA01}
CLARKSVILLE 2106CB | {C9DBAC79-A55E-4BD0-B21C-240D7C28DE49}
CLARKSVILLE 210951742 | {678500B4-CC40-4993-94C8-A8D3584C2E9B}
CLARKSVILLE 210951744 | {D119674C-FF38-4F45-A342-82E8B18FF02E}
CLARKSVILLE 210951796 | {4682A97D-092B-40D3-AAD7-69641B1B3CC1}
CLARKSVILLE 210955666 | {58AFEF14-24B5-49DA-AC14-3989473D0CBD}
CLARKSVILLE 21096502 | {E3844F20-2FE6-44AF-AD52-4D8F66E4C3E1}
CLARKSVILLE 21096502 | {B1661BB1-2298-4568-8F99-3AB48F48A478}
CLARKSVILLE 21096502 | {4E507525-2BE8-47B7-A931-7115823F0D5C}
CLARKSVILLE 21096502 | {365B71C9-0B41-480C-BFE9-EF8CE2AE1726}
CLARKSVILLE 21096502 | {A0936C28-A756-47FA-9C1E-76F4B7CFFF7E}
CLARKSVILLE 2109CB | {7686CD28-0AD3-49A6-802B-4CD3DF814107}
CLARKSVILLE 211011112 | {6508E8D3-0E1A-4D53-A06C-C666BBE3F64E}
CLARKSVILLE 211011142 | {3A0A47C5-9EE4-402A-889E-C298AEE1970F}
CLARKSVILLE 211019692 | {E7EDC231-ACD1-4AD9-A89B-5DAED0E6D6EA}
CLARKSVILLE 2110CB | {45555E2C-8D80-4EF7-9197-7511D877BC26}
CLAY 110113442 | {31882BA6-5D81-4512-9217-A61120B12235}
CLAY 110113450 | {27131A9E-D142-4A6D-93D0-301DB39F0FC8}
CLAY 110184572 | {537E07C0-FB8F-462B-87E9-2D8AA468190F}
CLAY 1101CB | {CC3A7F8F-5717-4639-B6A5-ECE8361467E4}
CLAY 11029999 | {D868AF66-93C2-4B3E-8187-2C428023C31E}
CLAY 1102CB | {D868AF66-93C2-4B3E-8187-2C428023C31E}
CLAY 1102CUST | {D868AF66-93C2-4B3E-8187-2C428023C31E}
CLAY 11031230 | {D62CDDF4-E093-4960-B995-54A7DAF191D3}
CLAY 110314674 | {6FB5453C-8E3A-4B58-AB8D-8BEBE74026D5}
CLAY 11031821 | {AE111B59-4073-4BA6-A6F7-C46E4FCA24F4}
CLAY 110334338 | {AE111B59-4073-4BA6-A6F7-C46E4FCA24F4}
CLAY 11035386 | {85E341A9-44AE-48B4-AEF5-91CF5EF041CB}
CLAY 110359714 | {CC378BAE-BD49-4ABE-8599-52019F7E517A}
CLAY 11037124 | {90124199-1243-4A62-BE12-797EFE6331CC}
CLAY 11037142 | {9E89ADDE-355B-4153-8A3A-140410223CE4}
CLAY 110398680 | {710E8DB6-BDC1-4CFF-BF25-79C21CA3FC16}
CLAY 1103CB | {12C9081C-95BF-4D8B-9422-8F9EBEEF2908}
CLAYTON 2211CB | {6C43A4A0-2BED-42F1-970F-3C9A6C36E609}
CLAYTON 2212158138 | {86E6EBE9-AB18-4CA9-B6B7-D151B1A6516B}
CLAYTON 2212204416 | {D1603D4D-EDBC-4667-A394-6A5E09388F26}
CLAYTON 2212334476 | {463B1668-4DE2-4C88-A747-EE241BC43F5E}
CLAYTON 2212523764 | {F3AF2874-1B26-4F8E-A2D1-24B02ACC6A03}
CLAYTON 2212614950 | {4884B072-CC16-4259-AE22-6A15B8CC59ED}
CLAYTON 2212681608 | {1FCED433-5B38-45B2-A635-D0F6F632FB56}
CLAYTON 221296224 | {3D0FC142-36D5-4662-84E1-74BFFF12E068}
CLAYTON 2212CB | {E96A0569-DCDE-4681-A6D1-E506A3CBE6D9}
CLAYTON 2212CB | {2D5D20E5-A0A7-4026-99AD-2AE1DA54D715}
CLAYTON 2213167700 | {C972F264-64D1-4FA4-8935-EB84A5191895}
CLAYTON 2213CB | {BE7BFFAE-6862-4503-AA75-EA4658F3F71F}
CLAYTON 221442582 | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLAYTON 221465785 | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLAYTON 2214CB | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLAYTON 2215184604 | {E913837A-6C3A-41F3-92AB-2B49EC8EE227}
CLAYTON 2215500240 | {6A2904BE-6CF6-42DD-B2C9-F94DF16B8A15}
CLAYTON 2215556215 | {D62CEB8E-E87D-4021-9028-58C41CA4CA60}
CLAYTON 2215812394 | {5C22565B-317C-4A78-8439-2CD9CE62BBBD}
CLAYTON 2215880066 | {7D32A00C-635A-44F6-950B-F3537B52DE0D}
CLAYTON 22159765 | {E913837A-6C3A-41F3-92AB-2B49EC8EE227}
CLAYTON 2215CB | {17D49159-2A99-4FB5-B2DC-0815D2D13280}
CLAYTON 2215W531R | {32128C45-30E5-4BD3-83C6-38B6DDD0B832}
CLAYTON 2215W573R | {C86C14F4-2F7A-4D9D-966F-4FE249C0F52F}
CLAYTON 2216C544R | {DB6FE7F1-AC75-4C7E-83AC-CE5B6DE225C5}
CLAYTON 2216CB | {DB6FE7F1-AC75-4C7E-83AC-CE5B6DE225C5}
CLAYTON 221714102 | {2E89F027-67FF-4082-9169-E158A83D0166}
CLAYTON 221738248 | {2E89F027-67FF-4082-9169-E158A83D0166}
CLAYTON 221798080 | {02D34549-5AC7-4AFF-A057-7824A31FF47B}
CLAYTON 2217C500R | {2E89F027-67FF-4082-9169-E158A83D0166}
CLAYTON 2217CB | {2E89F027-67FF-4082-9169-E158A83D0166}
CLEAR LAKE 11011302 | {4A405FCD-64B2-4AE1-B455-764875D385D0}
CLEAR LAKE 1101444 | {55694D06-24E9-4D6D-8BD5-E5D434DB5805}
CLEAR LAKE 110145252 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
CLEAR LAKE 1101486 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
CLEAR LAKE 1101529830 | {91E6CF65-65E6-49D9-99AE-7F739C671773}
CLEAR LAKE 1101699062 | {93794068-C446-4FF0-B0C2-C723FD11D3AC}
CLEAR LAKE 1101740076 | {AF3B7AFC-B2F6-4613-A8C9-551A8B6F40B8}
CLEAR LAKE 110181976 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
CLEAR LAKE 1101832686 | {4352C464-74E0-4EAA-9A4D-DC58892F06BA}
CLEAR LAKE 1101881362 | {22A23993-BAC9-4CAA-B619-505FC6C27874}
CLEAR LAKE 110192870 | {91E6CF65-65E6-49D9-99AE-7F739C671773}
CLEAR LAKE 1101CB | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
CLEAR LAKE 1101CB | {F863487A-BF6B-4D3E-93AD-9325B53F05BD}
CLEAR LAKE 1102223792 | {EE43D8DE-EC78-4D51-AA66-FA42E0AD335E}
CLEAR LAKE 110237580 | {2BE21FFC-75C5-4000-AF51-9092A99D4F5A}
CLEAR LAKE 11024708 | {A2C04B2A-E46B-4144-845F-8FC5D9963BCD}
CLEAR LAKE 11024708 | {7C347C2A-D137-4C7B-9A15-013D3BAB11C4}
CLEAR LAKE 1102904 | {F2BFF36E-7C09-45BB-8051-33603CB60365}
CLOVERDALE 1101112 | {A3010E82-252F-4B74-842A-7F85E53824BF}
CLOVERDALE 1101112 | {EFFBC73B-5CF0-4391-8D52-00A9D7379A46}
CLOVERDALE 1101112 | {1E501E9A-8949-4278-8D21-F330EF7F0FFB}
CLOVERDALE 1101409224 | {B0E9356B-01BC-40EC-86CF-A93C8EF70CFD}
CLOVERDALE 1101474708 | {70DF189A-0B8F-41F8-947D-2C012503D21C}
CLOVERDALE 110184088 | {58421E59-40D9-4FE6-B6D2-E336A596F8EF}
CLOVERDALE 1101964556 | {C8B8F7FB-319D-436A-B288-8DB11A5DC4AF}
CLOVERDALE 1101CB | {1FD9348C-4D4E-4981-80D7-DF41347DC4BB}
CLOVERDALE 1102156 | {0AFDFC2C-BE93-4295-B473-DFD529280FFF}
CLOVERDALE 1102262 | {79D04444-8804-48FE-A949-F2CD7D36457D}
CLOVERDALE 1102307342 | {A0D136BC-BED5-4E61-825E-2EC84D15BD33}
CLOVERDALE 1102383183 | {FC7CF79F-4C61-4A20-81A3-5285A1A20685}
CLOVERDALE 1102429006 | {7E3BECFF-8D7D-4E66-87B8-14F0BE7604FC}
CLOVERDALE 11024646 | {08D74C7F-8D6E-4EDB-8355-DEA79828121D}
CLOVERDALE 1102570 | {32B34880-BC93-4771-BC39-2E887BB96BE8}
CLOVERDALE 1102654084 | {5BCD5375-5195-4DF6-9339-79690A1EF9AB}
CLOVERDALE 1102670 | {A30CE951-E1DA-4695-8AD7-7CACD863A0D4}
CLOVERDALE 1102670 | {40B1E31D-7977-4CD1-A0DB-03E15686CC3E}
CLOVERDALE 1102672 | {B86F1274-5A5C-436E-B792-43E98848CB75}
CLOVERDALE 1102674 | {D3629DD4-F83C-4237-B37C-A36F4F11F0E0}
CLOVERDALE 1102736078 | {BF061E01-5578-402B-9978-43AB1F8350D8}
CLOVERDALE 110276878 | {1AAF0353-36A0-471D-9307-CCC6B1BFBE5C}
CLOVERDALE 1102801904 | {AC125630-32B8-4336-8024-7175EE6E43AB}
CLOVERDALE 110282888 | {B5A8374E-B790-43DB-958F-6C84A7C12E44}
CLOVERDALE 110294476 | {80FED0BE-D166-42DD-AD9D-F9569A62BF53}
CLOVERDALE 1102CB | {A0D136BC-BED5-4E61-825E-2EC84D15BD33}
CMC 1101CB | {BCDF55E9-752A-4470-8F8D-971D8F755C6B}
CMC 1102CB | {8AF78B6A-BE16-4226-B393-4AC8AD7FF084}
CMC 1102CUS6960 | {DFCC21F5-4AEA-4EAC-8FE8-846BECBF3765}
COALINGA NO 1 110878186 | {3697C802-0557-4876-8B2E-ADF61773B7C5}
COALINGA NO 1 11089080 | {C2C023AD-0CC1-4E83-AF7F-98D1E04D84AD}
COALINGA NO 1 11089240 | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
COALINGA NO 1 11089714F | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
COALINGA NO 1 11089850 | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
COALINGA NO 1 11089860 | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
COALINGA NO 1 1108CB | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
COALINGA NO 1 1109696152 | {D2837AC8-6682-41DA-9CAE-EF262EB89AC9}
COALINGA NO 1 11099210 | {1B415827-7E73-4327-8D34-697190EF078A}
COALINGA NO 2 1105134928 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
COALINGA NO 2 110541882 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
COALINGA NO 2 110541954 | {8311BA01-975F-40BD-9A68-D357106FF2E2}
COALINGA NO 2 110541954 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
COALINGA NO 2 1105897858 | {BB2EB972-0241-4416-BB6F-CD01FA83C53E}
COALINGA NO 2 11059000 | {09F38874-A51D-4724-BABB-AF0D78EDB524}
COALINGA NO 2 11059260 | {B78C04E8-BE41-498A-893C-A7AC253857A0}
COALINGA NO 2 110770250 | {C9B31884-8FA9-436F-9425-CE594852B802}
COARSEGOLD 210210040 | {68513B5A-56EB-4D19-97D2-4A9509C9FEBC}
COARSEGOLD 210210050 | {246AEE64-BD98-43AF-876E-DF5040419CD3}
COARSEGOLD 210210330 | {426A5610-C0CB-4740-A0E9-5755646CBB70}
COARSEGOLD 210210330 | {FE7641C5-7812-4FD4-8B21-6308923D8DFD}
COARSEGOLD 210210610 | {8FCA88A2-5287-4980-B557-B7704EA7B310}
COARSEGOLD 2102383092 | {96EF7A8C-C5F4-4169-B851-BA4324B1FDB9}
COARSEGOLD 21025380 | {28AC0DE3-760D-482C-B0A3-0B7999D74D44}
COARSEGOLD 21025722 | {28AC0DE3-760D-482C-B0A3-0B7999D74D44}
COARSEGOLD 2102CB | {5FCD3F70-B3EF-41B7-B59A-4AF393BD948D}
COARSEGOLD 210310300 | {D52EB2EB-C85C-45E0-96F5-17449635DB4E}
COARSEGOLD 21035020 | {19623F95-3D51-435E-B42C-17FE4878C880}
COARSEGOLD 21036110 | {04B6E7EF-7D58-4AD6-8C95-F9DC0FD8A439}
COARSEGOLD 2103731524 | {906462EC-73D3-4A4A-8B59-E052896B0724}
COARSEGOLD 2103CB | {2E4BA31C-6FC8-4D7D-B79B-DB347A05F67C}
COARSEGOLD 210410030 | {A8CB9256-CE86-4125-B378-C2EE50D5BB11}
COARSEGOLD 210410110 | {B491FAF3-D57C-4407-A408-814947D65184}
COARSEGOLD 210410400 | {7CAE9E3D-9A6E-4166-92A3-E494C4AA002D}
COARSEGOLD 21045525 | {7CAE9E3D-9A6E-4166-92A3-E494C4AA002D}
COARSEGOLD 2104570682 | {9485A7D0-401F-403C-A8F4-B704232548DB}
COARSEGOLD 21046210 | {37CEC619-9FFE-4BA7-9FD0-D8641CD59BBA}
COARSEGOLD 2104791582 | {8C9C1F4D-9C24-4A9A-947D-D1CEA924DCBB}
COARSEGOLD 2104828842 | {8C9C1F4D-9C24-4A9A-947D-D1CEA924DCBB}
COARSEGOLD 210490356 | {B3FDA245-0020-4744-99E0-2E32EA3113C6}
COARSEGOLD 2104905960 | {D13472F2-B468-44F9-94C6-B98D2DACFC98}
COARSEGOLD 2104CB | {9126AC99-906D-4CEE-8034-3EECC4C90F16}
COLUMBIA HILL 11012212 | {04384579-0651-4BF6-A92C-36154DEBC10E}
COLUMBIA HILL 11012212 | {BA4E3F60-A7E4-477D-9CC6-E4ABC3E72986}
COLUMBIA HILL 110135424 | {474A8BDA-95BF-4717-B362-885E409D4F7A}
COLUMBIA HILL 1101764 | {9DC430E4-865B-40A1-B9ED-F689C9145BC5}
COLUMBIA HILL 110190730 | {8D36000E-CB6A-4063-B9B3-E1FA6651AB85}
COLUMBIA HILL 1101CB | {472D2B95-5CE0-4AF5-93B6-7762ECA68067}
COLUMBIA HILL 1101CB | {301371C1-F917-4D83-99A4-9C27E8A52D68}
CONTRA COSTA 211496897 | {E98A5614-0363-4815-B36D-4D8FAB4E4D57}
COPPERMINE 110438474 | {E99FC5E0-5A56-4D2F-900E-4A688BBB4069}
COPPERMINE 1104556430 | {B8BBE87E-B0E7-4F0B-A461-482C2514F445}
COPPERMINE 1104613086 | {3C011A8C-6358-4933-B5ED-50C9AF8F36E1}
COPPERMINE 1104R3170 | {4532B921-F6B7-42D7-8837-06939F7F1ED4}
COPPERMINE 1104R3200 | {D5328BB7-8D1B-4713-8DFA-263EA71DC9E2}
COPPERMINE 1104R755 | {7AEDC5DF-B44F-49B0-91EC-479413610904}
CORNING 11011624 | {DFFCBFCC-EE62-47E7-8ED4-582D4BFF492D}
CORNING 110154906 | {9E4CA485-3B3D-4A5A-B314-7734F5C8C14A}
CORNING 110182846 | {0237A482-F336-4387-BDDB-C855D376A309}
CORNING 110185152 | {789DE4DB-ACCC-46BB-B059-D9142CE79F75}
CORNING 110185162 | {9C401B14-4A54-4DA8-B9DB-3EDB68F74D1D}
CORNING 110187304 | {A9C774C3-1428-4B46-A99D-50AD5766C649}
CORNING 1101972454 | {1508BCF5-AB97-4CDF-A787-A57A58E9D5A2}
CORNING 11021622 | {96C223CD-EECE-427E-9B50-0567153A92FD}
CORNING 11021622 | {1E555403-7FC2-464B-BDD6-14FBD4EE8B9D}
CORNING 11021900 | {097280CB-BBAB-443B-A213-61E2653EB02B}
CORNING 110238162 | {9739935D-6CDE-49DF-B214-4F89D603A9E6}
CORNING 110253184 | {15DF5EF9-6694-4A35-B7F3-919A8A286CFC}
CORNING 1102801546 | {04785D5D-D938-486C-AEF4-859D63028BE7}
CORNING 110290036 | {3333A9F4-A222-4545-831F-9DC4F4A4E477}
CORNING 1102915324 | {AEA3FEAB-DF92-4C59-8174-0DEFB565D38C}
CORONA 1101248 | {028C9314-BFED-46A4-8526-CFB499FC78E8}
CORONA 1103176 | {C751DAA9-A68F-4E3E-9A3D-8380575CF487}
CORONA 11034446 | {D1AA7A01-6717-4A8D-8AC5-0F1F18BEAC1F}
CORONA 11034446 | {DC9BD939-EE4C-4BE5-8C2C-6AD7A533B4E4}
CORONA 1103776806 | {02DCFD19-ACE4-4ED7-8974-B818BB682331}
CORRAL 110112304 | {C6783DDC-8CCC-4EFE-8097-5CE8336375DE}
CORRAL 110112606 | {83EA1908-090F-4204-B568-C4FACFA08477}
CORRAL 110112612 | {30A29F57-3EDB-40DD-A238-DD66DF206CFB}
CORRAL 1101173174 | {488178E5-61FC-444B-88C1-9B8C60F860FF}
CORRAL 11012128 | {B16B71D1-22D0-45E3-8592-F21047B1C034}
CORRAL 110133616 | {ADB98FB7-737B-452B-893E-B8C57E3FA760}
CORRAL 110136652 | {B537B104-D44A-45F9-BCC9-AE639B2EEDC6}
CORRAL 1101639614 | {6157CE71-7864-4436-AA7C-5C09CBEE33F6}
CORRAL 110175204 | {C6783DDC-8CCC-4EFE-8097-5CE8336375DE}
CORRAL 1101CB | {67B48D0E-E0F7-48F9-B3C0-C31311AFB61B}
CORRAL 1101CUS9215 | {488178E5-61FC-444B-88C1-9B8C60F860FF}
CORRAL 1101D1495 | {B16B71D1-22D0-45E3-8592-F21047B1C034}
CORRAL 110213498 | {A0B72D64-342D-4CD8-B398-D7C01DA365B3}
CORRAL 110214026 | {9D2DD8C8-FD4B-4B60-ACA0-0CCE69EA2F96}
CORRAL 110214028 | {485BC0B3-AC72-4623-B01D-27E2B69AFA49}
CORRAL 110236666 | {D6BA7AB0-BD1E-4258-B5D5-B64D6E99400B}
CORRAL 110275622 | {C5570B1A-B071-4827-88D1-68633BB92AFE}
CORRAL 1102CB | {A70761E3-E888-44FB-B083-651B5C823F25}
CORRAL 110313474 | {6748E8F4-5236-4133-9E21-482CCE2EC069}
CORRAL 110314716 | {69E7CCAD-089B-4A0D-AFD3-F9DC2B18E72C}
CORRAL 110336680 | {EB467927-3D28-42DC-B202-516334CB2DF4}
CORRAL 110359770 | {A87A01D7-FDFF-4B8F-B41F-FAA11796C3AB}
CORRAL 1103936674 | {6A75A276-6764-44DB-AA5D-741492F8A6AA}
CORRAL 1103CB | {64858239-7E97-43B3-8DF6-6A5627532E97}
CORRAL 1103CB | {03D991AF-6109-4C4F-9E0E-284738E05B02}
CORRAL 1103CB | {4981751E-CE05-4494-A91D-08CCD674D767}
CORRAL 1103CB | {9A391715-6E90-453E-8F9B-52BCEA2804B7}
CORTINA 1101107710 | {30FD709D-FDD9-476F-A094-8F17316D4F25}
CORTINA 110130014 | {30FD709D-FDD9-476F-A094-8F17316D4F25}
CORTINA 1101302192 | {C85ADA73-8870-45FD-B010-320E0217B2D6}
CORTINA 110130262 | {30FD709D-FDD9-476F-A094-8F17316D4F25}
CORTINA 110149858 | {CE64727D-AFA9-4CB2-B083-0E8C4E6C1F9B}
CORTINA 1101CB | {E3B77E93-BB57-4588-891B-4456F675EF56}
COTATI 1102282 | {25F749B3-A74D-4E71-A304-4CB2AAD2E132}
COTATI 1102282 | {307C6E99-F23B-44B2-9403-EE1517D0BB70}
COTATI 1102462 | {2E0FB866-9F6A-4839-A968-F9A8CD3FA6CE}
COTATI 1102464 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
COTATI 1102468 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
COTATI 11025080 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
COTATI 110257108 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
COTATI 110259258 | {94E0088D-6FDA-42A4-A01C-471E05EB28CA}
COTATI 1102825 | {94E0088D-6FDA-42A4-A01C-471E05EB28CA}
COTATI 110283200 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
COTATI 1102CB | {991C05ED-971F-4D32-B6E6-51948C4F329B}
COTATI 1103132 | {D681E6AF-06CA-4983-B4FB-ED08B0DAD260}
COTATI 1103148 | {E6932BC8-83DE-4484-A9F8-B83591D802E2}
COTATI 1103252 | {5C4483AA-BF97-4BA1-AC7C-28760FD1BF47}
COTATI 1103310 | {40F0C968-F731-4A61-A453-D93A6C5B08AE}
COTATI 1103446 | {181E81CC-8A10-40D6-ABD4-3AD397DDF786}
COTATI 110361736 | {BCD422E2-9AE0-44D1-BF49-26A0E5D7C844}
COTATI 110379140 | {8B07F2D1-E8C2-46BF-BEB1-6EA256DCFEAC}
COTATI 110387402 | {EEE52A91-AF03-4B18-9CCC-F7F6825D7052}
COTATI 1103CB | {9A3F5ECF-0D58-446E-BB8C-0FCF9D3017A7}
COTATI 1103CB | {181E81CC-8A10-40D6-ABD4-3AD397DDF786}
COTATI 1104232 | {0D1EAD50-F416-4D20-B817-3BDC9FDA64E8}
COTATI 1104426 | {B13BE392-390E-4E3B-A432-5336348FF9E8}
COTATI 110494186 | {2F39A049-2BA5-4A00-94B6-4F8A51F9E4CE}
COTATI 1104CB | {D0082608-F94E-4A4E-A9EF-A114F6AAC5C3}
COTATI 1105103816 | {775E53AE-0A4A-4EB7-B07F-0C65E0B68CCC}
COTATI 1105104502 | {1E254E89-80C2-40C5-86C1-3418E85098A5}
COTATI 1105136 | {47497F55-F48D-47C7-AAFC-7B07673C8B7F}
COTATI 11052121 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
COTATI 1105213984 | {681EF2A3-DED2-470D-950D-0263CA946ECD}
COTATI 1105328 | {711CF875-45FB-4C9E-91F5-632D204CB23D}
COTATI 110536536 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
COTATI 110536536 | {59C20F9E-941B-4368-AC69-729A9F11D7BD}
COTATI 11055156 | {ACC3FA28-9FAB-4AE9-AABE-1ABF0B659322}
COTATI 1105616 | {4B1C4FCD-287E-4417-8568-2D11E983B37F}
COTATI 1105701873 | {970A448F-8FB4-445C-86EA-CEC681F3DA87}
COTATI 110578286 | {E3F3EE76-01DA-4EFD-A1DD-D7EE0921249A}
COTATI 1105844060 | {8FC5790B-23DE-4032-81D7-65E070CCE3DA}
COTATI 11058459 | {1E254E89-80C2-40C5-86C1-3418E85098A5}
COTATI 1105893 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
COTATI 1105CB | {03190DAD-5324-4E1C-86DE-04D88D55A9A0}
COTTLE 170178452 | {D07798BA-B7E6-4FB9-A5A9-A05BC7F2FB6F}
COTTLE 1708968888 | {9FFC0599-7BDD-4120-9A8C-31EF3E3F7596}
COTTONWOOD 11011510 | {DB300DCA-6215-4B3C-914F-828156445EA8}
COTTONWOOD 11011610 | {FD19D23C-6A96-40C9-9542-F7EF9A6AB34E}
COTTONWOOD 110131500 | {29DB4A9A-9909-45FE-9CC1-C3F1A6A44799}
COTTONWOOD 1101384360 | {6E9AA275-95DB-4AA1-8ECE-7A4C85318300}
COTTONWOOD 110168190 | {B9D0806A-E952-4DB8-821A-8A74AB16F016}
COTTONWOOD 1101CB | {509EDC5C-5C13-447D-BAA5-6AE957D846E4}
COTTONWOOD 11021578 | {0E682A09-C0D8-404A-8B27-2B967048024C}
COTTONWOOD 1102306414 | {923B374B-55F7-4545-A3FB-1BD97DF88ECF}
COTTONWOOD 1102544790 | {7F934250-B67B-44F2-9547-08902728DC9E}
COTTONWOOD 11029026 | {BD544C17-FF5A-4B33-BB2A-02C4080D2F78}
COTTONWOOD 1102CB | {7F728486-5D30-4578-BA26-525DB688C650}
COTTONWOOD 11031344 | {B1A37D66-F35D-4EB7-8214-339B94F2CF9F}
COTTONWOOD 11031348 | {7B732F61-9830-429D-98CB-A07442DFF2C3}
COTTONWOOD 11031508 | {86195D79-B13D-4A31-9815-45E1A5BFFF0A}
COTTONWOOD 11031616 | {6AAE7F1E-BB91-4B40-919F-7A37BE5E005F}
COTTONWOOD 11031616 | {DB1CB0BF-953F-4047-B280-2F768227CB6A}
COTTONWOOD 11031616 | {C5040B2B-4C8C-4639-95E4-0DB3DBF91F3A}
COTTONWOOD 110331548 | {5C7585A0-7AA3-4054-BF6B-A9176A3B037F}
COTTONWOOD 110335470 | {E7F7F25C-AE9C-459D-9EB5-32BCE8602EF6}
COTTONWOOD 1103389928 | {323D98DF-F7C8-439D-8E63-3A2D9C1F2EC2}
COTTONWOOD 110359128 | {9ABEF7F9-4364-4AF5-84C8-8C5E0DDABB90}
COTTONWOOD 1103732932 | {B34D6510-4EA4-4D05-870A-2F82DCFA67AE}
COTTONWOOD 110385050 | {7567B55E-AD2E-47FA-B262-240B7B9C7A1E}
COTTONWOOD 11039072 | {CCBE325F-DB08-456F-8920-C4494B0832D2}
COTTONWOOD 1103957942 | {FE2A03BF-2A82-4C60-A029-FE923684D1C7}
COTTONWOOD 1103CB | {7A360B24-DB74-4302-B7FF-A7991F9BEB20}
COVELO 1101112804 | {5A8F3694-A0F4-41C3-88AB-492CAEAEF38E}
COVELO 1101225458 | {A1037E1E-1E0B-4B86-909D-EE36FE670AFC}
COVELO 11012467 | {149E5268-4926-4B7A-B9E2-928EA9B5F83B}
COVELO 110137328 | {D4E144DE-8AEF-45D3-9080-EB1CCEA62B46}
COVELO 1101430286 | {64F3E707-0C89-449C-A14A-0CB9EA1C7E88}
COVELO 110146208 | {1E92B113-D351-4051-A3ED-221149B2FA2D}
COVELO 11014678 | {8CC880C0-D20D-47C4-883B-62E97018E45A}
COVELO 1101516510 | {EADD8CA4-64AF-4618-B2F5-C69C9631D28B}
COVELO 1101536 | {7897A070-7C30-42E9-B1B0-EB5E015E733B}
COVELO 1101562360 | {149E5268-4926-4B7A-B9E2-928EA9B5F83B}
COVELO 1101679050 | {211F2948-077B-47E2-AE1D-731B8C6DAA7F}
COVELO 110196896 | {C93D43A5-1B00-47F7-99CB-5288FDBDDC41}
COVELO 1101CB | {F774F37B-0BFB-4E5C-8B3B-83726F441387}
CRESCENT MILLS 21012056 | {BEDEF3DF-E1F0-4BAB-9E81-90CA4240CF80}
CRESCENT MILLS 21012230 | {729A138E-F406-4953-BD8A-A6BF7C82CC1C}
CRESCENT MILLS 21012232 | {6FD1FEB7-53BB-4905-92FA-6BF228EE659D}
CRESCENT MILLS 21012562 | {50FC30D9-9631-47C1-AB52-87E3C16BC0D9}
CRESCENT MILLS 2101CB | {13C79B20-35FA-46F6-90D1-7123E115130F}
CRESTA 1101103126 | {8CC5C28A-D4E3-4E7C-8DC9-1431E561B6CC}
CRESTA 1101546650 | {A1AFFBEB-1EC0-4B98-95D8-379CD77E7C39}
CROWS LANDING 110190600 | {5A5D22BF-24BA-433C-9E32-EE55B80DC70A}
CURTIS 1701842008 | {11782BED-BAF4-482E-B926-E7AFADCE2119}
CURTIS 170190120 | {9E6CCAD4-16BF-438A-8FB8-933F07D27C09}
CURTIS 17019230 | {BD6EE575-4256-4E66-B07C-5D3BE152301A}
CURTIS 1701CB | {74641153-5847-4D3C-B484-25FD29972F96}
CURTIS 170210940 | {16922C05-7DEF-4043-B388-9531C1140314}
CURTIS 1702278740 | {3F3B50FA-3E42-4B14-8E0A-7FFA3136F01E}
CURTIS 1702295684 | {A1BFE45A-13E7-4FF1-9988-30B11E2FBC1C}
CURTIS 170234426 | {897848FB-F125-46A8-B9E9-7A6CE5229B91}
CURTIS 170247488 | {A13891AD-BB5A-427E-8F5C-CEB24021177B}
CURTIS 17026008 | {B65A3679-2982-4589-9816-E14BDF4C9657}
CURTIS 170268380 | {45D5D58B-80DE-4D2E-89C9-FED8B8DCC26F}
CURTIS 17028000 | {C413BF51-2D4A-4E14-8A5C-AF93355185D2}
CURTIS 1702CB | {7226EEDE-AAEC-45AB-A41D-23DA3572485A}
CURTIS 1703258550 | {E57DD2D7-FAFD-479E-9BAB-621A0696EA30}
CURTIS 170349746 | {7D0477A1-3B70-4629-B0DA-1E96F8ADF8DC}
CURTIS 17036064 | {1D6F2813-1DE7-4CF3-9F1D-B6618158D284}
CURTIS 170384944 | {46CEA7E9-BB3A-493A-8627-27189E1BD87C}
CURTIS 170390320 | {419BA50F-A9D8-4C0B-BAD7-EA55841BE036}
CURTIS 17039210 | {28A07299-BAB6-4846-84FA-366E13AEFEE9}
CURTIS 17039240 | {11F969DC-9C50-4BBE-BE33-15DB7CEEDE86}
CURTIS 17039330 | {BE967458-9C2E-4DBF-9D1D-857D10B2BFD4}
CURTIS 1703CB | {C4B116D3-EE04-4D0A-96A8-6CF57FE78721}
CURTIS 170411290 | {5B03EFF1-F12F-4656-8D60-84D55FFB9841}
CURTIS 170411300 | {1342493A-4682-4997-B671-32B9B4D877B0}
CURTIS 17046060 | {677BC4CE-74C4-4870-9B50-45491FB41EEF}
CURTIS 170463502 | {A5122D22-FC3B-40AD-B1C9-1922AC7D5EB3}
CURTIS 17048140 | {44BC81C9-8540-477A-9326-99FB3CD481E2}
CURTIS 1704CB | {6CFF4874-9416-4562-8168-A66869F04B91}
CURTIS 170510590 | {EA84943C-5C73-4028-8D85-A074BC119CA8}
CURTIS 170511790 | {82A7B687-8833-4D9D-84AF-D482AF9F7393}
CURTIS 170539256 | {60313232-3855-4646-B9A6-D03E4546E4FB}
CURTIS 170565908 | {2ED0FFD8-DF5F-45A0-8687-5F34F37A5A97}
CURTIS 17058110 | {09598188-CE5A-44C7-8CBD-CFBA0AA34580}
CURTIS 17058170 | {944E3EC7-4285-4D17-99A0-D6960B77E4D2}
CURTIS 1705CB | {87827028-00DC-43D6-989D-C6C9D1E3E860}
CUYAMA 11031635 | {7338276C-0737-41F2-B421-53D877AA647D}
CUYAMA 1103282557 | {B9AA0189-24D7-4071-9165-3E1FA51856CE}
CUYAMA 1103622728 | {EC646814-C576-4C16-B414-32B05AD6EA11}
CUYAMA 1103684566 | {D1C13827-3D8F-47CF-923A-969F7154F0AA}
CUYAMA 1103934590 | {85AC51B2-8F96-41CA-A563-24966A62ABEE}
CUYAMA 1103CB | {086ABE98-CA07-4B5E-94A2-D2E7EF6983E6}
CUYAMA 1104CB | {C3CB332E-B41D-4DA6-9C37-1357A17FBA81}
CUYAMA 21013039 | {AE254590-1F13-4FEF-92B1-1F8EB5A8892D}
CUYAMA 21013533 | {AE254590-1F13-4FEF-92B1-1F8EB5A8892D}
CUYAMA 21013542 | {F9E131D2-E655-4DF9-A7E0-8C8B213A0782}
CUYAMA 2101952122 | {A7BC3A91-18C0-47E6-A9C8-4D7D73EA0E4E}
CUYAMA 21021000 | {78102D0F-3634-4153-BADD-EC52C2E98E32}
DAIRYVILLE 1101147562 | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
DAIRYVILLE 11014679 | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
DAIRYVILLE 1101CB | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
DEER CREEK PH 0401CB | {F552B7B1-BED9-44D6-8E42-3FC8759927EC}
DEL MAR 11032702 | {FAA4BB2F-A14A-4ACA-9B63-02DFB58C1EE6}
DEL MAR 11032716 | {EF81CA1C-18C9-4299-AF2A-DDBDF91E767C}
DEL MAR 1103624 | {C849372A-DDB7-468F-9EC0-AE7D09002A23}
DEL MAR 1103CB | {8F0FCBB5-348C-4DDA-9D44-60778A054848}
DEL MAR 21051270 | {DD87F226-71D9-4417-928F-44802F1E6068}
DEL MAR 210551692 | {DD87F226-71D9-4417-928F-44802F1E6068}
DEL MAR 210584138 | {DD87F226-71D9-4417-928F-44802F1E6068}
DEL MAR 21061686 | {1E127AF9-846D-4194-872F-DBA8A5888781}
DEL MAR 210938684 | {970BC050-24B8-4916-A013-B639A58BC60E}
DEL MAR 210975802 | {AAD63AEA-E006-40EA-8F1E-5C283AEC521A}
DEL MAR 2109CB | {1AC49A61-94D2-4C02-B343-C9B71226B2E7}
DEL MAR 2109CB | {96C68544-319F-47DB-A974-F7A5B4652808}
DEL MAR 2109CB | {A3D1D6B2-C2DB-46A7-9A60-CC55ABB31E62}
DEL MAR 2109CB | {22B160E3-E935-4B26-93DB-42C315B0CA8A}
DEL MAR 211064434 | {17A14D41-ABC2-4BCA-9DAF-12F930E89A32}
DEL MAR 2110CB | {67D76908-7B70-4DAD-A31C-C1F7E75F3357}
DEL MONTE 210138582 | {2F70F4D8-3BA3-4012-9A01-B8B771F3D276}
DEL MONTE 2102396158 | {C195EA2E-4577-42D2-B33A-631AD864FAE4}
DEL MONTE 2102615458 | {C195EA2E-4577-42D2-B33A-631AD864FAE4}
DEL MONTE 21032000 | {A7511424-C0A7-4DC4-BAD6-B60505BBA431}
DEL MONTE 21032144 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
DEL MONTE 21032642 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
DEL MONTE 210332886 | {95BA16F1-C0BE-4BE8-9C3E-AD056E7BB712}
DEL MONTE 210342226 | {8CF433ED-5D30-4AF4-B399-FAE6BF4CEC35}
DEL MONTE 2103468158 | {6129877C-0FCC-4F26-BBF6-7A6117D5D7AC}
DEL MONTE 2103617344 | {A04AFFEA-C849-4263-A535-5ECE95BFA747}
DEL MONTE 210386496 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
DEL MONTE 21039106 | {900D5BA1-EA68-418C-9CFF-B7A1E9A4FECC}
DEL MONTE 21039452 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
DEL MONTE 2103CB | {B9CA7C26-A10E-4143-8CC2-799A8D4A9979}
DEL MONTE 2104181640 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
DEL MONTE 21042032 | {C1DCB446-91BC-4976-8E19-E90A61136DD7}
DEL MONTE 21042624 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
DEL MONTE 21042762 | {32A9C949-424C-43B5-963D-82C15E14F50A}
DEL MONTE 21043088 | {FB7A8750-C967-4B2F-BC27-F33BBB5DCEFD}
DEL MONTE 210448004 | {C1DCB446-91BC-4976-8E19-E90A61136DD7}
DEL MONTE 21049096 | {53A81FCC-6CE7-4EE5-B8F1-AB89BF2F3989}
DEL MONTE 21049500 | {9F487EDE-1254-4232-B1F0-1B8CB4720B05}
DEL MONTE 21052644 | {317B7582-B045-4053-8009-5D848CC65A15}
DESCHUTES 11011380 | {53F1163A-2879-44DA-A8DC-132948A94C1B}
DESCHUTES 11011580 | {064EA007-8A62-40F7-BDB2-55C9C2572F4C}
DESCHUTES 11011652 | {FDD63F63-31B3-4440-A376-DFAEA489B8E7}
DESCHUTES 11011654 | {1A40C8BC-051A-4DE6-8C9D-412DD5FF54A2}
DESCHUTES 11019722 | {2EB378FB-B271-4EC9-A2B7-75CAD47F81DF}
DESCHUTES 1101CB | {FE5A37BD-E086-417E-B0C1-D984D30B636B}
DESCHUTES 1104100170 | {C6E4D1C6-A148-459C-BC88-ACC391E7C0CA}
DESCHUTES 1104116082 | {C3EF95F9-70F4-48A0-B2DD-F52E93DD3550}
DESCHUTES 11041370 | {7B256BE5-97E8-449E-A46C-21FA2871BA72}
DESCHUTES 11041582 | {1467DC6C-6C30-498B-9696-60E37D99774A}
DESCHUTES 1104269170 | {2ABC92FF-56CD-4099-9E14-FDA9128A7AC4}
DESCHUTES 1104378894 | {BC7A1387-B3D8-4140-98B2-87298F0B6696}
DESCHUTES 1104421598 | {101F2F9F-D72D-4EB8-8A9A-E537C20D5C27}
DESCHUTES 110449024 | {6DDF5542-CAB8-4ED4-9238-C0F4D392F99F}
DESCHUTES 1104589602 | {A660A9BE-07D9-4051-AC7B-0365C697FBAD}
DESCHUTES 1104622260 | {77B43BDD-8E2B-4B03-A902-769AAAC5407C}
DESCHUTES 1104715242 | {A9629347-170C-4912-B206-AFC987807C15}
DESCHUTES 11049718 | {105AF226-5705-41BD-B206-D294BEEB8D68}
DESCHUTES 11049718 | {F164BF8B-3484-47A3-8EEF-5FFD77D4911A}
DESCHUTES 1104CB | {969F6F9B-F1AA-4EF5-A1EE-31E0C15FF124}
DESCHUTES 1104CB | {D7FE7EC5-7478-43B3-9A24-52065EFA1755}
DESCHUTES 1104CB | {5D26706C-A4A6-4F70-88DF-BA9D990C37DF}
DESCHUTES 1104CB | {D8DA000A-2BA2-48CB-B580-008FC2511D24}
DEVILS DEN 1101824190 | {2555B82F-7B04-4543-97DE-389AB426740D}
DEVILS DEN 11019470 | {EA4C9C10-BAD2-4A0F-9CF7-5CA727AB7653}
DEVILS DEN 1101CB | {E637B763-1297-4DA3-B168-C020DBAC2EB8}
DEVILS DEN 1102460850 | {1ABBA2B1-53B5-449A-A275-B6A0999D81FE}
DEVILS DEN 11029340 | {85D70EAB-58A6-4861-89D2-07CC374A0ABB}
DEVILS DEN 1102CB | {A92A6C8C-B557-4608-A4A1-975F3E0D9109}
DIAMOND SPRINGS 1103467046 | {2A7BBA85-AF71-468C-A351-10A5AC7DB14A}
DIAMOND SPRINGS 11039432 | {A12D2A90-44E6-4ECA-BE2F-8893B2D17E74}
DIAMOND SPRINGS 1103CB | {F21436B1-06B1-4781-A6B4-F2B85E06831B}
DIAMOND SPRINGS 1103CB | {A0F6FAAB-8AD3-4FB6-80FD-2F7C87739A36}
DIAMOND SPRINGS 1103CB | {9212A36D-CBC9-4C2D-979D-8E57F583136A}
DIAMOND SPRINGS 1103CB | {5ED167AC-20A8-4AC6-A90B-E7A7EBAEFD8B}
DIAMOND SPRINGS 1104147386 | {8D8139BF-D216-4D14-B0AC-67DE21E71989}
DIAMOND SPRINGS 1104705100 | {B2C0084B-109E-44CB-BAED-2939A6DED126}
DIAMOND SPRINGS 1104CB | {6872443C-7FE4-416F-92B9-65D58A293737}
DIAMOND SPRINGS 1105146980 | {47C81E1B-8837-481E-AA75-EC428AEB85F2}
DIAMOND SPRINGS 110518935 | {C35B7B84-D418-41DB-BA63-E9DFFDA08709}
DIAMOND SPRINGS 110519910 | {B086CF84-D2F5-42B5-8FBA-007201735811}
DIAMOND SPRINGS 11052102 | {51B4FBA6-E864-4F62-B988-2A8243E75100}
DIAMOND SPRINGS 11057722 | {9B3053D4-0FCD-415D-AE49-1C1AC44BB827}
DIAMOND SPRINGS 1105CB | {76BB324A-98B3-4C58-A6D4-32DC864FAEB9}
DIAMOND SPRINGS 1106176130 | {069FC1F9-26AE-4248-95D3-8B4718D722BC}
DIAMOND SPRINGS 11062100 | {6647B708-EB30-40C8-9FB8-1AD5D9953BA6}
DIAMOND SPRINGS 1106279670 | {1FAA72D4-5699-41F5-A2F3-C539D6B6ADA9}
DIAMOND SPRINGS 1106337536 | {4FE0ADB2-8944-4613-9148-3D68B70EC500}
DIAMOND SPRINGS 110650324 | {DCB9D4A3-4396-4AF7-B5A4-4405D20B6E8E}
DIAMOND SPRINGS 110656026 | {95AAF818-10A5-460C-909E-8A1D81C4AEC8}
DIAMOND SPRINGS 1106583890 | {FB9AE970-0795-40A3-9446-AC1D8383DEBC}
DIAMOND SPRINGS 110676088 | {423A8C76-9A51-45A6-B374-FEBC31B925B4}
DIAMOND SPRINGS 1106762780 | {5E624FA1-8898-49A2-BC33-0C0CCA1E740F}
DIAMOND SPRINGS 1106930190 | {DBEBD4F1-7629-44E7-936D-64D99597E03A}
DIAMOND SPRINGS 110699658 | {AE525890-6C02-4814-857B-4FEF1E7D58A9}
DIAMOND SPRINGS 110699658 | {5F542D36-4FC1-413E-B114-C90AD9930E1C}
DIAMOND SPRINGS 110699658 | {66BEC755-EB33-41C4-BD19-8B49A68F1B0F}
DIAMOND SPRINGS 1106CB | {C99F1365-4BA0-493A-A0A5-5D7F7D14700C}
DIAMOND SPRINGS 1106CB | {21AB04EE-D7E1-4680-98C1-D718C5F41455}
DIAMOND SPRINGS 11071402 | {04F6A01A-981F-4306-9D80-21027E2CEC32}
DIAMOND SPRINGS 110719702 | {635CA5E5-8968-4E76-BA11-3BE643BA9E35}
DIAMOND SPRINGS 1107203504 | {C468F999-9DD1-4480-AEEA-A7CA15687805}
DIAMOND SPRINGS 1107217974 | {EA651BD1-B1BE-4A95-908A-06FA4832B9F5}
DIAMOND SPRINGS 1107301798 | {87CBC4D7-654D-4F94-B8EF-BF8BE88A6CF0}
DIAMOND SPRINGS 1107336076 | {01A8C6BD-323D-44E5-A686-1246351A46F2}
DIAMOND SPRINGS 110777086 | {124D6D8B-14FB-4F2A-A51D-104BDFD91E41}
DIAMOND SPRINGS 1107CB | {01A8C6BD-323D-44E5-A686-1246351A46F2}
DIAMOND SPRINGS 1107CB | {9EEBDB00-7814-4DCA-94A7-A89D1F5F04EB}
DIVIDE 1101CB | {24B4C5D2-9190-403A-BD5D-182F06265073}
DIVIDE 1101M78 | {D82C0681-14F5-4168-A5B8-47CCE62ECA70}
DIVIDE 11021385 | {A0FD2E34-A735-4A8C-A9DC-394B15A3212D}
DIVIDE 110245067 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
DIVIDE 110266960 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
DIVIDE 1102CB | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
DIVIDE 1102M130 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
DIVIDE 1102M144 | {A0FD2E34-A735-4A8C-A9DC-394B15A3212D}
DIVIDE 1102M46 | {CA16F48A-6A4D-4E2F-9307-EE7712739B5B}
DIVIDE 110323614 | {AB1CE55B-42CF-42B2-8A5C-221DBBC685D8}
DIVIDE 110348160 | {6ECC9377-E065-4FCE-971C-2036CD830EDE}
DIVIDE 1103567884 | {8595AA03-4461-43F0-83E3-96D1A07CC7F4}
DIVIDE 110398166 | {4AF5ECF8-33C4-4E7E-9141-A6CD2D4FF4E6}
DIVIDE 1103CB | {BFA942F4-E00F-4B4B-9BEC-83B4F4C04B73}
DIXON LANDING 2101XR340 | {78E11C69-9A86-4183-B3C4-869A091C2B3F}
DIXON LANDING 2101XR580 | {2E4CE54C-8476-4E1A-805A-F9485D5B2B5C}
DIXON LANDING 2109MR211 | {270CEB57-AF3B-4573-86AD-B73952A8BF6B}
DOBBINS 11011264 | {81A1F156-C98B-4850-992A-A7159456D080}
DOBBINS 11011808 | {E4399593-CC75-4E6C-A098-AD618A358CCA}
DOBBINS 11015202 | {65B27162-E2B7-4CEC-9138-2917B0C9553F}
DOBBINS 110169722 | {DCD6C7A6-BCDE-42A2-9036-021FA6ED047F}
DOBBINS 110183186 | {79296F22-0716-473A-A665-0DFCBF4642CD}
DOBBINS 110191464 | {93C56D43-333C-4331-959E-24C064CB9C39}
DOBBINS 1101CB | {3EEFA179-0D60-4808-A6C9-A2D8F6C0C66D}
DOLAN ROAD 1101156268 | {A6335D58-E606-4A31-A5A5-958C5FE37A92}
DOLAN ROAD 1101173702 | {F06F081F-C9F5-4637-B24B-42F86E64048D}
DOLAN ROAD 110122158 | {95DA73C9-4DB4-4C31-AFD8-C43A5BC36425}
DOLAN ROAD 11013048 | {75D6BA77-B219-460D-A17E-99E648854306}
DOLAN ROAD 110157184 | {18BD8A9E-072B-4ADD-8F74-F890B89581F0}
DOLAN ROAD 1101590402 | {B7B666E0-E3B4-4668-B112-954F6AFA2706}
DOLAN ROAD 1101672110 | {18BD8A9E-072B-4ADD-8F74-F890B89581F0}
DOLAN ROAD 110169466 | {8DAD43E1-C0B6-4B91-89E1-55DFB8ABD7AF}
DOLAN ROAD 1101857972 | {EB37E4EB-78C1-4046-AF1B-2299D2328F22}
DOLAN ROAD 1101882610 | {6AB13B35-5C7E-47B3-B58A-5166F0A77CC1}
DOLAN ROAD 1101CB | {75D6BA77-B219-460D-A17E-99E648854306}
DRUM 11011602 | {4FA3034C-CC34-47A2-AF7A-8A1D1515E919}
DRUM 1101CB | {4FA3034C-CC34-47A2-AF7A-8A1D1515E919}
DUNBAR 1101137736 | {7EED3CE2-525A-40E2-A0FE-AAB7CF9E89BB}
DUNBAR 1101142052 | {973AD71F-0A48-4C76-99A8-AC94CF8D1012}
DUNBAR 1101440 | {5AA0A9EA-0FB6-4230-B4CC-9462B9350D46}
DUNBAR 1101440 | {6FF82866-EF3C-4AEF-B41F-362F035D5794}
DUNBAR 110149556 | {AAAAB995-BEE5-4E3E-A4F6-5814FD3767E5}
DUNBAR 1101534 | {8CA59690-B3BA-4A2A-90F5-8A9118795C50}
DUNBAR 1101534 | {5426272A-AD0A-4461-A119-14316B37A620}
DUNBAR 1101725292 | {86609C6B-F85A-40FF-9C70-59FE9D214477}
DUNBAR 110181584 | {BDFCA591-2F6A-41F8-B3C8-57FDA10FAC4E}
DUNBAR 1101835658 | {E3222172-78EF-43FF-8CE5-0E25731FEA0D}
DUNBAR 110184678 | {053B6290-C448-4801-B1A5-3E9ABB283E0F}
DUNBAR 1101872066 | {7BA4959A-2F94-4080-BC9D-0C53D9644F4F}
DUNBAR 1101904852 | {EE9E2000-1BCF-4D6D-94B0-B0FE09254374}
DUNBAR 1101CB | {099221CD-5C0A-49E5-8576-2B334B5F477C}
DUNBAR 1102246 | {E5FC257A-973F-414F-A273-EE859A543B23}
DUNBAR 1102246 | {ECF0597E-C523-4664-9DE2-2ED0EC5C00F2}
DUNBAR 1102261774 | {04FFFA70-53BF-428C-99F6-1A2E798AF420}
DUNBAR 1102264 | {18F70BF8-C85A-4C7D-8180-406A04F2532F}
DUNBAR 1102386158 | {672F5B11-4A5D-4A77-BAE9-574FB74B1678}
DUNBAR 1102448 | {19F00F46-8DF2-4369-8C23-B78BEB3B793E}
DUNBAR 1102528 | {FB8DED4F-C1A4-4542-AF21-D3D770C633DF}
DUNBAR 1102694641 | {9330F6B0-760C-4338-A4C1-C3EAEF5F2D51}
DUNBAR 1102861496 | {200F9B52-1051-48E9-985E-1C9F81A1D6A9}
DUNBAR 1102CB | {46D8BBC2-519D-4FA1-BC3E-5FF3581AAFDB}
DUNBAR 1103160 | {98861C56-51D3-43DB-9804-E460E1D0C1F4}
DUNBAR 1103234 | {E64AC1A3-7B00-44C4-B413-8ED8E1419B88}
DUNBAR 1103234 | {670EEEC7-97F3-49B4-8DF7-BA5F346AE80F}
DUNBAR 1103302 | {6B9EB51B-5FA3-4BC3-9024-69ABFBD94AA6}
DUNBAR 1103302 | {34794EA8-41B0-4C58-A267-88FB7ED2F311}
DUNBAR 1103416 | {BF23F54F-E263-4EE1-9D2E-F9BC52287A4F}
DUNBAR 1103416 | {E1077E4E-022A-4658-906D-61D41C4EF125}
DUNBAR 110347964 | {565357B0-3D43-4998-81C7-7EBC74E038B1}
DUNBAR 11034882 | {2B1CF1D9-BF9E-474F-B027-6D9BAFB42F24}
DUNBAR 110379086 | {EDA68B39-7DBD-43E4-954E-1185A3CE9473}
DUNBAR 1103831696 | {E0CFF63C-79DD-403F-842B-413C7E8A35ED}
DUNBAR 1103839384 | {BDF50AB5-3CEB-497D-9CC1-A6453469223A}
DUNBAR 1103CB | {587017B7-CF95-40B8-A31E-326EDAB4E012}
DUNLAP 110239190 | {03B91929-B748-41B7-BED2-9D46A08F08B1}
DUNLAP 11027050 | {1A4C84BC-5487-41C8-8DEF-67BCD120C5BE}
DUNLAP 11027050 | {DA87C478-BBD3-40FA-ACA7-D9696B584D48}
DUNLAP 11027060 | {DC0C9AE9-E0EC-4108-AF9E-4DDFE694FC71}
DUNLAP 11027360 | {81D716EF-AF38-46F5-8FD2-48383247DE01}
DUNLAP 11027849F | {DC0C9AE9-E0EC-4108-AF9E-4DDFE694FC71}
DUNLAP 1102CB | {A6D1F5C5-C503-4CFC-844D-2877BC97AA39}
DUNLAP 11037040 | {079BD93C-880F-493A-A5F3-34E94A52D05E}
DUNLAP 11037080 | {3474C71F-C417-4DFD-9033-1EBD72D1A9BF}
DUNLAP 11037170 | {733D4902-C475-4A3B-A2B1-E7586C4C7AE4}
DUNLAP 11037220 | {5755A55C-8127-474D-99F5-38E2401D21A6}
DUNLAP 1103CB | {2C485712-3D09-43E6-B47A-A2006FA28A66}
EAST MARYSVILLE 1108900690 | {D1622BED-440D-498A-AED4-D8C420D1B767}
EAST QUINCY 1101186938 | {627D9E79-9527-4BAE-9B90-33425D67192A}
EAST QUINCY 11012452 | {D7BCD386-8384-4488-96C5-A2E06819036D}
EAST QUINCY 11012452 | {6969282E-3667-4FB6-817B-4CFA67C6A49F}
EAST QUINCY 11012452 | {59C7C56F-8F8D-453D-B2CA-2A56446D1413}
EAST QUINCY 1101424048 | {13F95C63-620B-4827-AE11-2F38727C8122}
EAST QUINCY 1101951424 | {D3FA1F53-9642-40C0-A05D-D3416EB9964D}
EAST QUINCY 1101951424 | {83723391-EB93-4D6A-A5B4-68EA4AD17B8A}
EAST QUINCY 1101951424 | {181CA5A4-D7E4-4D9E-BABB-349CF307AC6C}
EAST QUINCY 1101CB | {7BDDAA75-E6EC-4597-A704-7B9866E3D480}
ECHO SUMMIT 11012500 | {52018984-7699-4174-8C0E-5E599E3F4F55}
ECHO SUMMIT 1101265728 | {0BBBFD3F-9382-4B18-B4F1-25E570CA311D}
ECHO SUMMIT 1101344250 | {501D001C-604C-4CB0-BC61-4A03C3824F33}
ECHO SUMMIT 1101481660 | {F8951716-F878-4227-AE2D-235860A82922}
ECHO SUMMIT 1101507864 | {F4871223-6C42-4618-A561-E6E1513340DF}
ECHO SUMMIT 110155262 | {D6DB5AF9-E5B0-458F-9897-3AC3E052AB08}
ECHO SUMMIT 1101741586 | {C75EBAF8-0756-4F0F-AECF-0B1CCDC1C4A6}
ECHO SUMMIT 1101889106 | {F991AA46-5F55-4799-A06C-6C07D5355682}
ECHO SUMMIT 11018922 | {3CE51A5B-7612-4EAB-BF43-95EB9AC2B5AB}
ECHO SUMMIT 1101927328 | {14BBAC88-26D3-4F29-8425-274D619391ED}
ECHO SUMMIT 1101927812 | {23975705-6B7B-4563-9AB7-FBDE3FDAFF86}
EDENVALE 1102XR064 | {7567099C-0C78-4F90-B664-1299D6F2A2C9}
EDENVALE 2105469810 | {8B87811F-B323-4484-BBE4-38B55670D94B}
EDENVALE 2105739448 | {0DDD3612-D5D8-453A-817C-994BF75B062F}
EDENVALE 210589634 | {3428AB16-83A3-41CA-A97D-9F45E561A9E9}
EDENVALE 2105CB | {8A7625DF-9660-4682-92E4-DE9581577DA5}
EDENVALE 2105XR336 | {15F04618-5F16-4576-9451-1BBF99F669DC}
EDENVALE 2105XR350 | {8A7625DF-9660-4682-92E4-DE9581577DA5}
EDENVALE 2105XR392 | {8483E0B5-64AC-44E8-8893-21CFBA8E4B48}
EDENVALE 2113CB | {CBC2E590-65E4-4DD8-9118-7B6CB910201C}
EDENVALE 2113XR106 | {CBC2E590-65E4-4DD8-9118-7B6CB910201C}
EDES 1112417626 | {8BEFF91A-7C09-4291-9AE2-AE9219165D14}
EDES 1112484536 | {D3882565-9819-45B1-A12B-BBD1105FE66C}
EDES 1112CB | {2D451082-1A86-4185-BC9F-55534CD32ABA}
EDES 1112CB | {8BEFF91A-7C09-4291-9AE2-AE9219165D14}
EDES 1112CR100 | {63D64072-C2FD-480F-8116-E56FEE7BD425}
EDES 1112CR282 | {C2D0F25E-59C9-41E0-A6F7-60C91C33934C}
EDES 1112CR306 | {1CFCF663-0CF6-44D7-93F9-73671725C761}
EEL RIVER 11021902 | {AD459C08-CBDF-43AA-86A2-CD8C1B5B6101}
EEL RIVER 1102409694 | {FB6BD3A7-81A9-4DC9-861C-0BEFD220DE29}
EEL RIVER 11024396 | {890D4B8A-DB25-4CCA-9D69-562BFAFFB09E}
EEL RIVER 11024600 | {6D6CFD45-47DB-4466-97E2-D7B4460098A9}
EEL RIVER 11024814 | {CCE91D7C-BCE4-4F01-BD5F-6C83E3A409D2}
EEL RIVER 110249130 | {1527E47A-434D-4693-8754-4E5320E20B87}
EEL RIVER 110249130 | {ADA0B946-8139-4D75-A3D4-894703D1FC57}
EEL RIVER 1102530 | {B0F5DD9B-BA5B-4914-9A80-5D9AD769A95A}
EEL RIVER 1102630456 | {BA4CF323-BCF8-49E7-A1D7-D6A1F53933B5}
EEL RIVER 1102680 | {4D91C2EE-0E70-4830-92FF-2507FF07CCFB}
EEL RIVER 11028416 | {6D6CFD45-47DB-4466-97E2-D7B4460098A9}
EEL RIVER 1102CB | {27E2901A-1EBE-4CC0-B5CB-538A633C6C56}
EEL RIVER 11033820 | {A8C66523-6BAD-4410-B093-1D69B3A4DEED}
EEL RIVER 1103CB | {A1A1D221-0393-4995-8057-AA9153B871D9}
EL CAPITAN 110311670 | {BCF947C4-6F66-4253-A6FE-897D9621AEC6}
EL CERRITO G 1105978484 | {A06397A2-6E65-4BA1-B08E-782C28C5386E}
EL CERRITO G 1105BR160 | {473DFDCA-EA19-476B-B0A4-B163B0B91B7F}
EL CERRITO G 1105BR164 | {14BEC098-B04A-4CB2-9AA3-38D63A101CE1}
EL CERRITO G 1105BR304 | {9DF9A52F-32F8-4676-BE5E-F9A3D03712AF}
EL CERRITO G 1105BR316 | {3F882A80-2491-48FC-AFA8-BDC3FFEA4D12}
EL CERRITO G 1105CB | {63FDD22C-1D84-438C-BDD2-97E9627809B3}
EL CERRITO G 1108BR346 | {47E84AA2-B51F-4F91-9057-B9557EEB1018}
EL CERRITO G 1110BR236 | {DBB65B1C-D816-44BD-B6A7-C95BB0A659FA}
EL CERRITO G 1111760530 | {EC819229-CAFA-4A70-A2A2-F76BBD0A5610}
EL CERRITO G 1112418480 | {F4711D50-C892-433D-B1D0-EB1B6E0C6AE7}
EL CERRITO G 111257953 | {253DD6AB-E4CF-46A7-A9CA-31B26BCFBF2A}
EL CERRITO G 1112649732 | {7A0FE4A4-8FE2-4A7A-9013-EEA423D246F9}
EL CERRITO G 1112664184 | {253DD6AB-E4CF-46A7-A9CA-31B26BCFBF2A}
EL CERRITO G 1112779030 | {1F8F52CE-D6F8-4FF1-8C8D-BAA757FE8A8B}
EL CERRITO G 1112BR152 | {7A0FE4A4-8FE2-4A7A-9013-EEA423D246F9}
EL CERRITO G 1112BR196 | {00AF1949-B9F3-40C7-B655-E7207FF7DB49}
EL CERRITO G 1112CB | {C8CD1F48-28E2-4083-A5C4-229D22866F79}
EL DORADO PH 210113362 | {5789A00B-A217-4C31-8B0F-242AC56113D1}
EL DORADO PH 210113532 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
EL DORADO PH 210119612 | {5BE9A1BF-757A-4781-BCE2-C4049CA25F7D}
EL DORADO PH 210119752 | {8256574C-8B3C-4A26-BCE0-BA059359AE5F}
EL DORADO PH 210126000 | {563CD71D-CD80-49B9-9B00-20025334D5E0}
EL DORADO PH 210136764 | {4869E28B-32E6-4BF0-B134-B967D290269A}
EL DORADO PH 210152456 | {20EA6D57-AE8A-4389-B5E9-F8A1FC109811}
EL DORADO PH 210163464 | {9722F7CD-905A-4FAD-885D-DF51D2B7EB29}
EL DORADO PH 2101668674 | {01911214-C578-4D28-95F0-0465555805C9}
EL DORADO PH 21016852 | {550714A4-7303-4842-936D-572C7CE200C4}
EL DORADO PH 2101757474 | {6BCEB58C-CB22-4981-9390-53A109F1FE33}
EL DORADO PH 2101887684 | {45EE85CB-8EDF-4EEA-84E0-238BA75D28B0}
EL DORADO PH 2101CB | {9026688D-0DDE-43F9-BDC1-1D8B37EA23F4}
EL DORADO PH 210219542 | {D823F384-3D02-4716-90A2-5DA25C95DCED}
EL DORADO PH 210219562 | {40FC7F52-2B65-471F-ACDA-BEA2893716D4}
EL DORADO PH 2102542272 | {5B8E36B2-B12B-4F00-8166-D1E50ADA08E5}
EL DORADO PH 21026645 | {876266AC-37EA-414C-92FC-94A2ACD4EB2D}
EL DORADO PH 2102771208 | {06B529E5-576A-4A82-B77A-D8131F4A0F31}
EL DORADO PH 2102927014 | {E3E5615A-B2A3-4BC1-8E71-88BAE49F47C5}
EL DORADO PH 2102CB | {876266AC-37EA-414C-92FC-94A2ACD4EB2D}
ELECTRA 1101105880 | {3B44BEAE-4498-4CF7-B761-D8F28E5D84CB}
ELECTRA 11011238 | {79D3DE13-EDFE-4798-9C48-8D9438D496D5}
ELECTRA 1101175840 | {46D2F232-282F-454C-99DD-05E7F6733AC1}
ELECTRA 110136816 | {7E08659E-39A5-4373-949B-319BDC171EA7}
ELECTRA 110161816 | {467D6E51-4EB9-458F-952D-00686C463F1F}
ELECTRA 11017104 | {21E26CE5-9BFF-45A6-8272-2A9D442E9691}
ELECTRA 1101CB | {0D0FEEBA-0BD3-4962-B35B-0A3278052F45}
ELECTRA 1101L1697 | {21E26CE5-9BFF-45A6-8272-2A9D442E9691}
ELECTRA 110213414 | {BE69B59B-6EEF-4362-A602-62B1E76AF725}
ELECTRA 1102285758 | {3AE63E7E-BC8A-4108-80CA-C0CC877CF92B}
ELECTRA 11024756 | {7D7E61A9-DD15-4C94-B46D-9A82D231AEA5}
ELECTRA 11026014 | {0CAC2312-4B19-49F7-9A0A-4917B3A62B39}
ELECTRA 1102CB | {F6B2F362-298B-4DEB-8C9E-04B14858212A}
ELK 11011260 | {AE0E521E-C3FF-493C-8531-F1F586FF92F5}
ELK 11011272 | {F425053C-9FE0-4926-9CAB-F59A4CB15D1A}
ELK 11011272 | {3D58B5E8-C497-424C-B6D5-A78808606784}
ELK 11011272 | {C106E6C0-BE33-4DE9-BA28-0A0FBC944510}
ELK 11011272 | {62C9F82C-9B7A-4C03-B528-D0CC602C0334}
ELK 11011298 | {EAE624C5-B9BF-4507-A953-B6224BD5618E}
ELK 11011298 | {CC206E8B-BFD5-4BC9-A4B9-F9D20633FB11}
ELK 11011300 | {731B8D8A-0D26-4FAC-B904-5F57E7A23907}
ELK 1101311906 | {818DDDEB-2E77-45C3-96C4-F6724182B49A}
ELK 110137434 | {6922CCC5-514B-4036-B876-FA769B5FF66C}
ELK 11014628 | {894D739D-783F-4BF2-8769-235C809A09C6}
ELK 1101900 | {32CDF0E8-BDA5-4E37-8B42-CD1492E2A580}
ELK 110191336 | {51F158BA-B081-4FAF-A03B-EC569F9C35AD}
ELK 110191336 | {8492A7AF-8A1F-4223-A71C-9C76842CFDD1}
ELK 1101CB | {73B4F2ED-84BD-4C50-9DB1-F9DAD696FAA9}
ELK CREEK 11012002 | {E8F1018C-E626-4FA1-B3DB-30BAFE068623}
ELK CREEK 11012004 | {DECCC899-88C1-4943-B78C-B486089CB76D}
ELK CREEK 11012008 | {49F083FF-CCD6-4656-915A-45D76A900BBC}
ELK CREEK 11012032 | {93B1D857-8A90-4B8A-BADD-0500DBB7E745}
ELK CREEK 11012106 | {9C349921-70C5-4A1B-82FC-D82E641B2142}
ELK CREEK 11012228 | {AC290F88-25E1-47EB-BF8A-1F1AD055C84D}
ELK CREEK 110137334 | {D0CAFA51-0A62-4D26-BA1A-5435FD46CC21}
ELK CREEK 1101915302 | {A3FDB9E9-9009-4CEF-A0DA-9DE8B09BD5D4}
ELK CREEK 110193504 | {00AF6662-643C-446B-915C-CDC0C3350ED4}
ELK CREEK 1101CB | {C805E056-6565-4701-B47E-65A72A694487}
EMERALD LAKE 0401CB | {BF748DD1-7EA7-463E-91B5-1F0876DD9BB0}
EMERALD LAKE 04028858 | {6E19C0A5-86DD-49E4-909F-112A4E9E5B6E}
EMERALD LAKE 04028872 | {18156E3B-3444-414F-97B1-9EC6878D0720}
EMERALD LAKE 0402CB | {A0667D06-51C5-41CE-85EE-7B2260B907EA}
ESQUON 11012054 | {25AD8CDA-2DAA-40D1-AF6C-EC42757AE02A}
ESQUON 1101717130 | {25AD8CDA-2DAA-40D1-AF6C-EC42757AE02A}
ESTUDILLO 0401850884 | {F934F942-DE0D-4D16-AAE7-D119512DF37A}
EUREKA E 110429676 | {B8F6F54B-5EF0-44B9-9BD5-BD98BEED42D3}
EUREKA E 110435934 | {B435E505-091B-4464-AF4F-65421296FB23}
EUREKA E 110498682 | {DD1791F2-46B7-4249-A231-CD7E88BA8BFB}
EUREKA E 1104CB | {6272DCE1-80F1-4C3A-8B1B-A5CE246BB5C1}
FAIRVIEW 2207752858 | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 22078275 | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 220799096 | {55278842-270D-4261-9B21-666405A19DF7}
FAIRVIEW 2207CB | {EA507D40-73C6-4FB5-9309-B2611D605E9F}
FAIRVIEW 2207CB | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 2207M500R | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 2207M501R | {9F1312F5-B448-48CC-A9C3-FC2DE03C4391}
FAIRVIEW 2207M514R | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 2207M526R | {9791B2E1-CE42-470F-873B-7EBAB5F5B113}
FAIRVIEW 2207P142 | {0B7F62BF-A04D-4B9C-AA26-AFE69516CA65}
FAIRVIEW 2207P148 | {61CE2DCB-0D53-494B-8C34-3F4D665DD273}
FAIRVIEW 2207P150 | {0F676DC3-CFF5-456D-B8E2-CAA231B3A90A}
FAIRVIEW 2207P302 | {31523F0A-9FD2-41D0-8A36-117080631D88}
FAIRVIEW 2207P304 | {31523F0A-9FD2-41D0-8A36-117080631D88}
FELLOWS 21031100 | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
FELLOWS 210382182 | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
FELLOWS 2103CB | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
FELLOWS 21041052 | {B4133E9A-3C47-443C-9B0E-8525C1EE28EC}
FELLOWS 21041073 | {837EBEEA-6D15-4355-A56E-82983C8D6DE0}
FELLOWS 21041074 | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
FELLOWS 21041098 | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
FELLOWS 2104274456 | {7F80779C-1619-4C01-8BF5-4EDD2481CA9B}
FELLOWS 210442100 | {D4386F50-ABF5-43E7-8326-09F92A4E0719}
FELLOWS 2104CB | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
FITCH MOUNTAIN 1111424 | {12685307-B1B3-4B99-A51F-5759145ED4DA}
FITCH MOUNTAIN 1111555644 | {D010A5A5-D5D9-4C0F-9746-9A3B4B4F8B0D}
FITCH MOUNTAIN 1111592 | {AA2E97C7-3759-4D9E-BC19-D9ED237F5DA1}
FITCH MOUNTAIN 1111610 | {1D8E3949-43DF-43FB-98A9-8DD711C7AB01}
FITCH MOUNTAIN 1111752596 | {1E79F907-28BC-4BCD-8BF6-A38789A74B9B}
FITCH MOUNTAIN 1111792628 | {89345583-C072-4A34-9FA1-B63C26C09270}
FITCH MOUNTAIN 1111821431 | {85F11AC0-E7F5-415C-8928-2202FEFE7CC2}
FITCH MOUNTAIN 1111CB | {AA2E97C7-3759-4D9E-BC19-D9ED237F5DA1}
FITCH MOUNTAIN 1112CB | {B406A001-5E88-43B9-9966-330465F8E093}
FITCH MOUNTAIN 1113154 | {E5E424DC-C8C0-4A20-B0C0-11A950F19719}
FITCH MOUNTAIN 111324550 | {C4DDBB89-4E15-4D06-A02D-161343869D3B}
FITCH MOUNTAIN 111324918 | {30AC1F79-37C1-4981-9C64-81FC3670878D}
FITCH MOUNTAIN 1113352 | {F0A897EB-747B-40C7-9836-35FB75DF52B9}
FITCH MOUNTAIN 1113356 | {F1192C47-0912-4CBD-BF6E-19925F71459A}
FITCH MOUNTAIN 1113406 | {31A95017-FE64-4D4F-A4CA-39176F23B79F}
FITCH MOUNTAIN 1113443164 | {82F1B323-9F47-4844-B053-6FD72157B262}
FITCH MOUNTAIN 11134566 | {7C0F49AE-FCF7-4330-B22C-F61243651B62}
FITCH MOUNTAIN 1113482752 | {BE29C1CC-62E1-4311-8E3E-30A3FF867046}
FITCH MOUNTAIN 111349826 | {9C1AE994-AAFB-42C4-B159-C85E938EE24E}
FITCH MOUNTAIN 1113677510 | {034C6230-F1B3-44AD-89C0-4E5511DEDDB5}
FITCH MOUNTAIN 1113775992 | {D0DDB5C0-186A-4907-865A-9BE93C7A605E}
FITCH MOUNTAIN 1113824468 | {DEA1978F-46CC-423B-B61B-1E6D21D8F6B2}
FITCH MOUNTAIN 1113CB | {0452ACFB-6610-4670-BD1F-C0548BB4EE02}
FLINT 110138570 | {955D903C-5509-48C2-968E-AF52E8AD5941}
FLINT 110140666 | {F60C4C6E-928C-45EE-B5E3-FE18B260D743}
FLINT 110150960 | {347D4345-ECE4-4101-A340-58299F24E405}
FLINT 1101750 | {070C906B-0802-4429-8F7B-A68007FED9B4}
FLINT 1101958726 | {E5FFB0D3-B57B-4F94-B4AC-8B76666355C5}
FLINT 1101CB | {68DF9E12-6736-4943-BDEF-9FA6962872B3}
FLINT 1102CB | {C6A91D98-B704-457B-84C0-0DADC269F3D4}
FLORENCE 0401110836 | {013CB3A7-7F48-4CCC-AAF7-D8407E0657E6}
FLORENCE 0401CB | {9898F55D-4181-4FB3-A3AA-B13258B3B860}
FLORENCE 0401CR220 | {D87265E8-5674-4799-A45E-7F1EC7B446CA}
FOOTHILL 1101251688 | {2342B1BA-896A-4C52-9E39-F87AA4527061}
FOOTHILL 1101549904 | {BEF6045A-3518-436C-A876-62625F5A4B60}
FOOTHILL 1101549904 | {5DE69153-3C7C-4310-A10D-0098A2A3216B}
FOOTHILL 1101549904 | {2710935D-955C-4B3B-AB55-13FA5CE7C745}
FOOTHILL 1101645910 | {DA93CD43-4632-46CD-9EF3-906DC0AD12DA}
FOOTHILL 1101CB | {A0154153-BF56-4706-9955-FEBD0CFAAAA7}
FOOTHILL 110299432 | {7C9F6E98-6AD1-45C0-AA12-C5A39FC092A4}
FOOTHILL 1102CB | {CF5272DC-8419-42E3-A72F-BD395166C5DF}
FORESTHILL 11011802 | {9A3F5548-F595-4F3F-89FC-9574388096DE}
FORESTHILL 11011820 | {D7E3765B-F7D8-4BEF-8206-669D15220FDF}
FORESTHILL 110137238 | {05132EF1-E962-492C-8CE4-DD542C3B3D15}
FORESTHILL 110150486 | {FE85142D-4AEA-430F-BD77-45CC919584AA}
FORESTHILL 110175340 | {8414F562-3617-4BAD-BBB4-DAC100815794}
FORESTHILL 1101890670 | {ED9435F9-E06B-4A98-B053-EB0C1DC8369F}
FORESTHILL 1101CB | {ED9435F9-E06B-4A98-B053-EB0C1DC8369F}
FORESTHILL 11022106 | {01403AE6-90D4-4B19-983B-B7AD8BDC29F6}
FORESTHILL 1102359542 | {27195F6D-400C-4416-B7C7-104E52ECD248}
FORESTHILL 1102CB | {D5AE9DC8-C124-4C49-BB35-C0CDE45BC05E}
FORT BRAGG A 11013100 | {0D62503E-67CB-4A8E-BC3C-093230B8FF31}
FORT BRAGG A 11013113 | {C40FEC6C-4399-4FDE-8ABD-E729D917D61E}
FORT BRAGG A 11014622 | {FD379B27-6785-4E43-84D1-7E22C4EB286F}
FORT BRAGG A 11014698 | {C40FEC6C-4399-4FDE-8ABD-E729D917D61E}
FORT BRAGG A 110195294 | {68CC0E2F-7024-44BE-85E9-7639B7540AB9}
FORT BRAGG A 1101CB | {34DFDDBB-39B7-422C-B7C0-767BF9731AB2}
FORT BRAGG A 11021226 | {75E57175-6FC2-4C18-9858-49FEBB55AE91}
FORT BRAGG A 1102265870 | {E0FAB4E0-B6D5-48CE-BF78-A57BBF22B01A}
FORT BRAGG A 110231304 | {BF12DE8B-4E1C-4761-B900-F5DD3C822515}
FORT BRAGG A 110233064 | {13E2F68D-5FE0-429F-8E83-F4D9D6BCB638}
FORT BRAGG A 110235592 | {88ABC052-C1CA-454C-9520-7292289269D5}
FORT BRAGG A 1102416218 | {7A8B738E-E99E-4EA8-B90B-160DFB70847D}
FORT BRAGG A 1102416218 | {88ABC052-C1CA-454C-9520-7292289269D5}
FORT BRAGG A 1102418 | {2F10EC8A-D66D-41A3-A96A-C091A52D1815}
FORT BRAGG A 1102667996 | {267610AC-9BEB-429F-830E-E78C6931DCD3}
FORT BRAGG A 1102816 | {DCB2091F-52D0-405B-8DDE-82750DB61471}
FORT BRAGG A 1102956 | {63294CD0-4D7E-4FB1-9784-991B87B370C8}
FORT BRAGG A 1102CB | {A11A44BE-5FF6-4EAE-B643-DC3914767492}
FORT BRAGG A 1103CB | {C8B7B79F-9539-45C9-8977-9A8FC5806A25}
FORT BRAGG A 11041316 | {BC4F0196-621B-4CEE-9F22-55FAA9EB12A8}
FORT BRAGG A 110436526 | {741F819D-F84A-48D0-B917-155D72B8DC6A}
FORT BRAGG A 11044690 | {9AB01B94-B2A5-4A8A-9109-9F42C093DB3E}
FORT BRAGG A 11044690 | {510564D1-DEEF-4962-A1E8-3812661AD494}
FORT BRAGG A 1104529076 | {ED095E9E-F3A0-4C4B-ADA3-9E3DFB5A9FCD}
FORT BRAGG A 110465894 | {DDA08885-FEC3-49A8-9C1B-A5CDAFE21444}
FORT BRAGG A 1104872358 | {F09AC1B9-9514-473B-B8B0-A2B230C8B557}
FORT BRAGG A 1104CB | {743824B8-B7E6-418C-AF37-30E4E0572D08}
FORT ORD 1101131442 | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
FORT ORD 11019516 | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
FORT ORD 11019518 | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
FORT ORD 1101CB | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
FORT ORD 210531972 | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
FORT ORD 21059140 | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
FORT ORD 2105CB | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
FORT ORD 210633694 | {95AB47FE-6B9D-4A04-9C44-EED36F1BA13B}
FORT ORD 210637286 | {9AA16F48-39A4-4006-910E-3E37752DF955}
FORT ORD 21069136 | {AB7BD794-6A54-404B-96D0-00596CF55B93}
FORT ORD 21069138 | {2DB40D5F-4BD1-40A5-9FBF-211C9D3CC0A4}
FORT ORD 210695186 | {0139AD78-6D54-4C40-B88F-B8F196A0FC71}
FORT ORD 21069656 | {8BA4213A-D34B-4B87-B8F6-E146FF0B7281}
FORT ORD 21069658 | {6B4BEF51-729A-495B-8FC4-CA82105C9822}
FORT ORD 210736596 | {121773FD-4C4B-4842-BF5D-136BCB9BFB8D}
FORT ORD 210779670 | {018C3E1E-E9D7-4770-B296-F1B4D7801EF4}
FORT ORD 2107CB | {5AF19FAC-D5B1-4A0E-9483-EA04C351FFDD}
FORT ORD 2108CB | {AF7D3D91-B816-4BC0-A0EF-CC9A68E30A8C}
FORT ROSS 1121124 | {228A6257-66FD-4F4F-AA34-7D22FE084DBC}
FORT ROSS 1121134 | {D2E66D36-59AC-4BEC-BEE9-31C660B6B4ED}
FORT ROSS 1121204 | {62984F08-7842-4FBA-8D96-707DCA078F65}
FORT ROSS 1121204 | {031CA341-2C0B-4194-9FCE-C18FD57B6895}
FORT ROSS 112137326 | {56EC8BE0-B402-4A7D-9076-C44EBD9A9DDD}
FORT ROSS 11214614 | {36E821CE-0F96-4DE1-8152-1087521FEC6A}
FORT ROSS 1121560 | {C44E173D-32C1-4900-92A5-AD54BFE2000C}
FORT ROSS 1121612266 | {F813F206-BF9E-4739-A94F-434D2CFC229C}
FORT ROSS 112170288 | {19BB688C-7539-4331-8ED9-2B0221333B05}
FORT ROSS 1121CB | {6432AE5E-F371-470F-8E71-1BA304A7A433}
FORT SEWARD 11211690 | {E448EB4C-7ECC-4C43-A720-97024B873C96}
FORT SEWARD 1121CB | {F2B197B6-F439-443B-9926-76B11912B9BA}
FORT SEWARD 1121CB | {9D061223-5B52-4134-9A27-9EB1E4A74BC8}
FORT SEWARD 1121CB | {F3EC175B-7845-4CA9-AB09-DEC2A3B40256}
FORT SEWARD 1122CB | {DDBF5221-9BD5-419F-9A17-E9260A89D7CD}
FRANKLIN 1101P132 | {6376A175-D3DE-423C-8B8A-9B6318316FA7}
FRANKLIN 1101P138 | {DB131498-A71D-4A26-A77E-BBAB941A8DB9}
FRANKLIN 1104615788 | {EC1037DF-9D9B-425C-812F-13D2FBDE6247}
FRANKLIN 1104CB | {DDFFEADB-3F2B-4296-80F5-9B1536EA3D55}
FRANKLIN 1104P136 | {F15BB3D1-0A60-48BB-96E4-777A07B496BE}
FRANKLIN 1104P146 | {4B04C7BE-F037-4E43-AD43-455E3B1A9C74}
FREMONT 11041516 | {CA0B1D0C-E4E8-4109-942A-39C0D83AA3E4}
FREMONT 1104645342 | {5FF4B67A-802C-4B9E-AA95-209BF5DD22D4}
FREMONT 1104CB | {62124451-9B9F-46EB-B50A-534B1B0CB257}
FREMONT 1104MR339 | {02184DCE-4986-4759-8E54-71AE9F6D44F7}
FREMONT 1104MR584 | {B59BCFB8-3D30-441A-916B-9810D227F102}
FREMONT 1104MR707 | {62124451-9B9F-46EB-B50A-534B1B0CB257}
FREMONT 1109MR735 | {E8F7F7CC-6E45-4B77-9E47-6A6BC522B971}
FRENCH GULCH 11011464 | {CEDB41D0-D0A4-4C87-B076-5057F893A246}
FRENCH GULCH 11011892 | {EEFD67FE-817D-4F21-AFBD-03D493187270}
FRENCH GULCH 11012905 | {CEDB41D0-D0A4-4C87-B076-5057F893A246}
FRENCH GULCH 1101CB | {20DFFDEF-5135-4324-A022-CDDC3E81B3A6}
FRENCH GULCH 11021462 | {673B1BD0-3EFA-4599-AB2C-B37C28829526}
FRENCH GULCH 11022902 | {CBEFA52C-F905-473F-B9BB-602279DBF4B7}
FRENCH GULCH 1102CB | {68ED899E-4033-413B-A72A-EE83BDC8B804}
FROGTOWN 170113412 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
FROGTOWN 17011623 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
FROGTOWN 17016807 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
FROGTOWN 1701CB | {CC00F970-8F13-4247-87D9-81AC67764BAD}
FROGTOWN 1701L3361 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
FROGTOWN 170211212 | {275411B9-F65E-4C2D-AC92-04E91C75A810}
FROGTOWN 170212282 | {3C80F4C0-E9A6-46C9-A594-5586FAD2CDE6}
FROGTOWN 17021573 | {7D119895-6544-4FC7-A1BD-CC0A5D84976F}
FROGTOWN 1702204480 | {A12EF9F2-A626-4D54-A592-A0BB35CB6549}
FROGTOWN 1702224708 | {35EE754C-7E3A-4C6F-81A6-D14B057757B0}
FROGTOWN 1702307998 | {89CC7A11-127F-43C2-800C-EB67E4FC6948}
FROGTOWN 170232556 | {9BE6D037-BD8E-46AF-A32B-7F2BB00D9E6A}
FROGTOWN 170236870 | {11F38DA8-6582-44F5-A0BF-18D25BB5EB9F}
FROGTOWN 170236870 | {94EE7076-462E-4300-BB9C-E1B2A1AE599F}
FROGTOWN 1702592404 | {2DE456BF-71ED-4278-9F9A-6A3D0E617A94}
FROGTOWN 17027108 | {3530973A-E1ED-42D6-80CA-474C64476B90}
FROGTOWN 17027134 | {0486726A-698F-459A-9224-3E1921E2AC68}
FROGTOWN 1702737236 | {F66F5E9F-01CE-4986-95ED-652F7B3AA4E8}
FROGTOWN 1702737236 | {F0E1E0FF-88A1-4ACA-9BA3-065AFC2B6B60}
FROGTOWN 1702739858 | {1A9CCDAC-B50D-483B-87EA-5C0A6CCF7B4E}
FROGTOWN 170274648 | {DC88F071-ABF2-47A3-B14B-581D2315B4AC}
FROGTOWN 170274648 | {7D18EBC6-B40D-40A3-A41D-AD9B31488058}
FROGTOWN 170274648 | {C985F098-6ECF-4C69-B902-1B5157262ED5}
FROGTOWN 170275252 | {7D119895-6544-4FC7-A1BD-CC0A5D84976F}
FROGTOWN 1702812366 | {4CE434B8-E02D-4920-A230-5B04B8D42C75}
FROGTOWN 1702815616 | {AC647AA8-B527-4875-A38A-FEBD0757B10B}
FROGTOWN 17028482 | {DEF24EAD-1BE2-4F6F-8D2A-6151341F3B41}
FROGTOWN 1702CB | {646B02DA-833B-4BEB-8A59-9FDCAF947841}
FROGTOWN 1702L5407 | {3530973A-E1ED-42D6-80CA-474C64476B90}
FRUITLAND 1141200856 | {549199A2-4261-43E8-8700-8DDEE28DEA6C}
FRUITLAND 114137410 | {CF682344-0C1A-411D-B173-CAE04AD6EAA0}
FRUITLAND 11413902 | {986A9626-2000-4CDA-907D-688340426BF2}
FRUITLAND 1141866852 | {7AAAEF20-BCE1-42D0-9686-CF0447F71CAB}
FRUITLAND 11418860 | {901979A9-33A5-4FBB-9019-2CBDDF98F849}
FRUITLAND 114195324 | {270A551E-565A-4C78-BA5D-427CE889B75E}
FRUITLAND 11422006 | {0E6F84FB-9664-4CC2-ABC9-E723037587E4}
FRUITLAND 11426054 | {4DE5CD9A-1BC1-4D9F-A13E-0336C2BFEF7C}
FRUITLAND 11426064 | {4A1EC5D3-CF7E-4E3A-B115-9A4757B7DAC6}
FRUITLAND 1142615540 | {C9D02877-D683-4E00-8203-11814AA4CD46}
FRUITLAND 114263170 | {BDFC6231-C003-4BB6-9C95-EEAEA882FC5D}
FRUITLAND 114263170 | {69FD4992-2A22-402B-ACAC-E090559F2AEA}
FRUITLAND 1142899734 | {84FB064E-BD98-4DA8-AF4F-2B45B0138D7B}
FRUITLAND 114293234 | {F2F5CD46-ED54-485C-8E9F-F1D6186FA89B}
FRUITLAND 1142CB | {C08075C5-E7BA-4353-AF25-7A00C76C5CA3}
FULTON 11011734 | {30FC3806-038C-4AC3-A393-91BFE1889F67}
FULTON 1101CB | {30FC3806-038C-4AC3-A393-91BFE1889F67}
FULTON 1102258281 | {09E88888-5AC3-4010-8136-EE66FDCF2B20}
FULTON 1102287172 | {1B09A511-4056-470A-B00D-4FB4522380B2}
FULTON 11024334 | {F2C72F8A-06E0-42ED-81D6-01D05809B312}
FULTON 11024522 | {4783296A-689D-4C7A-9F23-C015688BF301}
FULTON 11024994 | {EA9B2479-0C7B-4A59-82AF-47AD3E8F521E}
FULTON 11025102 | {A7116264-DEE4-49AB-8F9D-DDEB0877D031}
FULTON 110257686 | {08567963-8339-4FA1-9F78-3A951553BB03}
FULTON 110258990 | {D9F1E4D5-6C65-4B74-B28E-1D1E2528E5E8}
FULTON 1102885254 | {2F7CFFF4-26D8-43F1-AB7C-C43D0BC5D438}
FULTON 1102904058 | {A7116264-DEE4-49AB-8F9D-DDEB0877D031}
FULTON 1102CB | {6ABCE308-047E-4F2E-99AB-65F7E6BEAD99}
FULTON 1104466 | {AE97AA30-6595-4674-A3E8-E3C81CE235CD}
FULTON 11045016 | {AC56E29F-28CE-4D76-8621-1CA9BB136C25}
FULTON 1104CB | {86598FBB-5AAE-49A3-956D-D4079C4EFDE4}
FULTON 1105142 | {63777790-64ED-4263-AFF5-02757B725BB7}
FULTON 1105172 | {63777790-64ED-4263-AFF5-02757B725BB7}
FULTON 11054106 | {957874C2-FA06-452C-924E-A5E4C30E68F3}
FULTON 110555802 | {957874C2-FA06-452C-924E-A5E4C30E68F3}
FULTON 1107126742 | {C134E3B9-E693-4C16-B3A4-BFE77C3B9516}
FULTON 1107145720 | {6604208B-F35A-44BE-998D-E714E06DE284}
FULTON 1107214 | {82FFCF9A-29C9-4CD0-A5CE-AFFBFF95F55A}
FULTON 110746958 | {01F2557C-4641-4BA6-8DDF-FA4264339C1A}
FULTON 11075058 | {72AE5EDE-AC15-4265-AF32-67B0F370C217}
FULTON 1107604 | {E553BB4B-1179-4653-BCDF-D0DE748C3124}
FULTON 110777670 | {5B55A465-FAC4-48C8-B9A5-F80EA4DBED38}
FULTON 1107914380 | {6CE1CBF7-A8F6-461B-83E4-323985F1F354}
FULTON 1107CB | {72AE5EDE-AC15-4265-AF32-67B0F370C217}
GABILAN 1101270626 | {6D5B17B5-960C-48B4-806D-BF9DA1A8A3B0}
GABILAN 11013034 | {D9D7498B-EECD-46C9-B5F7-8D9ED4F7E924}
GABILAN 11013090 | {43462865-0ED2-47A6-A8E8-8B52D18F5577}
GABILAN 11013722 | {6D5B17B5-960C-48B4-806D-BF9DA1A8A3B0}
GABILAN 1101460414 | {0008E3B5-1496-4F6F-834B-CA7B37853F9B}
GABILAN 1101566352 | {0B568E58-6FDD-401E-8368-A329B6DA6B93}
GABILAN 1101989608 | {E7781237-9688-49BD-8E68-B925FC8E3926}
GANSNER 11012006 | {AD16C82F-076B-43F6-B112-51D5058EB123}
GANSNER 11012424 | {7FF9C2B4-7885-497B-BE5B-64337D7948AA}
GANSNER 1101336664 | {13627031-EE44-4823-A048-AA36CB9BE013}
GANSNER 1101372132 | {EA937CC6-E132-4325-A59D-A7FEA701DEB9}
GANSNER 110137550 | {2D495744-1EEC-4B5A-AB6C-8BE5D83F4E62}
GANSNER 1101489276 | {72504F1A-5BCF-43C4-ADF1-0100A2C7CFD0}
GANSNER 110152664 | {ABF9C0D8-FB4B-45D8-8766-B92175021507}
GANSNER 110152664 | {98C593A0-E92A-4B31-9CFB-8318376E6172}
GANSNER 110152664 | {248F09B8-1D5D-4034-96B7-C372BB4594AA}
GANSNER 110152664 | {837222F9-D8A2-4260-8BFB-B6E14FA07798}
GANSNER 1101590690 | {2EBA9C84-1564-4E97-B683-C3C5B09E3911}
GANSNER 110199388 | {13627031-EE44-4823-A048-AA36CB9BE013}
GANSNER 1101CB | {40645203-FB29-4536-8849-C6C7781BFE2D}
GARBERVILLE 11011514 | {7F9C85EF-487B-454C-8489-CDBA87D32E67}
GARBERVILLE 11011604 | {905A282A-4E87-42B0-8385-244613D03E1D}
GARBERVILLE 11011750 | {08393BA3-C925-468F-82DD-D9087C4038E5}
GARBERVILLE 11011770 | {BBD56973-ABAA-4951-A1EE-E863C47010B2}
GARBERVILLE 11012026 | {E7486DD4-0A7D-467A-B7E3-9401480FC5B2}
GARBERVILLE 1101323694 | {624B3FD3-11BE-4D35-879D-7A58EF854DA3}
GARBERVILLE 110139524 | {4FAFA82B-3330-476C-B978-ABE18A7516EA}
GARBERVILLE 1101438596 | {39301543-F3C9-446A-ABF8-E960F80CEDFE}
GARBERVILLE 1101574630 | {7F9C85EF-487B-454C-8489-CDBA87D32E67}
GARBERVILLE 11016014 | {B179FF8C-723A-4A8D-97B0-90D4F52587A2}
GARBERVILLE 110197300 | {BA71994D-6A0B-4F0B-9E44-79C1DD5F42DD}
GARBERVILLE 1101CB | {E1AC8377-8E8C-4414-AED8-68291E68F4CE}
GARBERVILLE 11021510 | {1339ADD4-8465-4C5F-ADF0-25D79054621F}
GARBERVILLE 1102176634 | {221BC5D9-51C0-467D-BFB7-19AAD7C5E6CD}
GARBERVILLE 11022010 | {0FD31FD2-8045-433E-9D12-C8669CFF0383}
GARBERVILLE 11022124 | {4AC60F3F-45CC-4080-B7C8-2A403EC32A74}
GARBERVILLE 11022500 | {37DB383D-2CA0-40C2-9028-FCF646539713}
GARBERVILLE 11022540 | {09BB38E4-7FE7-4BD1-9CFE-F62698521734}
GARBERVILLE 1102343364 | {221BC5D9-51C0-467D-BFB7-19AAD7C5E6CD}
GARBERVILLE 11024744 | {5647EDBD-9C48-41AB-BE66-016C6AAA1D29}
GARBERVILLE 11024744 | {221BC5D9-51C0-467D-BFB7-19AAD7C5E6CD}
GARBERVILLE 110256048 | {BF5AD074-5FDE-42FF-9EE4-EC1E7EF14392}
GARBERVILLE 11026084 | {0A529EA6-6476-4FE6-9A4C-9E2DBC5F560C}
GARBERVILLE 1102802246 | {DAE65BBD-586B-4687-A386-299C8E68232F}
GARBERVILLE 11028652 | {56012ECF-3863-4B00-9D44-45818E54BBA2}
GARBERVILLE 1102CB | {76599403-EF2F-43B7-895E-85F706D26E36}
GARBERVILLE 1103CB | {81BF210B-E399-451E-B158-93FB561813DD}
GARCIA 0401666 | {2B626DC9-13BD-4F58-BFDD-9C1FE143AC91}
GATES 1106755338 | {BD3133DA-EDF7-4B1E-B188-9C3D48C9C62F}
GATES 1106879496 | {3E771B8A-A2BC-4AF3-89F7-B4D332DE2C00}
GATES 11069090 | {0403AD0A-8957-4413-B5CA-AB406F66F7FB}
GATES 110692202 | {0403AD0A-8957-4413-B5CA-AB406F66F7FB}
GATES 110699914 | {0403AD0A-8957-4413-B5CA-AB406F66F7FB}
GERBER 11021560 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
GERBER 1102190339 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
GERBER 11023771 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
GEYSERVILLE 1101122 | {69EA27A3-0D2B-4A2D-A229-63A3090F6AF6}
GEYSERVILLE 1101166 | {DC4595FD-6B3F-430F-8A6B-C07BE18B58D6}
GEYSERVILLE 1101354 | {8735F018-B7F6-43BE-A1D1-DAC1AC58E1A0}
GEYSERVILLE 1101354 | {02D0A0CA-B431-4FB2-AF18-E6305A42917F}
GEYSERVILLE 1101354 | {77D178FA-A5A9-4C63-A9B3-CE34D67D6A01}
GEYSERVILLE 110135492 | {A4A124EA-8920-4709-8090-23E3A2E000DC}
GEYSERVILLE 110137454 | {8E06DD08-111B-4D73-B845-1ABBADC77B32}
GEYSERVILLE 1101406798 | {EC9348DB-6FAC-4BC4-A3C0-6B6419696175}
GEYSERVILLE 11014570 | {7BF9631F-F2B9-4D9F-A7A1-8FB9FBCDDF84}
GEYSERVILLE 1101480 | {B067E8FC-275B-40E3-B858-2220AFBD2EF2}
GEYSERVILLE 1101482 | {FC698F49-08CB-4375-B278-3C062280B4C5}
GEYSERVILLE 1101711966 | {1896BE4A-1AA3-4F21-93D4-ED4B47D95FC3}
GEYSERVILLE 110179788 | {CD516753-E346-488C-8A28-4021B3A7E490}
GEYSERVILLE 1101975350 | {1C85BACB-B649-4EAE-8382-1B9833570386}
GEYSERVILLE 1101CB | {377EDE62-95BF-4247-B5CE-2FDAD489198A}
GEYSERVILLE 1102220154 | {4D770C11-A9C0-4B50-BC88-1E94F5926B75}
GEYSERVILLE 1102235124 | {4D75EBF2-65F6-4895-9B4E-AAD6D6F48D1D}
GEYSERVILLE 1102274 | {F335CD9B-C6EC-489A-8E1A-57248916AA35}
GEYSERVILLE 1102331444 | {D1475177-49FD-4D65-8D0F-817A6104925A}
GEYSERVILLE 1102350 | {95D38DE9-E8FF-48E8-A441-5433C36DE660}
GEYSERVILLE 1102429530 | {6B65A809-12E3-40D6-89FF-84D72C02075E}
GEYSERVILLE 1102484 | {1E362916-4E6D-4E8A-A229-F0750B3C8096}
GEYSERVILLE 1102501402 | {3DF9989A-5EFA-4A4A-AF4B-080E167575C3}
GEYSERVILLE 1102504260 | {BA062BA2-FAD7-4707-A9BF-0F5097E508D7}
GEYSERVILLE 1102522 | {B09D42AC-0CDA-4ABD-917A-C98377E7425E}
GEYSERVILLE 1102522 | {B7726FE8-A35B-4883-A20B-6CA79C5DB82B}
GEYSERVILLE 1102522 | {C28A65D7-37D3-4F6C-9C48-AF74AD2858BE}
GEYSERVILLE 1102537096 | {1CBBA641-695F-4908-8A3F-72BA5ADCB13F}
GEYSERVILLE 1102548206 | {61A40993-1799-45E2-A875-A7E8542BA751}
GEYSERVILLE 1102735600 | {1793E18B-A8B5-4A05-B096-C6FF30B6AFC8}
GEYSERVILLE 1102756 | {5A3AA98B-24A2-41A0-8E61-B5A0B5E2F3E7}
GEYSERVILLE 1102776178 | {082C86BB-EE1F-40DF-94C4-4FB1575D2884}
GEYSERVILLE 1102785626 | {BD048B94-FDE8-4EDB-AB8C-2693863E8CA6}
GEYSERVILLE 1102868292 | {FC4A4168-3718-4179-B688-0392741460DB}
GEYSERVILLE 110289714 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
GEYSERVILLE 110289714 | {225505FE-91AC-45A2-A8F4-D9DAE66F2063}
GEYSERVILLE 1102904170 | {012EDF18-DBAC-4496-A5CF-592EEBEC324C}
GEYSERVILLE 1102CB | {B7169D14-D576-4EBC-83AD-DD429DE5E777}
GIRVAN 11011330 | {614F599C-8E41-4F43-93F2-0A1EC10532ED}
GIRVAN 11011636 | {2A2FAB19-EBE2-405E-9DCE-8FB9750FB831}
GIRVAN 1101257982 | {FD332C17-8990-415F-9100-8E4ED8DC0A1B}
GIRVAN 1101323094 | {70CD880F-1DDD-4F51-9E9A-370D1CA1A5D7}
GIRVAN 1101409530 | {8B1F4C30-3A4A-4A19-A6E9-5A1F7F44786A}
GIRVAN 11019732 | {AC347828-D402-4D52-85C5-6B49A3874218}
GIRVAN 1101CB | {DEF16B60-E22C-4BAF-BEFC-F4B0E169B38F}
GIRVAN 11021028 | {F99AC090-1DE1-40AB-890A-9A8208858415}
GIRVAN 1102212096 | {2CF3750C-AFAA-443E-A704-CD883AA64DE4}
GIRVAN 1102259230 | {1E5A3AA1-D2B5-4DA2-AE6A-652FB4FE0C5F}
GIRVAN 1102296428 | {88D9B85D-5E99-45AD-AA48-D39463FC6691}
GIRVAN 110255307 | {F8758432-B450-4943-97B4-52B80EF2F512}
GIRVAN 110280726 | {1C2C814F-78D0-401D-8386-69906E2875F3}
GIRVAN 11029012 | {10010FC4-3D49-44D1-8CB1-63E2C5CA1480}
GIRVAN 1102CB | {F8758432-B450-4943-97B4-52B80EF2F512}
GLENN 11012012 | {79FEFA25-425D-4CA0-8714-2AC25C0E088A}
GLENN 110137496 | {AAF1B526-755B-4552-86BF-96B7CE58000B}
GOLDTREE 1105551904 | {FF54465D-5764-4C87-9FA1-2FCC27FF3FF8}
GOLDTREE 1105588830 | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
GOLDTREE 1105912920 | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
GOLDTREE 1105944608 | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
GOLDTREE 1105CB | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
GOLDTREE 1107477878 | {E099D2A0-66BE-4A41-88A9-690DFD5F2504}
GOLDTREE 1107CB | {011DEA9E-857C-400B-8F07-19E7424464B0}
GOLDTREE 110814115 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 110815803 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 1108939400 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 1108961060 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 1108CB | {0CEB70F5-2209-4B8B-BEA6-B7EBAFD3DEEB}
GONZALES 11013094 | {B8E5DB63-2FB3-475E-A16D-C9AC460D90A7}
GONZALES 110165704 | {71137ABD-E3E9-4FF8-AD99-B6537D8F36C1}
GONZALES 110422418 | {33EF8994-00DA-4C8F-AF23-8D41C5EB4753}
GONZALES 1104415382 | {1F605782-8F30-4773-8038-34124B7BD9C5}
GRASS VALLEY 11012208 | {15B21A5E-7758-402F-AB04-357FA8BC8C24}
GRASS VALLEY 11012766 | {9368A9FD-8241-4EF3-80EC-43B66D341976}
GRASS VALLEY 1101750804 | {A36BB2C2-2D85-4DEA-B11A-BCA9D91106FD}
GRASS VALLEY 1101CB | {A2EB9A1B-29CB-4BF2-A3D8-CB94BC2FB584}
GRASS VALLEY 1101CB | {B0F41A34-F762-41B4-ACDB-9C11F27E225A}
GRASS VALLEY 1102CB | {343B25CA-8FEF-457F-8025-88904C29692A}
GRASS VALLEY 11031700 | {34D5CE89-BFD0-4BEE-AD2A-0183175AD2BA}
GRASS VALLEY 11032110 | {B3488AFC-B0D0-44AE-ACC7-3FB60ED8C1AA}
GRASS VALLEY 11032180 | {5AF8F290-EBD8-4203-A9EE-DEB7B6BE68A5}
GRASS VALLEY 110358498 | {F4833127-5C39-470B-A2CB-DF77602CD67E}
GRASS VALLEY 1103CB | {EB087661-42A5-46E0-BB53-1DC1A49FC6AA}
GRAYS FLAT 0401904916 | {F832BEDC-DD34-4E26-9782-93FD35112F64}
GRAYS FLAT 0401CB | {0DD81C15-0750-470B-8405-5D786A5E8465}
GREEN VALLEY 210110976 | {5C8DA4CC-DB0C-4E65-BF7D-024442DE4F36}
GREEN VALLEY 210111054 | {D718FE21-E107-484D-ACA1-7018B98129C1}
GREEN VALLEY 210112106 | {C8470ABD-D047-4E6E-A601-35B08D6D1BD2}
GREEN VALLEY 210112130 | {A0B73F98-66D4-44F0-A30D-DD6726111A66}
GREEN VALLEY 210112824 | {4709726B-1243-485D-89BF-CB13962C950E}
GREEN VALLEY 2101128618 | {47221F99-4C03-4459-B587-C3379C27406E}
GREEN VALLEY 2101135762 | {E176FCE3-EE7E-480F-BF55-388C6C19C1B5}
GREEN VALLEY 210136820 | {1058939C-63D6-4E6A-BE26-51405BD3A77F}
GREEN VALLEY 210136820 | {0EBE586C-72F8-4C18-81D3-2D4BBB15CB1F}
GREEN VALLEY 2101380922 | {167D6A57-A795-4EF1-A1DB-E61FA7A54614}
GREEN VALLEY 2101454176 | {E90E3E0E-A1FE-49A3-B997-86202410CB3E}
GREEN VALLEY 2101509068 | {CDC61CD0-0FE2-4F7D-9501-2D67363E1B49}
GREEN VALLEY 21016625 | {C8470ABD-D047-4E6E-A601-35B08D6D1BD2}
GREEN VALLEY 210182789 | {5C8DA4CC-DB0C-4E65-BF7D-024442DE4F36}
GREEN VALLEY 210190860 | {67D84718-A6F9-4E7B-97A1-8A07F4A83E01}
GREEN VALLEY 210190860 | {6F3DC4C6-B30E-4E87-89BD-977051E850B3}
GREEN VALLEY 2101912058 | {B0D88627-777F-40AF-8B34-573084F90AF3}
GREEN VALLEY 210310932 | {71F18CE4-D284-4752-9621-5F4A7D3D2F8E}
GREEN VALLEY 210312656 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GREEN VALLEY 2103478624 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GREEN VALLEY 21034929 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GREEN VALLEY 21035140 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GREEN VALLEY 21036661 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GREEN VALLEY 210397492 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GREEN VALLEY 21039959 | {71F18CE4-D284-4752-9621-5F4A7D3D2F8E}
GREENBRAE 110182270 | {FE2E59EB-BA50-4D05-88C6-174D3F07D4AE}
GREENBRAE 11021254 | {343DAC73-DC1A-4C06-8C35-1C7245E7BB91}
GREENBRAE 110276992 | {AEDCB032-1AC1-4F9E-A5A8-36B12E3777AB}
GREENBRAE 1102CB | {AEDCB032-1AC1-4F9E-A5A8-36B12E3777AB}
GREENBRAE 1103343788 | {F008DFF3-E06F-4A9D-BE65-7AFC32973FC7}
GREENBRAE 1103718674 | {B4FDB7D9-192B-4627-9F31-9C96B3E85045}
GREENBRAE 11037315 | {9E4C5477-E966-43D5-8E24-BB781F7AED7E}
GREENBRAE 1103CB | {9E4C5477-E966-43D5-8E24-BB781F7AED7E}
GREENBRAE 1104107508 | {3BE2CA95-ED55-4C1C-B1D4-36EDBF365BB4}
GREENBRAE 11041302 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
GREENBRAE 1104300 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
GREENBRAE 1104751 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
GREENBRAE 1104751 | {E460C92A-0C1B-4EE6-9D61-6E0297E7830B}
GUALALA 1111289822 | {CEF9E817-A890-4D55-A76F-8D46E6790C4E}
GUALALA 111135562 | {FD400AC6-30E3-4FB9-965E-48825707A861}
GUALALA 1111402866 | {DDD68DD3-36B2-4580-BE12-D96815D31D50}
GUALALA 1111445166 | {69ECBFC6-9041-42D6-B70D-8E6BF5F8976F}
GUALALA 1111887180 | {F1237B34-AE98-483F-8E45-6E7314FDEDD2}
GUALALA 1111CB | {73132ABD-89F1-46DF-ADF4-0148C2A7C9B0}
GUALALA 11121294 | {6177229C-DB60-448B-B309-D4C2F1A2330C}
GUALALA 111223444 | {CAD50E3B-E1AA-4BD0-B856-9F05498FC7E2}
GUALALA 1112662 | {4C471213-8F1E-4783-A9BD-8E19C8202DBB}
GUALALA 1112CB | {8A730939-42F5-47D3-8D16-1FB3EEA2BAEF}
GUSTINE 110264140 | {643C42D4-351A-432E-B651-277EC983F63B}
GUSTINE 11026926 | {70573641-CA59-4111-9B6C-A1864C98CC90}
GUSTINE 11029100 | {FC926262-8B0E-4F06-BF55-D74DA7FE90D8}
GUSTINE 11029628 | {FC926262-8B0E-4F06-BF55-D74DA7FE90D8}
GUSTINE 1102999258 | {09DAC264-33D4-48C8-811A-344E9E34B63F}
HAAS 210110954 | {9258B2D2-A536-49F7-80AA-889F46A8DA16}
HAAS 2101CB | {60CC4C1A-8161-40D9-B812-120C86651584}
HAAS 2101R2640 | {918E67A3-B8AA-4550-95DB-73823B8E223E}
HAAS 2101R2770 | {FE71AAF6-F6E9-485B-A3C2-10412CBC3ED0}
HAAS 2101R4610 | {58CC59BD-D32A-413F-871C-B048589E5421}
HAAS 2101R9223 | {FE71AAF6-F6E9-485B-A3C2-10412CBC3ED0}
HALF MOON BAY 1101125326 | {DA4B3A2D-36B3-42B6-B1B8-A06A1F335036}
HALF MOON BAY 11012500 | {75B0B322-68D2-4160-BC4E-E90092A2B4DE}
HALF MOON BAY 110148868 | {0C9E66AB-FF7E-4958-AED9-234BEE09CC6F}
HALF MOON BAY 110155210 | {DA4B3A2D-36B3-42B6-B1B8-A06A1F335036}
HALF MOON BAY 11016369 | {DA4B3A2D-36B3-42B6-B1B8-A06A1F335036}
HALF MOON BAY 1101818874 | {94188B54-65D0-48E4-B281-167ED6270B8E}
HALF MOON BAY 1101821698 | {4C57C032-9144-4113-A71E-DB2019EE4077}
HALF MOON BAY 1101857728 | {9D907261-0F86-4269-BCD0-948CEEC70925}
HALF MOON BAY 11018902 | {C41F4E5E-7BB3-4EF6-9D85-B639632114A4}
HALF MOON BAY 11018940 | {2DBAB1CF-D3D1-4CC0-A406-0CDA12AB2548}
HALF MOON BAY 1101CB | {D114DA17-C3D8-4F00-837D-4551FAA55B77}
HALF MOON BAY 11022032 | {B1DF2EF5-B79B-49EC-9036-B92FC4D1C70A}
HALF MOON BAY 11022032 | {1AC2F406-7414-45B2-894D-D807C20227F2}
HALF MOON BAY 11022032 | {04338CCA-7EF9-409D-9ECF-B4834D579CE2}
HALF MOON BAY 1102350336 | {61D17DF6-ADDA-4D95-BD25-C42B9D51757B}
HALF MOON BAY 110258448 | {51B7F99B-37F1-44D1-A380-3A17DA62C971}
HALF MOON BAY 110260703 | {EC65686F-B15A-4CBF-8005-BF1274876E69}
HALF MOON BAY 11026097 | {04338CCA-7EF9-409D-9ECF-B4834D579CE2}
HALF MOON BAY 11026153 | {72FA64D8-3A63-4420-A7D7-130A2E3D886E}
HALF MOON BAY 110264293 | {AE99FE40-5E2F-4EF7-A496-F7D5D1016060}
HALF MOON BAY 1102665624 | {E6EDD644-68A4-422C-8253-6913368C1272}
HALF MOON BAY 11028848 | {B38DB0B8-9B03-4771-A545-1316F725B1B3}
HALF MOON BAY 11028910 | {72FA64D8-3A63-4420-A7D7-130A2E3D886E}
HALF MOON BAY 11029114 | {EC65686F-B15A-4CBF-8005-BF1274876E69}
HALF MOON BAY 1102CB | {EC65686F-B15A-4CBF-8005-BF1274876E69}
HALF MOON BAY 1103157944 | {15F0AF2B-7A00-4F13-A75F-67F47F9B4603}
HALF MOON BAY 1103256249 | {3A40FD55-A6F4-42AD-BBB6-244D25E7BB11}
HALF MOON BAY 110329454 | {6106A145-F67B-4637-A42F-8BCEA85E7B24}
HALF MOON BAY 1103341542 | {D82172A1-B65E-4492-A8B4-CC58BA0F7717}
HALF MOON BAY 1103389114 | {2F83CE4E-0855-4D8B-B1C5-D4FFD94A6F8F}
HALF MOON BAY 1103461558 | {5B63424F-7E68-45B3-A042-84BE563149F0}
HALF MOON BAY 1103531594 | {939B38BB-613F-4A01-A922-509D65700968}
HALF MOON BAY 11036012 | {7A26C173-B69B-4907-B599-46F01DDAB9CB}
HALF MOON BAY 11036014 | {C9FA3CBF-AF0B-40A6-8062-0EE0474AC48A}
HALF MOON BAY 11036018 | {2DDD3645-3AB5-4B35-8936-1A369FDDE7B2}
HALF MOON BAY 1103623460 | {1E711061-9006-460A-8EEE-DB532A4DAE2D}
HALF MOON BAY 1103655644 | {8768B1B0-4DEA-4BD5-97FA-A78DED5BFD8E}
HALF MOON BAY 110376762 | {07C4DB8D-20E6-4803-A265-29C92D756E21}
HALF MOON BAY 1103825502 | {753853E4-C224-414D-99C3-DFD71085C7CD}
HALF MOON BAY 1103869962 | {0FAB28AC-2D6B-4CD3-818B-0321B62F4BC8}
HALF MOON BAY 1103880484 | {2C061CFF-5BC9-419E-A2B7-324612618450}
HALF MOON BAY 11038894 | {65F40270-9C1F-4F03-A2E4-A1FA52E4266C}
HALF MOON BAY 11038898 | {F439C87D-AAE9-43A5-B8D6-BA1AB4C5C362}
HALF MOON BAY 11038920 | {326D13C2-6BC0-4D12-9CFE-64D0722362EA}
HALF MOON BAY 11039112 | {F951C9B5-DFF6-4F18-959A-6543A104D243}
HALF MOON BAY 110398440 | {0D33DD6E-C54D-4E64-89FF-46D8E0E605B6}
HALF MOON BAY 1103CB | {32412CB3-3D8C-4A7B-A553-49E12B00D983}
HALF MOON BAY 1103CB | {D0EDFCD8-2A8A-490D-A06D-0BAFCCC6E362}
HALF MOON BAY 1103H80 | {196D5A62-8277-4556-8937-1330E86D299E}
HALSEY 11011704 | {CDE691D3-842E-414A-AF2C-C34EFCC94439}
HALSEY 11012414 | {C7CE8EEC-BFCB-464B-A0B6-4DE95EE01B52}
HALSEY 11015731 | {FA7F836A-C8A0-42D3-8E43-389B5B7AEC7D}
HALSEY 110176178 | {7B5F2382-5AE2-4C66-951C-F3B7A019CDB8}
HALSEY 1101CB | {FA7F836A-C8A0-42D3-8E43-389B5B7AEC7D}
HALSEY 1102164068 | {4B3281BE-5BD0-48E2-A99C-0ACCD9AE2A68}
HALSEY 1102164068 | {61D3CA53-774C-411C-906D-B5C7A38BEC7F}
HALSEY 11022514 | {D24FE68D-C3B0-43F0-8A16-C357F1C466D0}
HALSEY 1102281660 | {FF4361AE-2C9A-41F6-9A85-9A3B186A6735}
HALSEY 1102318786 | {1F953F3A-69CC-4716-9EFF-8FDAD16E8151}
HALSEY 110239104 | {033C2E2D-A850-40FA-9417-37D899E25ED1}
HALSEY 1102514616 | {DAAF3E0E-FB0F-4550-AEFD-6EE835712C5E}
HALSEY 1102664826 | {73704D7B-529D-4BE7-B911-0F988D30BD14}
HALSEY 1102676064 | {BF3289E0-80A5-4D48-A3FA-50A7D697D692}
HALSEY 1102751626 | {53861E9B-B78F-4B30-887A-55D46A9C63B9}
HALSEY 1102CB | {0961801B-845E-4B14-847B-854C50E3739F}
HAMILTON BRANCH 1101161872 | {7FEFC5CA-2496-46DE-BE2F-DEB25BC01D17}
HAMILTON BRANCH 11012046 | {385C1178-1E10-4C92-A2B8-B11436713899}
HAMILTON BRANCH 11012082 | {C6BC6538-2EB6-4DA5-9982-6A2D9BE60DD8}
HAMILTON BRANCH 11012436 | {637602BE-E394-4D87-B06C-9852D4AA6AF2}
HAMILTON BRANCH 11013049 | {B799CE92-A5F5-41AF-A189-4F32E6DC30EA}
HAMILTON BRANCH 110137436 | {32D1F0F9-DFF9-4513-A71D-93DBB94A9BB3}
HAMILTON BRANCH 110137534 | {B799CE92-A5F5-41AF-A189-4F32E6DC30EA}
HAMILTON BRANCH 110153192 | {D03C18EE-E1AA-4630-B396-89DAD0F5DDA8}
HAMILTON BRANCH 110187784 | {512E7C3F-C5ED-477A-A43F-85AACCF18F8D}
HAMILTON BRANCH 110190334 | {6FA22C4C-B16C-4BDC-8F70-7E0F32F87C45}
HAMILTON BRANCH 1101CB | {CF1292FF-09D7-4946-B3C9-5DF5A5CB48C9}
HAMMONDS 11019760 | {EAC018D0-6E0A-45C6-BAE5-BAE564C53C44}
HAMMONDS 110212100 | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
HAMMONDS 110212140 | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
HAMMONDS 1102CB | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
HARRIS 11082062 | {0E0C2894-9F4C-4F14-AF8A-F5A44822C594}
HARRIS 1108395498 | {956DFF7A-2597-4885-8155-9B37AFB45D53}
HARRIS 11084674 | {55AE43E4-ABFA-4493-997C-A8117F747A98}
HARRIS 11084674 | {1983F28A-08C9-48B3-9CC8-597EC6A45F0E}
HARRIS 11085984 | {9A3D8818-9236-4C74-9C67-0369FA031A48}
HARRIS 110866386 | {9A3D8818-9236-4C74-9C67-0369FA031A48}
HARRIS 11087920 | {9A3D8818-9236-4C74-9C67-0369FA031A48}
HARRIS 1108CB | {9A3D8818-9236-4C74-9C67-0369FA031A48}
HARRIS 1109183860 | {62242811-5FAB-4F8A-8BA0-8F1F1D633349}
HARRIS 1109355914 | {C9FD0E2E-E3CC-4613-86C7-481937B54700}
HARRIS 11095982 | {0E899392-4139-4EF4-8C02-780C18A47141}
HARRIS 1109700 | {B45E3CF5-024E-4735-BFDA-B714A7EDABF9}
HARRIS 1109700 | {6EE208A5-6ADB-44F7-95B4-016C09D6A385}
HARRIS 1109700 | {E7CD4EFE-FF2D-48E6-A810-D2B9643B4C3B}
HARRIS 11098862 | {0E899392-4139-4EF4-8C02-780C18A47141}
HARRIS 1109CB | {0E899392-4139-4EF4-8C02-780C18A47141}
HARTLEY 11011306 | {CE237446-8B77-4B6F-A151-0796DF2727A1}
HARTLEY 11014710 | {801F0074-FB1F-4C52-9EC5-EE9281D564FB}
HARTLEY 1101658 | {D05A5F97-BA6C-4210-AA67-0AC96ADACE28}
HARTLEY 110167994 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
HARTLEY 1101698 | {14B018BB-E4F3-4418-8464-262A2B2FE900}
HARTLEY 1101738 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
HARTLEY 110186876 | {0628807D-B297-4343-8118-F7F853EA05DA}
HARTLEY 1101871312 | {385BA61F-2E87-46EF-B5EE-E4C4A5DF5993}
HARTLEY 110194178 | {33AF121E-F118-4B6E-94DA-FB39FA49A86E}
HARTLEY 1101CB | {9A7B1854-4374-4D14-BB43-EA4EAD6446AB}
HARTLEY 1102113786 | {DCE882BC-8AF0-4EA1-ADB4-CEF6A7B948D0}
HARTLEY 1102247988 | {F4698279-C7C5-4840-A723-E16454FDD382}
HARTLEY 1102471 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
HARTLEY 1102490 | {81602399-62C7-41C1-B875-F30FCB0774B7}
HARTLEY 1102524 | {45C1901D-E49E-428E-8B0F-B20AF66CAD20}
HARTLEY 1102841676 | {5D95B927-2424-488D-993D-ADBE978C5596}
HARTLEY 1102920190 | {FC0E3435-0D30-4899-A816-A589A6F77862}
HARTLEY 1102CB | {60D33697-692D-4938-96CD-E53257AEC032}
HARTLEY 1102CB | {5D76312F-4A10-451F-BDB1-97A9738A5919}
HARTLEY 1102CB | {BCBF8B7C-F641-49B2-AD94-3642665272A4}
HATTON 11012026 | {593FA41B-396B-4601-BD50-0DE927CB7E5A}
HATTON 11012654 | {38794799-8756-4269-B41E-6206BA101157}
HATTON 110137088 | {C7A22305-CC6A-494A-88D7-7F9AE8676071}
HATTON 1101399900 | {4ACA70E2-9D9C-40F9-8434-15B06F65DC14}
HATTON 110175304 | {CCEDCCA3-66CA-4499-B03B-2E805BEC4C06}
HATTON 1101CB | {19B86573-307E-4C6E-966B-96848CB70151}
HATTON 11022010 | {07CA7935-70B1-4CBA-B069-3C5BAF9F4438}
HATTON 11022070 | {E55048C4-CAB1-4B6B-99F6-30BB24FEA325}
HATTON 110240461 | {E55048C4-CAB1-4B6B-99F6-30BB24FEA325}
HATTON 110240465 | {DF6AF33C-27E3-43A2-A515-B3B27F7B49FE}
HATTON 110256680 | {15F21C1B-A03A-4E01-B20D-69BB0B19F555}
HATTON 1102648928 | {96F3BFFE-8B25-45FE-9E94-B3CC1506798D}
HATTON 1102CB | {DF6AF33C-27E3-43A2-A515-B3B27F7B49FE}
HERDLYN 1102575178 | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
HERDLYN 1102608254 | {CE97333C-59D7-4EFC-8B71-0C4A3CF5BCEE}
HERDLYN 1102609338 | {20393823-B77E-489E-817E-F72A23CAEA43}
HERDLYN 1102973026 | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
HERDLYN 110299602 | {BD7C976E-7CD9-4ACD-A152-480ECCDE08A2}
HERDLYN 1102B569R | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
HERDLYN 1102CB | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
HERDLYN 1102CUS1379 | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
HICKS 111512494 | {48560C68-AA30-4BF0-B246-3EDAD7DA0E36}
HICKS 1116583284 | {EC9FDCBC-C8AE-4588-B594-E3F1FCB0DA2A}
HICKS 111660050 | {AA1A8D76-D2A1-485C-9B69-D74FAC1101F8}
HICKS 1116647210 | {9B3BCE26-3F49-48E0-A9CF-1FFE9B2444C4}
HICKS 1116733078 | {B0CE2A51-CFF9-4904-B0B1-3919D3274116}
HICKS 1116983580 | {26706A0A-D462-4709-8596-704DD2D34F48}
HICKS 1116CB | {887C42B0-874F-48B4-B368-C0A3D7EE375F}
HICKS 1116LB16 | {128CFE15-7FAD-449A-AC53-530ECD1ABDFD}
HICKS 1116LB16 | {D3EAA91E-0FE8-4C2F-AB93-979EB58D8FBF}
HICKS 2101984788 | {D85A7626-E5FB-4537-BBDF-FBAAC03D082F}
HICKS 2101CB | {29DF4083-4850-493D-A17C-7E1454C0761F}
HICKS 2101XR162 | {C0376D9F-B470-4AB5-B207-928FB9998965}
HICKS 2101XR162 | {4BEE9D9E-BAC4-46AE-B4EA-D5A6948A1B98}
HICKS 2101XR250 | {56CCC6BA-5D72-4C21-B685-7DEDC2A0C078}
HICKS 2101XR250 | {7AD08992-20DE-491C-B310-C51F11D11659}
HICKS 2101XR250 | {890F1A16-F508-4C52-8FC3-9EC93773579A}
HICKS 2101XR548 | {21823ADE-60D1-49AF-96C7-A6BCD78F0512}
HICKS 2103CB | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
HICKS 2103LB50 | {7B884E42-31C4-4241-9616-799B5779F088}
HICKS 2103XR068 | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
HICKS 2103XR248 | {F3C9E330-5EFE-42AE-9971-7797E81AA91A}
HICKS 2103XR262 | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
HICKS 2111255740 | {EB7674B7-CCD0-4EFE-8467-AE9A3DE4BA98}
HICKS 2111XR210 | {CF04DCF7-F474-48E8-8533-36C336A15BD2}
HIGGINS 11032194 | {04FFA86D-12A8-4DCB-A786-7ABADD4FCF1A}
HIGGINS 110332120 | {EA74D320-F3F3-49EB-8286-8BD66424051C}
HIGGINS 110332120 | {42C0044E-B495-4983-9439-0351AC9E28F8}
HIGGINS 110350072 | {740DE1B6-71C4-4F89-BFF6-C379E023E99F}
HIGGINS 1103789714 | {D2804A73-7030-4736-9366-42176C492BFE}
HIGGINS 1103789714 | {FA627323-6B26-4F37-9BFB-AF25ACFDA17D}
HIGGINS 11039753 | {FA627323-6B26-4F37-9BFB-AF25ACFDA17D}
HIGGINS 1103995672 | {FCC40ADF-1FB7-4F80-97A9-6981FCDC8244}
HIGGINS 1103CB | {5963F19C-E1BE-46EC-9E26-B117A913E935}
HIGGINS 11041006 | {6831EC63-2DE1-4FA9-8E52-ECEB96F95CDF}
HIGGINS 11041374 | {5975A3D8-5B89-4D93-9C6D-113094290849}
HIGGINS 1104324510 | {477268D6-DE4E-4795-ABA6-DB4CC4C4808D}
HIGGINS 110432747 | {6831EC63-2DE1-4FA9-8E52-ECEB96F95CDF}
HIGGINS 11044281 | {46E9257A-F9DC-47D6-A72D-7B5FD7E2E022}
HIGGINS 1104498932 | {D5E00AD4-7C48-4E87-BBB1-92F5DE277EEA}
HIGGINS 1104533648 | {7316CABA-ACE0-4406-9BB2-A4017DAD0078}
HIGGINS 1104842642 | {77DD24A4-3555-45C1-AFB0-D6E3B0D6C267}
HIGGINS 1104CB | {46E9257A-F9DC-47D6-A72D-7B5FD7E2E022}
HIGGINS 11071070 | {735D1686-195C-449F-AFF7-F3F9879F6190}
HIGGINS 1107746082 | {8C53EC31-B3AB-4E33-B852-46094C79DBC8}
HIGGINS 11077559 | {735D1686-195C-449F-AFF7-F3F9879F6190}
HIGGINS 1107836688 | {B73B7429-00D8-4172-979B-F99C3A58EB55}
HIGGINS 1107CB | {AD1702BF-568D-4020-87DE-29F495495BCD}
HIGGINS 1108CB | {F3F43510-36DF-4FCC-ACB0-6058CB728BA2}
HIGGINS 110950078 | {13205944-27DE-4E69-8D25-637FC945A119}
HIGGINS 11095703 | {824F13D7-3113-4AA8-8BC2-89229A42D634}
HIGGINS 1109594 | {824F13D7-3113-4AA8-8BC2-89229A42D634}
HIGGINS 1109CB | {97806AE4-5D72-4FCC-8179-00CDE6E08736}
HIGGINS 1110166282 | {F3D6F46D-CE49-42B8-ABD9-DE4AEFF8E29E}
HIGGINS 1110197930 | {11090D9C-84B9-4B7D-ACA7-D3AC9294F29D}
HIGGINS 11102408 | {71CA17E4-B079-4EB2-8611-562BAD82EEBD}
HIGGINS 1110429714 | {3BDE57E6-D2E3-415C-A6FD-913D986E7AB0}
HIGGINS 111051794 | {B86F1700-5A54-45AD-BE5A-60237D0F62CD}
HIGGINS 1110861610 | {C6E8B2FD-D557-459C-B9FB-FFB281472FF9}
HIGGINS 1110CB | {29C788AD-BB0E-42D2-8EAD-CD59E3E03CF4}
HIGGINS 1110CB | {E56A3B9A-F6B2-438C-8FDC-DFADF12A0423}
HIGHLANDS 1101CB | {F7C77AB2-FB1A-424C-8DCB-D1ED89130316}
HIGHLANDS 11021304 | {DF76C57E-BBD1-4728-AA99-EBD33D60311E}
HIGHLANDS 1102230414 | {CD78E93A-B7DA-4A5F-A8CF-16853C69CA49}
HIGHLANDS 1102556 | {36BC008E-75DD-4032-9E44-5DB50949C39A}
HIGHLANDS 1102604702 | {4DCB4FA9-9915-461D-BB5B-612AECE3A33E}
HIGHLANDS 1102623120 | {B5C2A169-B3BF-48D4-8260-06DB123C1FCF}
HIGHLANDS 1102628 | {805F8CD4-618B-4641-8C2C-AEC1BF35DB49}
HIGHLANDS 110265650 | {D6E00327-F4CB-4F20-A907-68904C3BB997}
HIGHLANDS 110275140 | {D71C2E21-7CE4-4721-8677-0076FC6B52D7}
HIGHLANDS 1102914918 | {8F7C94EC-9C6E-4FA3-83B6-0BEF18BA51B7}
HIGHLANDS 1102CB | {12D5CC7A-B2CA-4EEF-8AD4-C988E70110AA}
HIGHLANDS 11031282 | {ADF7CDB1-D7EE-4238-AD1F-3FDE0907FF69}
HIGHLANDS 1103287766 | {AD7457DE-7857-4646-BC27-24CDE616604D}
HIGHLANDS 11034630 | {C0802380-5040-4C58-8433-9FF2FB3282BB}
HIGHLANDS 1103520 | {20B5CFDD-9238-415D-BF03-7EE0B92100FE}
HIGHLANDS 1103568 | {DE7AF2D5-E911-47A4-AE78-DD80A28A5D4B}
HIGHLANDS 1103665096 | {7A8FDD2A-0C0A-4E57-AF74-45A4DEE663B7}
HIGHLANDS 1103726580 | {D271DF75-70E3-4A5D-9E2E-6D2BE449ADB2}
HIGHLANDS 1103828 | {F617C2F6-F9CA-4233-ADD2-A5EEE40355DB}
HIGHLANDS 1103917328 | {E2763744-304B-4C72-A146-E33A686F8B6A}
HIGHLANDS 1103973816 | {45E82633-486E-4610-936E-63E014462202}
HIGHLANDS 1103CB | {F4CEECFF-9688-4F5E-82B6-98F3F42878F8}
HIGHLANDS 110439458 | {F73918F2-BDFA-403D-8839-D569F0C45575}
HIGHLANDS 110448262 | {05A2F271-E60C-4560-A544-2497E351C8FC}
HIGHLANDS 110476156 | {CEFF2CE3-E3F4-40F0-B7FB-D65976C4211A}
HIGHLANDS 110484640 | {E2438D63-9836-48BB-91BE-1736CBE6A21A}
HIGHLANDS 110486807 | {4153AD52-F0C3-4F94-B9A7-DBFADEA8B1B3}
HIGHLANDS 110487040 | {4153AD52-F0C3-4F94-B9A7-DBFADEA8B1B3}
HIGHLANDS 1104CB | {EC0CBAAC-D25D-4166-8326-CC1A005227F9}
HIGHWAY 1101200662 | {27D0C7EA-6E05-4947-A47E-355769B9A693}
HIGHWAY 1101738 | {27D0C7EA-6E05-4947-A47E-355769B9A693}
HIGHWAY 110181590 | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
HIGHWAY 1101992028 | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
HIGHWAY 1101CB | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
HIGHWAY 1102700 | {17274A38-F8A1-462F-93E6-49EE52FB630E}
HILLSDALE 0401289582 | {3BC63369-8BB7-498F-AC59-3790414C1555}
HILLSDALE 040198526 | {E5751866-C01F-4B6F-A700-E0FAA4499012}
HILLSDALE 0401CB | {3840BE80-21EA-4670-95C2-6EA58C09B292}
HILLSDALE 040277056 | {6CAF4EA6-4ABD-4B11-B8DA-EB2F88BE9114}
HILLSDALE 040485812 | {2DBE6767-7D56-4562-8F78-31E59118A4C4}
HOLLISTER 21014792 | {6C3CFC54-A1A4-4370-AEA1-A2570E0F37DE}
HOLLISTER 2102113634 | {AA026DE2-36FF-41BE-B277-D062A4C54501}
HOLLISTER 2102406496 | {17B07670-0E53-4796-89E8-790E1D545BFE}
HOLLISTER 2102676164 | {5ED88047-4B28-4CB1-8810-2C6A7B9E00CC}
HOLLISTER 2102855412 | {1326B156-0483-47A9-A035-C6F98F761263}
HOLLISTER 2102CB | {D8069B78-C4A1-4306-A859-EF54203AE5F4}
HOLLISTER 21044046 | {38133BFE-606B-4796-A7F0-653C5DE724A7}
HOLLISTER 21044068 | {B4FE7570-1750-4673-B760-557A7D4F2C8D}
HOLLISTER 210441808 | {3A7DE5A9-6F9C-4704-A7B4-637F15326CD9}
HOLLISTER 21044403 | {B4FE7570-1750-4673-B760-557A7D4F2C8D}
HOLLISTER 21044782 | {C12B46D7-11F2-4E48-9DFC-9E2CC790DCEA}
HOLLISTER 210491424 | {951B1516-4326-49B7-849D-E72573882819}
HOLLISTER 21054018 | {201D4860-5BDE-4AE7-B543-F824A85004DC}
HOLLISTER 21054040 | {9EFCEC97-B945-4717-BB02-DD9746AC6A53}
HOLLISTER 21054042 | {1E6DC745-CC49-441C-9C9B-BCE1C0BE079C}
HOLLISTER 21054048 | {522758DC-D04C-45F3-86B0-6920B5847932}
HOLLISTER 21054060 | {F5425C52-6CB2-4CD9-81A3-7FCEE48AC283}
HOLLISTER 210542224 | {102DDCC7-B669-4F67-96A4-A65E2BB45451}
HOLLISTER 21054724 | {8EF9C157-EB82-4F95-9143-D4D285784E19}
HOLLISTER 2105475946 | {36C68467-DD29-4098-9B8B-C4FA03ACDAB2}
HOLLISTER 2105480430 | {2A202711-DF81-4789-BFD4-DC7744D8ADFB}
HOLLISTER 2105903238 | {0363382A-DCEC-4F0E-A9CA-F2D9B0CACBC3}
HOLLISTER 2105CB | {ED3912F5-3969-4789-A9D3-65A01A62E3A0}
HOLLISTER 2106281712 | {13BCDD68-D485-4507-BB4D-A6F297EC4EEC}
HOLLISTER 21064004 | {95C4B2EA-7339-48DF-9F61-FADDFD6FCDFA}
HOLLISTER 210683518 | {B3B33B44-B27E-4997-ADCB-104657A7A68D}
HOLLYWOOD 0401413432 | {E22C1D09-7C47-465A-849A-88FF56B8813C}
HOLLYWOOD 0401811742 | {492D154A-EE0E-4F92-B9B9-FEA1E967CA18}
HOLLYWOOD 0401CB | {854414CD-0C09-471D-91AA-83170F69D473}
HONCUT 110137322 | {4580F407-B405-4F86-9F13-8318C1F1927B}
HONCUT 11015581 | {4580F407-B405-4F86-9F13-8318C1F1927B}
HONCUT 1102301886 | {4E6B8B0B-875E-4AF2-B828-28889B8DD82C}
HONCUT 1102478754 | {B9E11B31-9989-4FA2-87A7-5FB52DF0CB03}
HONCUT 110255206 | {95CFDCE9-A6F6-4428-B8F8-A23AC65977EB}
HONCUT 11026130 | {3DAB252C-5A42-4BD0-ADD0-23CE62160133}
HONCUT 110275350 | {3ECFF3DB-033A-4FC4-B37B-A365EAF3EE98}
HOOPA 11013174 | {340CBFFC-8113-455B-B1D8-1918397994A0}
HOOPA 11013290 | {FBCD7012-56B0-4DB8-BFD1-768DDA012D1B}
HOOPA 11013304 | {72D61001-3395-45AD-8AA5-496E28074CB7}
HOOPA 110137202 | {E07D7DDC-2962-416D-9482-05DD47B79DBD}
HOOPA 1101405280 | {2415EF23-20CC-449E-97C7-29435A19FAB5}
HOOPA 1101561116 | {340CBFFC-8113-455B-B1D8-1918397994A0}
HOOPA 110182542 | {AF113D3A-C32B-4AE6-9683-F0B931A2BCC2}
HOOPA 110193038 | {1C7B29C1-9766-4E63-AFC2-ED97D59270C9}
HOPLAND 11011100 | {49DD2761-248F-4D1E-809D-C19E1A64F359}
HOPLAND 1101154790 | {90407EF8-546C-4CC0-BAC4-A3C598D39737}
HOPLAND 11014626 | {03A33F3F-5506-459A-89E7-ACD76DFFDD38}
HOPLAND 1101558 | {7D091198-DCC2-4EA1-AD83-C691E4F808C9}
HOPLAND 1101768 | {CF814E69-077B-44BB-9617-D51226ABE508}
HOPLAND 110180620 | {CEE02838-136E-45AF-B305-63BB762F2ACE}
HOPLAND 1101865263 | {876D2A2A-E47B-4C89-903B-5E516A574F17}
HOPLAND 110194006 | {8550FAE9-8660-4D0D-A46A-9FC5A8080BAF}
HOPLAND 1101960 | {1163B195-EACD-43BD-86EC-77A4B82C1934}
HOPLAND 1101CB | {7E6065FF-2C07-4696-A18E-5408BD7025E6}
HORSESHOE 11011682 | {462E2D82-20B9-4FAD-BC05-75852F2ACF8E}
HORSESHOE 11011682 | {D177ED3D-75C8-494D-9D73-9349634329F7}
HORSESHOE 11012714 | {3E108A7D-3BD7-484D-A219-8780A55EB7A1}
HORSESHOE 1101416226 | {DDC5A35F-31F2-4622-90DD-F12D8635E350}
HORSESHOE 110150140 | {223CF293-20C5-4942-B371-E6A6292ECAF4}
HORSESHOE 110151538 | {87800A96-4222-40F6-B470-AA1E26FEFB33}
HORSESHOE 1101603250 | {6501F20E-BB6C-44CD-B10D-FA9DBEF23636}
HORSESHOE 1101CB | {88F5CEC0-E8A5-4F1C-9B7B-06545C0D954B}
HORSESHOE 110450142 | {72194304-B9B5-4008-9268-F14D384C2205}
HORSESHOE 110451536 | {DCF001D4-BEE1-4DF1-BC31-9FDF6ADCEBFC}
HORSESHOE 1104CB | {3D4378F9-B822-4985-B4DC-F977157ECBFD}
HORSESHOE 11061680 | {6467CE55-E29D-44B6-B77F-76D86FE9D5B0}
HORSESHOE 11061826 | {E78C9DEE-4564-4CED-86F6-578EC71D6FE0}
HORSESHOE 1106CB | {E78C9DEE-4564-4CED-86F6-578EC71D6FE0}
HUMBOLDT BAY 1101898396 | {91BBB89B-9333-4A31-8E04-1784413A7D4C}
HUMBOLDT BAY 1101CB | {91BBB89B-9333-4A31-8E04-1784413A7D4C}
HUMBOLDT BAY 1102104220 | {92404771-2B96-4EE9-9A7E-4C0DA339A55A}
HUMBOLDT BAY 1102309413 | {0A5740C1-9196-4281-8753-B21C8EA0160F}
HUMBOLDT BAY 110242066 | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
HUMBOLDT BAY 11024714 | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
HUMBOLDT BAY 11024724 | {0A5740C1-9196-4281-8753-B21C8EA0160F}
HUMBOLDT BAY 1102741980 | {3D0CD5B3-E4C3-4E4C-848A-D16C0F741C16}
HUMBOLDT BAY 11027598 | {50FDFAC9-1C29-47B2-BBE8-2C25E0E08184}
HUMBOLDT BAY 11027600 | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
HUMBOLDT BAY 1102CB | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
IGNACIO 11011264 | {2723FD74-E215-4B66-BA9E-051AE21C4595}
IGNACIO 11011300 | {64639A8A-2672-4BE4-8EBB-2985CB356A36}
IGNACIO 11011779 | {64639A8A-2672-4BE4-8EBB-2985CB356A36}
IGNACIO 1101CB | {A57172F7-A24B-4226-8C15-DA9E4C31AFEB}
IGNACIO 11031068 | {F489C694-D583-42AD-BB91-0D15DCF9AC70}
IGNACIO 1103151462 | {A36BBD4A-24CB-4238-BDFE-096AC8C68041}
IGNACIO 1103CB | {09D14343-CC3E-46D9-99DC-4193E90EB264}
IGNACIO 1103CB | {2E2A9BE3-6328-45AB-919A-7693139C27D5}
IGNACIO 11041274 | {4117016E-C4E1-43D1-8702-FC75C137797F}
IGNACIO 11041290 | {EEF03FEE-E315-4DF5-BC12-E5292370248B}
IGNACIO 1104450582 | {F91156C0-E294-4BD1-9245-277084BD5819}
IGNACIO 1104469764 | {B15C4D34-840D-4CC7-96CF-D3ABBE50E477}
IGNACIO 1104CB | {4117016E-C4E1-43D1-8702-FC75C137797F}
IGNACIO 11051943 | {E636DD2B-323A-4E65-AE99-16FA1288A9E0}
IGNACIO 1105318 | {25FEAA66-B3E3-4A2E-9CFA-07C2BE62DF67}
IGNACIO 1105490728 | {ACF50790-A77B-4E22-9362-2A36912CA1D3}
IGNACIO 1105683542 | {BB37B807-9B57-4D41-8EE3-98B7B9A98DE4}
IGNACIO 1105775176 | {E636DD2B-323A-4E65-AE99-16FA1288A9E0}
IGNACIO 1105784032 | {087FC024-1431-4D83-A955-1FB7C9160A67}
IGNACIO 110584764 | {4C2B4F6D-8805-4D54-AEC8-8F73248C6F67}
IGNACIO 110584764 | {E1F2559F-5071-40B5-BFDE-D70EABF698BC}
IGNACIO 1105908 | {1C105F4C-AE80-4099-9437-85CB973612DF}
IGNACIO 1105CB | {71399AD4-B98F-4687-A48B-364B35890C76}
INDIAN FLAT 11044580 | {62B3D471-5018-455D-85A5-F307E381688B}
INDIAN FLAT 11045456 | {85C573CB-6CAC-4BD3-9BAE-88F4FB8F62BB}
INDIAN FLAT 11045456 | {62B3D471-5018-455D-85A5-F307E381688B}
INDIAN FLAT 1104CB | {8FE2B2A5-53AD-4D02-8B28-25A33ED98DCB}
IONE 110112236 | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
IONE 110113446 | {E7CD9906-89BD-49E9-822A-3B11AFC2B697}
IONE 1101510200 | {9C6D587D-CB16-40C3-BD97-BB988A8AB8BE}
IONE 1101CB | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
IONE 1101L3141 | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
JAMESON 110227210 | {8DC3BD73-58C4-4C11-8E95-874E726C1B5F}
JAMESON 1102865502 | {A17489AD-F8E6-4EDF-87DF-CA9C33FE9292}
JAMESON 11028842 | {A9A36598-2BF7-4270-99BF-EC9B9E23BB29}
JAMESON 1102CB | {CCF6C8D4-166E-445A-ACEB-16D79D2A6A88}
JAMESON 1103118944 | {A2248A11-F35A-465F-8815-05FAE8AEC21C}
JAMESON 1103CB | {D66EDA38-27E9-4939-96F7-B9EFA1F3B789}
JAMESON 110513392 | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
JAMESON 1105371694 | {CBED1D90-C1D1-43D3-861C-32471E7EFC40}
JAMESON 1105466348 | {8E99B7C2-09C6-4CCD-84A3-45313788DF3F}
JAMESON 1105512616 | {FA9AEBA0-4BB6-4E10-BAE3-C98A314D50BC}
JAMESON 110560052 | {13995F0C-BE80-4C13-B825-53F70579F93B}
JAMESON 11057652 | {15E7F33B-BC99-41F7-80A1-54BDC820E172}
JAMESON 11057792 | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
JAMESON 1105913400 | {E925FB90-0D67-4350-9303-9E202A799552}
JAMESON 11059472 | {4372CAAD-3581-4B8A-AB27-A49D177EEFCE}
JAMESON 1105CB | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
JANES CREEK 11011184 | {82D90921-E507-4935-9634-C0CEB766B38E}
JANES CREEK 110141990 | {B4EC8E85-89E6-4E1E-A58C-F910365EBD5D}
JANES CREEK 1102CB | {00625706-EEB8-45CB-9368-35DB90D22760}
JANES CREEK 11044844 | {26E770F4-F25D-4CF1-B69E-D7AF03209DEC}
JANES CREEK 1104CB | {74133F88-7C2E-41BF-994B-5D7BF579CEB8}
JARVIS 1101467034 | {C606228A-087B-437D-9A9F-1FD57375B95A}
JARVIS 1108289662 | {D0FD43E9-668D-474E-A42F-940591FD44BD}
JARVIS 1108548648 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
JARVIS 1108767280 | {518B32E2-92EA-4E90-A3AC-D00B405E1539}
JARVIS 1108CB | {6E2BBEB0-5FF2-432A-87B6-19D6CB26C1C6}
JARVIS 1108MR366 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
JARVIS 1108MR367 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
JARVIS 1110CB | {F27BF583-4544-41F4-91D5-3B4970C09DAF}
JARVIS 1111907698 | {756FEBB5-79F7-43A0-8D9C-AD33FFCC0DB1}
JARVIS 1111MR121 | {F5BF7E7D-4C96-4918-ABEF-C33B63B5DD64}
JARVIS 1111MR122 | {1A5CD57B-504B-4150-A099-4F8257FEDA9C}
JESSUP 11011496 | {7E13CC3A-AEA1-4A09-9EEC-1D6C86F4363F}
JESSUP 1101271314 | {B509E65A-277F-4CB2-9C36-94971C8A46D9}
JESSUP 11012839 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
JESSUP 11013383 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
JESSUP 110141356 | {7C8CD245-F5C5-41C8-8C39-1CC5C953323C}
JESSUP 1101509264 | {67C34A8D-7125-41A3-A0F1-303BFAA70FAB}
JESSUP 110168362 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
JESSUP 11019002 | {94370961-147A-42F3-9849-8A0C21F665DA}
JESSUP 110194468 | {D2D6973F-363A-4DAC-B85F-5E6E9B82592B}
JESSUP 1101CB | {A7720DBE-D298-421E-A3B2-FE12C335EE16}
JESSUP 1101CB | {D9430ABC-DFEB-4916-9501-6BC60BFCFBE2}
JESSUP 11021314 | {05CEA4F2-3636-4573-A883-9C548FA0A079}
JESSUP 11021550 | {B661BE4F-F0A3-491F-90E4-A5B76D06F645}
JESSUP 1102158468 | {B661BE4F-F0A3-491F-90E4-A5B76D06F645}
JESSUP 110238330 | {05EBFD7E-35A6-4E40-95CF-51485C56D3C6}
JESSUP 110269928 | {7CA3CBB2-5BD4-44E1-9364-BA8EE2FC0FBD}
JESSUP 110276068 | {B75A956B-8FBE-4735-92D0-A851A9ED4A9E}
JESSUP 110296554 | {14C3CF81-5A6E-4ADC-BDB6-EF5B849D6F19}
JESSUP 1102CB | {232A469F-DE89-4EE3-AC4B-F74419E6464C}
JESSUP 1102CB | {B338950F-D9D8-4372-BB98-92CC783C124E}
JESSUP 1102CB | {C668DEDD-A850-487D-8F72-3AE13FF1307C}
JESSUP 11031518 | {16E5A2EC-59F7-4145-9776-574EFD44BE58}
JESSUP 11031540 | {47DC31DB-63D1-4B41-9B4B-82351A2B9DE8}
JESSUP 110338864 | {05238085-585C-432C-A137-934EA80FC572}
JESSUP 1103728460 | {933860CE-81EB-48DD-96BA-C0297EF47CBE}
JESSUP 1103770356 | {CD04E6E9-9DF1-41F0-9406-3CAF5658019D}
JESSUP 1103770356 | {67FD1DC2-89EE-4876-ADCD-E9F08F9D2DAC}
JESSUP 11039281 | {995D3FA2-A637-43AE-9B3D-DDCFC4316118}
JESSUP 1103CB | {995D3FA2-A637-43AE-9B3D-DDCFC4316118}
JOLON 11027002 | {0490EF9F-4327-4CEC-AB8A-ADCAD043B99F}
JOLON 11027004 | {4198C21C-60CC-4B51-804E-CE0EA277ED81}
JOLON 11027040 | {15367F9D-D171-45F6-9CB4-6F5003394A6D}
JOLON 11027068 | {69E872AF-88D3-4B73-8E65-0B02DC82EDCF}
JOLON 11027070 | {FEA458B2-50EA-4AEB-8DEE-07F4099717FE}
JOLON 11027070 | {3C29C0B2-611E-468C-9FBC-81B8ED82FB52}
JOLON 1102CB | {370C8631-3D98-4FD6-A4A1-B8DD1604CB6A}
JOLON 1103549180 | {936AC0DC-51BF-4519-A62C-820C4933739F}
JOLON 1103CB | {13EB3903-13F9-40C3-94BE-AF1022EEB8B5}
KANAKA 110165606 | {342DEF5A-AA53-475D-8D7B-ABE1A3F6B4E9}
KANAKA 1101733624 | {FEA6C736-5618-4A67-8C3D-643D8CABAF98}
KANAKA 110183288 | {A419DB79-B16D-4DB7-B7A8-B2FF0808C0AC}
KANAKA 1101859138 | {779CCD7D-EBF1-49D9-866C-F06EC359F475}
KANAKA 1101CB | {0C0686BD-4FFD-40DF-98D5-F53EB4C7C859}
KERCKHOFF 1101CB | {5CEBE369-1234-4C2E-B50B-4FF49A63CB11}
KERCKHOFF 1101R308 | {88F7D35A-B742-45DC-AA55-32394737AD92}
KERCKHOFF 1101R353 | {B451B784-A247-4476-BBFC-D28DAAEE5803}
KERN OIL 11043843 | {9F23EB64-F3B4-4CBF-BA80-2578C2F13B01}
KERN OIL 11044479 | {5ACED025-283C-4765-A990-89285810D6DA}
KERN OIL 110476778 | {1080A12B-50AC-4BDF-B6F3-449377032E50}
KERN OIL 1104CB | {9F23EB64-F3B4-4CBF-BA80-2578C2F13B01}
KERN OIL 11062794 | {6ED1033E-54FE-4DD5-BA1F-9025AD47E265}
KERN OIL 11063301 | {BC48BC1B-FF6D-435C-9294-117A7961E04E}
KERN OIL 1106397902 | {CFE459FE-1CFA-431D-B9D9-918FFFA04245}
KERN OIL 110646960 | {1BEA114F-1545-4690-B5EF-CA295187FA4B}
KERN OIL 1106CB | {6ED1033E-54FE-4DD5-BA1F-9025AD47E265}
KESWICK 11011586 | {89760509-9943-408B-8BC5-66753273219C}
KESWICK 11011588 | {E337A679-257A-4862-A121-8FE4E1C11ADC}
KESWICK 11011590 | {F2F9B8C7-DF20-4B0C-A519-3E0E16F2B19B}
KESWICK 1101417066 | {12EBD860-DFFF-4DEB-897E-4876CD2E18E2}
KESWICK 110148480 | {669572AC-0804-48DE-A3ED-77BF33DD2E29}
KESWICK 11019712 | {7666B122-2C0C-4302-93AF-84BE4CAB5B18}
KESWICK 1101CB | {9C6E3EC5-697A-453D-8DEA-C3F8B751E8D1}
KETTLEMAN HILLS 110149656 | {E3191191-EC32-4B60-A32F-F8582A37B6F0}
KETTLEMAN HILLS 11019180 | {F47F682D-7138-4134-B3BE-7095779FF947}
KETTLEMAN HILLS 1101CB | {E3191191-EC32-4B60-A32F-F8582A37B6F0}
KETTLEMAN HILLS 2104358094 | {838618F9-BF36-4DB4-B2E1-2625851B3DC1}
KETTLEMAN HILLS 210464373 | {B01E9D88-F481-4C05-8823-888D25A886D7}
KETTLEMAN HILLS 21049020 | {B053CDDE-1D32-495C-9C06-5A87198FD76A}
KETTLEMAN HILLS 2104CB | {854D235B-BDF1-4D5B-90C0-9DFFA17AD61B}
KING CITY 11027024 | {3218C69B-BAC7-4C6F-9235-42A08CF69E6B}
KING CITY 1102728782 | {0D58B496-6AB1-442B-8B1C-174456B4DA3C}
KING CITY 1103139682 | {9E61253D-F8F8-496C-8DCF-19A52D48CF04}
KING CITY 11037038 | {6DF33D7E-A953-44F1-82DC-C36E39D2281E}
KING CITY 11047092 | {8B5FDE5B-06CB-46AA-8A11-AB1CDB733591}
KING CITY 1106202402 | {63D615E0-331C-41EF-8235-4A9E59F47BD7}
KING CITY 1106500 | {1EC73396-F2A3-41B2-A894-659988450DE2}
KING CITY 1106666728 | {E021D476-E098-4CDE-B403-FDCFAAF2A5C3}
KING CITY 11067032 | {EC91064F-2715-4BD5-A3A7-0B8166F6F214}
KING CITY 1106944510 | {1AF9D6E4-8A41-46E5-805C-196C04612AA9}
KING CITY 1106958502 | {2515B17E-1532-47B4-AD33-23C2F28EDE84}
KIRKER 2103850957 | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
KIRKER 2103CB | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
KIRKER 2103P524R | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
KIRKER 210475648 | {C74DE802-BF47-4D57-912D-652414113F12}
KIRKER 2104CB | {F61A533E-D44D-4AFC-AE85-9F4FD0A8F945}
KIRKER 2105A536R | {EABC5EEA-8AF0-4E4A-8184-A7D17C84C76E}
KONOCTI 11022293 | {3EE95B4C-7440-4D46-99D3-576CFD7E946C}
KONOCTI 1102354890 | {4DDD6757-963A-43B8-ACBB-E2723C52F74B}
KONOCTI 1102410004 | {3DD38877-E68D-4183-8213-2DCDEB2FC639}
KONOCTI 11024300 | {74BC573A-BB75-4EEC-A68D-D9673A89AFF2}
KONOCTI 1102532 | {43499343-6FDA-499A-9065-0F9A4F778AB9}
KONOCTI 110264664 | {B904F4CF-C6EC-4D85-9269-44343E279155}
KONOCTI 1102714370 | {8A5CF734-63C5-45CD-9511-BDF8DA98EA25}
KONOCTI 1102716 | {D5E7700A-E368-40EA-8C45-A0E9AA2F6F54}
KONOCTI 110275382 | {3635FD5D-8230-40C4-B52D-81B9839A55A9}
KONOCTI 1102806668 | {9379E03B-C4F4-489D-BBFC-90549BB13598}
KONOCTI 1102948 | {3EE95B4C-7440-4D46-99D3-576CFD7E946C}
KONOCTI 1102965078 | {D74BE118-5F8F-4569-9B30-2D3A4418CF36}
KONOCTI 1102985276 | {D903B690-6B65-4C8C-B64F-F1B088DE29C9}
KONOCTI 1102CB | {CB616978-006D-49B9-885E-104BFB9EEDAF}
KONOCTI 11081278 | {7B7F4A99-FA71-47CD-9812-ECE462607E94}
KONOCTI 11084037 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 11084039 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 11084041 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 1108430588 | {6FEDFF27-6826-4700-BE39-BD65EAE2E31A}
KONOCTI 1108950 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 1108CB | {E3192F4B-E306-4B2D-9341-C84584505AEB}
LAKEVIEW 11034488 | {DB6CF4A5-64C5-4D3C-8106-DF77F9284168}
LAKEVIEW 11064796 | {81284E87-D055-48A1-8D04-42381F10289D}
LAKEVILLE 1101266 | {B6A7196F-7623-49FA-8ADD-1DAFF9EDFE0B}
LAKEVILLE 1101CB | {DCB62918-25E3-416E-A1A9-9199A2CE1F5F}
LAKEVILLE 1102272 | {5BFD6D0E-9A91-4B87-9163-8304DBF587CD}
LAKEVILLE 1102280 | {F573D52A-B881-4B76-BAE1-75A508AA556E}
LAKEVILLE 1102347280 | {CFC0ACB5-498C-4299-AD8A-6B456236AB7F}
LAKEVILLE 1102367100 | {4BF5FD3C-5BBE-425E-88E7-6C08A33E293B}
LAKEVILLE 1102530 | {20EEDFE7-15DE-4AF7-B5E5-DDB50839E523}
LAKEVILLE 110287432 | {F16EF0FE-506D-4026-9FF6-A9B4826F67BC}
LAKEVILLE 1102CB | {B8DFA050-8FBD-478F-9E02-70E1BAA0DD09}
LAKEVILLE 1105CB | {F1AD241F-1F58-4A6B-9791-DB826ADDDA3E}
LAKEWOOD 1102CB | {957F3B05-D3E6-46BF-B6B1-74EF9A986684}
LAKEWOOD 1102CB | {6990C72C-A823-4961-8622-2BC87697FEBC}
LAKEWOOD 110492910 | {6E990274-D878-48AF-B3D8-9102E49E31C0}
LAKEWOOD 1104W528R | {6E990274-D878-48AF-B3D8-9102E49E31C0}
LAKEWOOD 210738404 | {E6E0CE7A-9AFF-4A02-92C6-B06263224357}
LAKEWOOD 2107396264 | {9DA5BB29-24BB-43F8-B179-1425D3AF09F1}
LAKEWOOD 2107474346 | {6A1EF0E0-D264-48CD-9270-B2391364A929}
LAKEWOOD 210757670 | {8B044506-1700-4270-904E-C6B876F0B7BE}
LAKEWOOD 210769586 | {9E806E71-872A-40DE-ABFF-C0053F485B27}
LAKEWOOD 210769586 | {CE63CF49-1D39-453E-8B0B-C0FA5C180D42}
LAKEWOOD 2107CB | {C476BEC6-6566-47F3-B164-264FA9A69083}
LAKEWOOD 2107GY401/2 | {C476BEC6-6566-47F3-B164-264FA9A69083}
LAKEWOOD 2109432198 | {0F07F3E8-FB27-41AD-9B59-87BC4E61A218}
LAKEWOOD 210964992 | {C65A3889-43E9-4E24-9131-D549D4446C2C}
LAKEWOOD 2110139484 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
LAKEWOOD 211021345 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
LAKEWOOD 211082806 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
LAKEWOOD 211093966 | {00D76738-D88D-4571-9934-906827AF7F21}
LAKEWOOD 2110CB | {8D56729D-62B8-4F70-8336-DC0D3C2D910B}
LAKEWOOD 2110D578R | {ED726999-1701-4168-B617-29D7FAC0197C}
LAKEWOOD 2110W577R | {84A8C5F2-D0FD-4CA4-8FD3-BE277808997E}
LAKEWOOD 2223289858 | {88CD6C9C-9F7E-42D8-991E-21DFC6F69316}
LAKEWOOD 2223920366 | {DAC222F6-911D-41F8-A045-FDB37DA63ECF}
LAKEWOOD 2223982800 | {88CD6C9C-9F7E-42D8-991E-21DFC6F69316}
LAKEWOOD 2223CB | {DAC222F6-911D-41F8-A045-FDB37DA63ECF}
LAKEWOOD 222454676 | {21362692-484C-4985-A610-FAAF4CA90541}
LAKEWOOD 2224568670 | {D3A4AC80-8F36-47DA-9894-6867B4AC6446}
LAKEWOOD 2224568670 | {6C96515F-B6CE-4B5E-91AB-166552C2F0C4}
LAKEWOOD 222464093 | {6C96515F-B6CE-4B5E-91AB-166552C2F0C4}
LAKEWOOD 222466408 | {E8CA3C31-B411-4BE0-B116-25507E333F7F}
LAKEWOOD 22247381 | {5BA403AB-BCA6-4612-86C3-4865011547A8}
LAKEWOOD 222475242 | {5BA403AB-BCA6-4612-86C3-4865011547A8}
LAKEWOOD 2224CB | {5BA403AB-BCA6-4612-86C3-4865011547A8}
LAKEWOOD 2224ROBLES | {DB5046C0-F316-4A2A-8BB0-71146674ABF8}
LAKEWOOD 2224W544R | {7FE65493-C4E3-44FE-B5DB-3B458CDD6C9C}
LAKEWOOD 2227W503R | {0052F236-02DD-4D59-831D-9E6CA4EBFC49}
LAMMERS 1101932641 | {1FC74B38-2F9A-4123-9EBB-CB817D34D821}
LAMONT 11021644 | {3E9A4648-30CB-4190-9869-1F4B7575C98E}
LAMONT 110217566 | {97C1B34A-95F8-4CCE-8DCC-4962D06B743A}
LAMONT 11024222 | {97C1B34A-95F8-4CCE-8DCC-4962D06B743A}
LAMONT 11029785 | {3E9A4648-30CB-4190-9869-1F4B7575C98E}
LAMONT 11043855 | {8B6D49E0-C511-4F4F-89E3-A3D706258A0B}
LAMONT 11044113 | {66C7A1C8-61A2-402A-9225-A301C2795EB0}
LAMONT 11044575 | {28DDAF39-AE68-4213-B81B-B1ED800C91E5}
LAS GALLINAS A 11041220 | {FE680FDB-B6EA-4407-A9C1-F85BBCDCB812}
LAS GALLINAS A 1104304 | {7112559E-7269-4FF3-BE61-B0339A94698E}
LAS GALLINAS A 1104304 | {4AFEE6B2-EE67-4D60-98DD-A0C3D3829D68}
LAS GALLINAS A 1104304 | {99403054-A35C-43B7-8AF3-73845ED952EF}
LAS GALLINAS A 110436840 | {B49A679E-AF73-47B6-A79D-47CB4D4EEA89}
LAS GALLINAS A 1104CB | {B49A679E-AF73-47B6-A79D-47CB4D4EEA89}
LAS GALLINAS A 11051218 | {D824A6B2-681A-48EF-8928-B97846B95D59}
LAS GALLINAS A 11051218 | {14B03F10-6F59-47D6-B547-62E7404D7BC9}
LAS GALLINAS A 1105126886 | {5D12B5EC-5DC5-4C0D-85E8-621A855AB9FB}
LAS GALLINAS A 1105532 | {B4DFAE90-941A-416C-9750-49FB5BAA5F55}
LAS GALLINAS A 1105904 | {BA4CC229-6FEC-4C97-A427-8049E1A3A120}
LAS GALLINAS A 110599904 | {C483C6B2-63CC-448F-80AD-EB7838DB89B8}
LAS GALLINAS A 1106206332 | {825543F8-A353-4A25-8EB9-38A89B92A91D}
LAS GALLINAS A 1106228906 | {65BDBB0B-2F19-42BF-A514-6268B91E4F4B}
LAS GALLINAS A 1106685656 | {7BDFA48E-615C-4CCB-95C0-B267A54E309F}
LAS GALLINAS A 1106685852 | {FB62643F-8EA7-437D-B912-4A4CCD18E192}
LAS GALLINAS A 1106CB | {0EC84767-A265-4D35-8CD0-07F4DBFC6169}
LAS GALLINAS A 1107554 | {DA43FDAA-0AFD-4DA3-9BAB-E9F0ED9A89B4}
LAS GALLINAS A 1107662 | {18214BA8-F1AB-49DB-836F-E6DF072AD66A}
LAS GALLINAS A 1107980 | {18214BA8-F1AB-49DB-836F-E6DF072AD66A}
LAS GALLINAS A 1107CB | {920034E3-10FC-4029-9455-A3F8C0B7BFF2}
LAS POSITAS 2107MR199 | {D8477CE0-E0EF-439F-B1B0-3F9E81D16F6C}
LAS POSITAS 2108631066 | {A35687F3-7828-400B-B177-522C0D2F58CA}
LAS POSITAS 2108794616 | {2B1147C3-9D98-4C09-9F8C-4AD8D92E147D}
LAS POSITAS 2108MR190 | {BBAD7CA8-9930-4EC0-8393-CDE6447A6BA4}
LAS POSITAS 2110MR195 | {8911B60E-25FD-4A9D-AB0E-C717D3E4437C}
LAS PULGAS 0401104588 | {1A6E13FA-4170-41DB-90FF-CC50D93E5B35}
LAS PULGAS 0401544518 | {6E6DF21F-8E99-4125-A51E-53DBB31F9125}
LAS PULGAS 0401CB | {32DE72AC-BD44-46F9-BF98-F2D8B456CA9C}
LAURELES 111110141 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LAURELES 1111198478 | {73A70956-44D3-4112-A68B-5E1D543D21BA}
LAURELES 11112020 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LAURELES 11112028 | {F252A13D-948A-43C3-954E-C03439B944E1}
LAURELES 1111239622 | {104DF701-D80E-43EF-BC28-6C0076869C1E}
LAURELES 1111432 | {C78621C3-DA62-4FAA-872F-5C934F1DDE39}
LAURELES 11116421 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LAURELES 11116617 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LAURELES 1111CB | {6ADA1603-F38C-494F-A594-401AD43EFE67}
LAURELES 11122142 | {5E20B311-BB0A-4C97-B880-E9EFFB1FD21F}
LAURELES 11122768 | {30178FDC-BE0A-4074-95F8-23AFFDDFE15C}
LAURELES 1112438 | {1F7CD2D0-886C-4D05-8112-AF25ABC480A2}
LAURELES 1112543790 | {8355DD95-F9FE-4048-BDAA-30DB26E42987}
LAURELES 1112562376 | {3DF232B2-C195-4351-91B0-CBF56F76D173}
LAURELES 111268454 | {2A037456-E4D6-4133-B41E-0D0ADCC9AA87}
LAURELES 1112779322 | {BE83B9CD-2DC2-4214-9C6C-BCF6CCBA05EC}
LAURELES 1112CB | {F70B7F2A-1768-433D-8A85-4CF42DC91D6A}
LAYTONVILLE 11011760 | {54DB955F-557A-474F-9DB9-2B3A7068B309}
LAYTONVILLE 1101402 | {03DB1220-E098-4294-96C0-8000CD99CD41}
LAYTONVILLE 1101448108 | {301116D8-18DF-4DD2-820F-B08551F93AB9}
LAYTONVILLE 1101518 | {48D8AB29-32BE-434B-A269-6B6F081BC956}
LAYTONVILLE 1101518 | {AF29DE4B-1137-4070-BCC8-1015CEA329AE}
LAYTONVILLE 110189606 | {17A00714-8A49-49C0-B860-6006F3A8F3AD}
LAYTONVILLE 1101CB | {65E5FC7F-8C6A-45F6-95D3-74B8F1E3F473}
LAYTONVILLE 1102141962 | {24057538-792C-47E6-85BB-163CA71B1FC5}
LAYTONVILLE 11022502 | {71012A72-9F3A-4416-A409-5A697A15AF1C}
LAYTONVILLE 110237586 | {389365FD-B3C9-4F63-9935-3457B5B05A11}
LAYTONVILLE 1102500 | {9FACD320-0A6B-4701-A9D9-81FE9755F114}
LAYTONVILLE 1102538750 | {22042EBF-768B-4F6E-A0FB-8BA05EA6F8F6}
LAYTONVILLE 1102572 | {33062E2A-6001-4611-8363-46C244F6285A}
LAYTONVILLE 110264908 | {9B107EC7-49C5-413B-94F9-4B15782C698B}
LAYTONVILLE 1102682 | {9C0210C9-FBB0-4C91-A32D-9DD4D26081CB}
LAYTONVILLE 1102CB | {90C83132-41C0-4461-99CD-C9A5052731EB}
LE GRAND 1104257152 | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
LE GRAND 11045010 | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
LE GRAND 1104RUSE | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
LE GRAND 11104600 | {B9B7E2CF-8396-4913-AA14-43F1BD9F0A32}
LE GRAND 11107120 | {B9B7E2CF-8396-4913-AA14-43F1BD9F0A32}
LE GRAND 11107130 | {3A9B1AE1-6BF6-4F46-86D7-C0F6964F286A}
LINCOLN 11011398 | {4AE4954C-B74F-45AB-A357-66A3AEBC8125}
LINCOLN 1101210168 | {CF1461D3-D5B5-459F-A63E-DFDD8EE92A51}
LINCOLN 1101744292 | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
LINCOLN 1101860022 | {EA2F5A18-032D-4EAD-88B5-87B9DC0F78D0}
LINCOLN 1101875554 | {D787BC67-53F3-4FCB-B678-A7FCAC7F29BC}
LINCOLN 1101881364 | {CF6D4C7B-077F-42A7-A24E-BAE6865A7D41}
LINCOLN 110195756 | {46334C59-6E86-4DFA-8790-B3204A43F682}
LINCOLN 1101CB | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
LINCOLN 11042070 | {FDA2EA55-8785-46E8-B115-1C92328E3E9B}
LINCOLN 11042072 | {A71D3F90-1807-4414-8E54-A388088D7CB1}
LINCOLN 11042308 | {FB48CF9D-FE80-482F-938D-2D781F244FF8}
LINCOLN 1104275986 | {9DA634BB-F98A-454F-AA17-CE93C4AB5C34}
LINCOLN 110451756 | {302C4176-4830-4D29-8953-2FECE7A076EF}
LINCOLN 1104685276 | {62CF7EB0-1F27-4DAA-93C0-D5A9F63BB597}
LINCOLN 1104693294 | {68BE4BEA-6B01-4263-BF4A-085FBF6C3513}
LINCOLN 1104818790 | {C5EA5C15-1CF5-4589-BD9C-EEF6FE17F558}
LINCOLN 1104997576 | {35BF67BB-6CEB-47E1-A7A5-F5CC82DEAE9C}
LINCOLN 2109924404 | {D78EA46A-E23B-4345-8961-C542C9C645D9}
LINCOLN 2109CB | {4E6AFF3A-F560-4015-9A7B-59C83CDB47B7}
LINDEN 1103542460 | {20BF9716-345C-4355-8648-C5A90D0DDDB0}
LLAGAS 21013835 | {BE437E1D-C597-4FF3-91BC-AAF18CB33659}
LLAGAS 21014523 | {4A87133B-C25C-4081-8935-66AE4E30F1EA}
LLAGAS 2101984552 | {689A7047-6554-469D-A572-0CDDE35EC73D}
LLAGAS 2101XR244 | {133545C9-FF59-4E89-AB9A-6D025A3D74E4}
LLAGAS 2101XR264 | {6D5B6410-E4BE-4661-9810-568D00627E89}
LLAGAS 2101XR584 | {4A87133B-C25C-4081-8935-66AE4E30F1EA}
LLAGAS 2101XR586 | {BE437E1D-C597-4FF3-91BC-AAF18CB33659}
LLAGAS 2101XR586 | {B1426F28-A34B-4992-80A9-A93CA76693A1}
LLAGAS 2101XR586 | {775E1FFB-162C-4436-A1F2-3394B067012F}
LLAGAS 2104603392 | {28E6C6D7-8DD9-401F-863B-133430EA57C4}
LLAGAS 2104735530 | {AF07F25E-155C-4D19-8872-642A3CCD5556}
LLAGAS 2104XR148 | {C84A9225-11AD-48B0-B13C-5F9DBEE07DEA}
LLAGAS 2104XR242 | {AF07F25E-155C-4D19-8872-642A3CCD5556}
LLAGAS 2104XR294 | {F11F1581-106D-4267-B291-AD8060715445}
LLAGAS 2105XR234 | {90264C2C-3ED3-42D6-BFF5-F41E927FBBE3}
LLAGAS 2105XR234 | {A3614058-D6F6-498F-B865-E27268AA97F2}
LLAGAS 2106338878 | {699C93CA-B67B-4D5A-B3DE-FBF338954446}
LLAGAS 2106517530 | {AC148FB9-082D-4C31-9937-1A18D38D116C}
LLAGAS 2106CB | {36DDC7E6-DD90-43BE-A64F-8D62BC22EEA3}
LLAGAS 2106XR296 | {36DDC7E6-DD90-43BE-A64F-8D62BC22EEA3}
LLAGAS 2107142710 | {E4B7388D-56E6-4038-9DF8-2387BF129F0C}
LLAGAS 2107374344 | {40BE7D0D-D7B9-4C64-B06B-437270976420}
LLAGAS 2107870396 | {4DC0A76E-797A-4818-B053-21B7BC501B6E}
LLAGAS 2107CB | {DD8395FC-A049-4EDA-8DC5-FEEBE3B0FF15}
LLAGAS 2107XR188 | {1B5D7998-B20D-4848-BE59-22884992869D}
LLAGAS 2107XR188 | {7FBBA027-0AB6-47D3-B07E-8956861A85DA}
LOCKEFORD 210212468 | {34045FAB-FD0E-4469-952F-B8E16E6D8945}
LOCKEFORD 210220355 | {34045FAB-FD0E-4469-952F-B8E16E6D8945}
LOCKEFORD 2102206884 | {2D298F6A-BEA8-4B07-AC26-301AFF0706CC}
LOGAN CREEK 21022226 | {0DB23F18-2307-44BE-917D-7278F1DC4733}
LOGAN CREEK 21022428 | {44523332-7517-43E5-BC5F-36858B2AD5AD}
LOGAN CREEK 21022540 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
LOGAN CREEK 210237316 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
LOGAN CREEK 210247194 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
LOGAN CREEK 210262032 | {BEFCE23A-309D-4D6F-8ABD-50878BF1EA08}
LOGAN CREEK 210269358 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
LOGAN CREEK 2102767046 | {E8966EB9-3CA2-4993-8729-F6FAD99583CF}
LOGAN CREEK 2102806 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
LONE TREE 2105708440 | {277CEF50-D68F-45AB-A795-84B9ACDD656A}
LONE TREE 2105CB | {BF1E0B7F-6FE5-43AC-AD5E-51535747C12F}
LOS COCHES 1101625902 | {24A896E9-4BBF-4DA8-BD42-A7972EEB8C30}
LOS COCHES 110255146 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
LOS COCHES 110256346 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
LOS COCHES 11027046 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
LOS COCHES 11027514 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
LOS COCHES 110275272 | {EE0BDD3D-35F5-4175-A0F2-FD670912F53D}
LOS COCHES 1102CB | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
LOS GATOS 1101206248 | {C5B5434F-C05F-41A4-93CB-6D3F98039D91}
LOS GATOS 1101502026 | {E1FA2A15-AD3C-4DAF-93F8-E10F60AD1FB4}
LOS GATOS 110160052 | {D47892F1-0CB0-45EA-A4B1-629482BAEB79}
LOS GATOS 110160136 | {A1B517D1-7F5E-496E-A188-34F488988F32}
LOS GATOS 1101CB | {B81601D3-2F43-44C7-B6E6-ECFC64FD48AF}
LOS GATOS 1101CB | {168FAC6E-221A-4D80-AD26-79821278B765}
LOS GATOS 1101LB40 | {2E2463B4-F331-472F-B632-0DB9F9C1E4AF}
LOS GATOS 1102526868 | {40479F22-BBD2-4DBE-B231-5BD9D16BE0F7}
LOS GATOS 1102CB | {9CE095E8-15BC-49D7-95AC-553D14C8CC1F}
LOS GATOS 110660116 | {86E17BC0-A879-45C0-9429-4A0FD02BA21E}
LOS GATOS 1106697500 | {5B274F91-3DCC-4D8C-9FA0-4D35A285F7F0}
LOS GATOS 1106917258 | {F0513295-9AFE-47CC-93E8-DF299D8C11AB}
LOS GATOS 1106CB | {D03187F3-5053-4E30-B164-D057F0065569}
LOS GATOS 1106LA64 | {CFFA07B9-8209-4D21-824C-C9A2945C083F}
LOS GATOS 1106LB44 | {41876CDD-E960-4684-B78D-E48B7ECC5753}
LOS GATOS 1106LB44 | {661964DE-1394-445D-8404-1E88A5E86A52}
LOS GATOS 1106LB44 | {5D70BF4D-C1AE-452C-84AB-8E4767458B84}
LOS GATOS 1106LB48 | {ED4FFAA8-32ED-4B25-8B3D-9D1525DB179F}
LOS GATOS 110760024 | {F77EAC7B-DF34-46F0-9E63-E76A1EA4BA50}
LOS GATOS 110760092 | {FE58AABB-4F2E-4F6C-8A2E-70A2F4BDC1F4}
LOS GATOS 110760114 | {9B2D8A48-20CB-454C-BA37-343177467945}
LOS GATOS 110760118 | {015FA28B-9402-44F1-AF6E-8F414A68AEDF}
LOS GATOS 110760118 | {996F801A-49DB-4E12-9C16-86F37BF363D7}
LOS GATOS 1107639614 | {A57DA086-5167-4A5A-95F0-BA291DD6146E}
LOS GATOS 1107772050 | {2D8F3B80-1078-4F21-A2C2-0C45F69D55BE}
LOS GATOS 1107781232 | {DB1D2199-2671-4DFC-86B0-02A91629C7CA}
LOS GATOS 1107812664 | {5685685F-A6FF-42EC-B764-0A6E777F0FC6}
LOS GATOS 1107914254 | {DCEB87E4-E9AF-44AC-9CD1-F1B1DDA3FBC9}
LOS GATOS 1107CB | {F9DF48B9-C722-406C-B401-60189B57E89A}
LOS GATOS 1108590544 | {181A63BB-5CD3-4EBE-A88A-6C87700E0247}
LOS GATOS 1108CB | {52AE67FA-770A-4A3A-8316-07026BFE1782}
LOS GATOS 1108LB86 | {179FE519-944E-4835-9C33-84ABCACF7D82}
LOS MOLINOS 11011308 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
LOS MOLINOS 110154804 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
LOS MOLINOS 110163998 | {13B78A6A-8DA9-4023-969C-3CD765D0B389}
LOS MOLINOS 110171402 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
LOS MOLINOS 1101CB | {2F05D844-382F-480E-A414-A8255A95CC97}
LOS MOLINOS 11023302 | {3C29BFDD-B708-4EA4-82F6-BE02F2280B00}
LOS MOLINOS 1102CB | {3C29BFDD-B708-4EA4-82F6-BE02F2280B00}
LOS OSITOS 21011132 | {4039D191-A1E0-4943-9C3A-CC09D2E36841}
LOS OSITOS 21017014 | {1106E17B-9FEA-4422-BC78-03AC3BC8E250}
LOS OSITOS 2102148504 | {36658DA5-CDD3-486F-B061-605207C26350}
LOS OSITOS 2102258878 | {03FDC6F0-8EFF-4D98-B64E-FE44DDCDA68D}
LOS OSITOS 2102624200 | {55FFD10E-AE85-4366-9D32-F7DB90B5CFE9}
LOS OSITOS 21027592 | {3616477B-E0BC-4A69-8662-9C027B6A345B}
LOS OSITOS 21031132 | {4039D191-A1E0-4943-9C3A-CC09D2E36841}
LOS OSITOS 2103174580 | {215C3316-AD64-4D86-B319-9811218FF7C5}
LOS OSITOS 2103220608 | {B9039DB0-DC75-45BF-9F2C-149A67BBE1F8}
LOS OSITOS 2103258688 | {095C4297-BB9B-47AE-9B30-7513251297A3}
LOS OSITOS 21033010 | {528CF887-3009-4BDA-941C-23A6FE9B29B6}
LOS OSITOS 2103606732 | {215C3316-AD64-4D86-B319-9811218FF7C5}
LOS OSITOS 210364348 | {8276CB14-B72D-46E3-83F9-1F1DCC6858E6}
LOS OSITOS 210366936 | {29735F50-C5F4-4F83-8013-D3D04A895748}
LOS OSITOS 2103695270 | {40F1B87F-AB3F-4DE0-8638-58D9EA205806}
LOS OSITOS 21037014 | {1106E17B-9FEA-4422-BC78-03AC3BC8E250}
LOS OSITOS 21037062 | {113FEF80-B5A7-4041-A279-F58DE4B71B87}
LOS OSITOS 21037082 | {E273F09C-00C1-48A4-A71E-352A62A15E75}
LOW GAP 1101274514 | {1F44035F-9F44-4D9D-BD78-79FFE4020D74}
LOW GAP 110137498 | {BD574B29-15C8-4B0E-8A1E-85F74B10E15F}
LOW GAP 11014086 | {71DE392B-20E6-4124-9FFE-851197719244}
LOW GAP 11014160 | {C206EE4F-0006-4ECA-9B96-00B5245745DE}
LOW GAP 1101449990 | {9677DC50-AB85-42C6-9822-52AD410900D7}
LOW GAP 1101603404 | {270C7C31-4E44-4C5F-A109-764C7D9C23E5}
LOW GAP 1101750090 | {7EAB9CA9-F4EA-480A-8BE4-2E97F9009D2B}
LOW GAP 110186816 | {35FAF06A-E239-4015-A854-21F6A4EC4F03}
LOW GAP 1101CB | {5346AC49-CDE1-40C3-A681-DA76F08A9FA4}
LOYOLA 1102429970 | {13464ED5-9F48-4024-B104-3201B180FAC2}
LOYOLA 1102550291 | {DEF8A973-66EF-4B4B-8E5E-9D523DD1F02E}
LOYOLA 1102550291 | {379AF1A9-16E4-4C0C-BE5C-4BB0C4F98451}
LOYOLA 110260128 | {6582F831-14AD-4AED-9367-19CCB6CFBE91}
LOYOLA 110260128 | {A6F27353-D8D5-4597-90A2-CB1701C67449}
LOYOLA 1102CB | {E303C5AD-824F-4E47-B866-CA2B13090981}
LOYOLA 1102CB | {27A786CD-A523-48EE-89CB-20E33A9B5F17}
LOYOLA 1102LL12 | {FC7EF3C1-E676-4F19-A408-525DCCC4AA40}
LOYOLA 1102LL62 | {AB8403D1-2343-4452-8395-9C954CC8DC13}
LOYOLA 1102LL64 | {8FF2C357-E560-4F49-BD6C-1A85C9D294D8}
LOYOLA 1102LL66 | {9C5A5E3E-259E-4BA4-92AC-E564F3B34976}
LOYOLA 1102LL86 | {2FF7416F-A3A8-49DE-8B6E-03DC5E89A659}
LUCERNE 11031280 | {A05AE75B-B8B1-4EF0-A327-427A302D4FDB}
LUCERNE 11031663 | {F34B7A71-9435-4BB4-952A-AC8430FF4984}
LUCERNE 1103245134 | {C983D5DD-ECD3-42F8-923D-50B966424F38}
LUCERNE 110327932 | {93D2CEDB-A4A6-4F60-93F8-470CFD18E884}
LUCERNE 11034200 | {0AEE71D0-17A5-4B33-BC11-93FDB3F0422F}
LUCERNE 1103438776 | {3F463C9A-62CC-48DC-94B5-9AFB49692D9B}
LUCERNE 11034624 | {4100FBA2-C458-44C1-B317-2EE92F5C04AB}
LUCERNE 1103630 | {F34B7A71-9435-4BB4-952A-AC8430FF4984}
LUCERNE 1103721 | {4100FBA2-C458-44C1-B317-2EE92F5C04AB}
LUCERNE 1103CB | {F830099C-EEA2-4CF4-B68F-D2F012925468}
LUCERNE 11062327 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
LUCERNE 11062355 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
LUCERNE 110638436 | {790F1996-ADCE-423E-BD1D-F157FD535C39}
LUCERNE 110638632 | {11292177-63B4-4D1D-9B97-B2A90B30A4AD}
LUCERNE 1106439842 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
LUCERNE 110647198 | {DA9B8D37-5C46-437A-B55A-1CC1BE987A25}
LUCERNE 1106480110 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
LUCERNE 1106526 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
LUCERNE 1106664 | {7BCF996F-5D44-49DD-8430-629850EC151D}
LUCERNE 1106709252 | {DE7938AC-4236-44EA-970B-170B6BDC431A}
LUCERNE 110676850 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
LUCERNE 1106857174 | {64C6F4FE-9745-4B83-9BA2-6905B1D464FF}
LUCERNE 1106988590 | {03794043-4739-4484-8FAE-7CD50FBF19C7}
LUCERNE 1106CB | {64C6F4FE-9745-4B83-9BA2-6905B1D464FF}
MADISON 11057712 | {2C14C00C-0CAD-4E64-99CF-10447EDEECD2}
MADISON 2101117644 | {03566FC1-B4DF-4D1E-A42B-48526D62FDEC}
MADISON 210112321 | {0CB657DB-6DA6-4A9D-A1FF-01F4FF1F9C5B}
MADISON 21011606 | {892EE518-0261-403B-AEBB-DE522B481F93}
MADISON 2101168918 | {9C777D0B-81EB-422B-9E3E-C0277E2A4B3B}
MADISON 21011943 | {DCC4F33D-94BC-4C20-B81E-44479B092EB6}
MADISON 210120052 | {3606619A-937D-46E3-AFC7-2B9E8CB032C3}
MADISON 210123272 | {C4B928B0-1315-4EFF-A9DD-F47090119304}
MADISON 2101274974 | {BBB7A181-0979-426C-AED4-D3871931C8AC}
MADISON 210134164 | {C4B928B0-1315-4EFF-A9DD-F47090119304}
MADISON 2101351038 | {9C777D0B-81EB-422B-9E3E-C0277E2A4B3B}
MADISON 210137082 | {8E6B668B-C3B5-476E-8081-82E065E91883}
MADISON 210144634 | {522A389A-AB26-4856-B015-C925A695BEA6}
MADISON 210144634 | {3606619A-937D-46E3-AFC7-2B9E8CB032C3}
MADISON 2101484892 | {64480341-2026-4E64-974C-9602D07F2EA7}
MADISON 210163762 | {FAFBD2A1-FFC3-48C9-9B09-E9ECE3AD7FAB}
MADISON 2101647730 | {9C777D0B-81EB-422B-9E3E-C0277E2A4B3B}
MADISON 21016617 | {FAFBD2A1-FFC3-48C9-9B09-E9ECE3AD7FAB}
MADISON 2101725408 | {A1A5DB3C-6B99-4418-9DB8-859C77A01E6D}
MADISON 2101732852 | {AC75A34F-2C0F-431E-97C9-68AB1FAD1B58}
MADISON 2101760730 | {0CB657DB-6DA6-4A9D-A1FF-01F4FF1F9C5B}
MADISON 21017702 | {DCC4F33D-94BC-4C20-B81E-44479B092EB6}
MADISON 2101845694 | {9F1D585F-4585-484D-A04F-23919C37AC0A}
MADISON 2101888814 | {7332DE5F-6F7A-45B8-8DD4-5630772AAE8E}
MADISON 210189332 | {D7243FB0-38B4-4640-8C10-2CD25C9CD868}
MADISON 2101936212 | {BB2CEA8E-784A-4217-8D58-EADEE452F20C}
MADISON 21019512 | {C556C375-7B0E-4693-B801-A5D6F39CB3E2}
MADISON 2101CB | {EA6111A8-7AB9-443D-A740-55705E7BEA72}
MAGUNDEN 1108250674 | {9C5EB345-7F42-4EDD-AEC2-EDD4964080F0}
MAPLE CREEK 11016906 | {8625CA5E-81C0-4BA4-B083-5D0354E4556D}
MAPLE CREEK 1101CB | {D3EDA1A2-8AF8-4A2A-853E-161161439812}
MARICOPA 1101931236 | {4BEF20F2-8B61-45E8-BE0E-DD28930DE8C2}
MARICOPA 11023082 | {F0D3E110-E06F-4F39-B085-758DD01FFE6B}
MARICOPA 11023558 | {341A5947-0E50-4A7D-9C85-BBC1E06228CA}
MARICOPA 1102453320 | {34FDF5FD-B2A0-4EFC-9338-7E46284554C8}
MARICOPA 110265196 | {341A5947-0E50-4A7D-9C85-BBC1E06228CA}
MARICOPA 1102CB | {3886D126-B275-4867-A304-EDF3653324EA}
MARIPOSA 210110070 | {26575688-884D-4CC7-8C04-F1F692E3F0D5}
MARIPOSA 210110170 | {36E417A9-B355-4038-92B6-BA6B805D598D}
MARIPOSA 210110240 | {4272B914-DD96-40AD-9866-404625A4A67D}
MARIPOSA 210110990 | {8667D6C6-0139-493E-962E-C5EBDBB9ECAB}
MARIPOSA 2101151918 | {AA9A1768-272F-4017-B4A9-F1105C658F25}
MARIPOSA 2101309438 | {50B1E436-CAE2-4BB7-88C4-FB7945F4E49E}
MARIPOSA 2101439030 | {B1C3BF34-DFE5-420F-B7AD-C0CAC681FC7D}
MARIPOSA 21014410 | {6FC28AC3-D7E2-4D2C-9C34-2FD4A55CB839}
MARIPOSA 2101752630 | {482F0B3D-137A-48C9-9E82-504F3E80E798}
MARIPOSA 210190180 | {DD0025EB-B991-46AA-8D21-AE164B513DA5}
MARIPOSA 2101929360 | {F15FE3D9-E711-401A-B57D-CC1BD9F02B6F}
MARIPOSA 21019400 | {D298C9EB-7969-4020-A299-D9B72D648E9A}
MARIPOSA 210197142 | {5AF7FF1D-FC61-4F2B-B337-918BFB6B463C}
MARIPOSA 2101CB | {050E06AF-91BE-429B-BDFE-3EAD80F24863}
MARIPOSA 210210880 | {AF85260C-2339-49D2-94BE-A2E04CBD4128}
MARIPOSA 21021960 | {C88CD342-0019-4371-8FA7-CA6CF25A5380}
MARIPOSA 2102241564 | {96707C24-07B2-408B-B719-59181F4D3F8C}
MARIPOSA 210237282 | {9C7CA36A-A220-4889-B18C-7665D5C736E3}
MARIPOSA 210237288 | {38642A96-8776-4716-B709-CC59463C3DA7}
MARIPOSA 2102527766 | {E89F466E-8BA2-4F18-BDD7-EDCC9695F74F}
MARIPOSA 2102594143 | {ECC5358A-3849-4B2A-9964-68FBF1B8D64E}
MARIPOSA 2102851902 | {E2D52595-66C4-483A-AAD4-1CA021357A15}
MARIPOSA 21029590 | {43662797-F521-40C6-867F-8BCF69F03BE0}
MARIPOSA 2102CB | {D6398899-238B-49AC-A776-D1F3468DFF9B}
MARTELL 110111244 | {E154310E-F1E3-4CE7-BE08-29FE6DF23F68}
MARTELL 110111244 | {FC415CBA-4F79-4B55-9784-C587178D6775}
MARTELL 1101131918 | {1E70E468-70D3-4521-B520-5062F501223B}
MARTELL 1101185268 | {9AC31B24-B4F5-4AE8-AF6A-88CA4695FB5D}
MARTELL 1101473004 | {8976069E-D4D6-425D-AFC7-6113345355FC}
MARTELL 11016074 | {52B817B8-3607-4215-94CE-6DB0D80039B6}
MARTELL 1101766574 | {2486729F-70E5-4A37-897B-69C2538DBD37}
MARTELL 110191216 | {111B8F03-A7A2-4ADC-B553-BFBB68F5B187}
MARTELL 1101915018 | {31785B7F-FA02-4970-9573-C491E47D5BE1}
MARTELL 110198374 | {277F84D3-A270-449A-A58E-FDC1A84261F4}
MARTELL 1101CB | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
MARTELL 110292172 | {90FE2AC1-F695-42FF-8EBC-FB82E3B206C0}
MARTELL 110299214 | {9F8CA5FE-A9BA-4EDC-994E-2CFB4235B5A0}
MARTELL 1102CB | {74DC8F54-4589-4421-89BC-E98BD5920B33}
MARTELL 11033152 | {138F1A45-4EE4-407C-9580-B6FBC2BCEC83}
MARTELL 110368192 | {2D2F9EB5-C573-4256-A9F2-6087D93C70C6}
MARTELL 1103CB | {4DC1CEF2-A050-43F8-AD47-CFA46D056F9F}
MAXWELL 11023306 | {F1C1856B-ECB8-4CF9-A778-CDB8457E4724}
MAXWELL 11053008 | {3FFCF8AB-2F3C-40D6-BE9B-68EE284722AE}
MAXWELL 1105429752 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
MAXWELL 110545180 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
MAXWELL 1105910362 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
MC ARTHUR 11011488 | {62976FAC-DE1E-4247-A5CB-A153442821DF}
MC ARTHUR 11011490 | {36BB4228-C5D9-43D2-9CAD-2C575004638F}
MC ARTHUR 11011492 | {4752BF93-70F8-42FC-8D3A-033549B0C98A}
MC ARTHUR 11011544 | {2548B457-03C9-4EEF-9E95-D0AA3CBA5A67}
MC ARTHUR 11011546 | {F58DF78A-C4B0-4969-9413-98D7022EFF8F}
MC ARTHUR 110137344 | {385A8486-C3EA-4FD6-BFA5-2F73ECF426BB}
MC ARTHUR 110137388 | {94162D16-0097-44C8-A147-FCAA580DD744}
MC ARTHUR 110138998 | {FAF0B739-3196-4C1D-A8BD-B6B12F707FEC}
MC ARTHUR 110151398 | {85EE7B40-6D93-48B5-9C94-EBAACB072BA9}
MC ARTHUR 110153120 | {4F05ED84-FE56-4A90-8DC4-86D939A68626}
MC ARTHUR 1101648698 | {21F41FBB-70A7-4D16-B9FC-2C23C6369432}
MC ARTHUR 1101CB | {180C9221-B3D3-4A32-9DB9-CD8B7E0EF9F1}
MC ARTHUR 11021324 | {76F913B6-6D49-4D3C-ACC8-2AE24DFE45A2}
MC ARTHUR 1102542920 | {937AC6EE-B826-41A2-9509-4DF206B104A5}
MC ARTHUR 110290546 | {E9334D2F-2952-4052-8ADD-E3F42DB77666}
MC ARTHUR 1102CB | {29D96E6F-9A6D-4E41-9CE1-0E9E869E48D9}
MC ARTHUR 1102LR-RC-B | {E9334D2F-2952-4052-8ADD-E3F42DB77666}
MC KEE 1103333750 | {91B9F546-2D22-40C9-BFB6-88E720FB1011}
MC KEE 1103XR028 | {58E90993-9BBD-4F51-9BA9-AD36025808B4}
MC KEE 1107827486 | {625462C6-F8FB-4C1B-B9B9-64AC08211124}
MC KEE 1107CB | {0AA07E65-EBF5-454E-BE3D-8A46CCE84946}
MC KEE 1107XR010 | {450C95A5-CC86-42A5-8643-E83181385ECD}
MC KEE 1107XR032 | {22D0F857-9929-4CD2-9E4F-9210026EF7ED}
MC KEE 1107XR462 | {AA6D8683-68CA-48B3-8BCC-B0F7A769A3DF}
MC KEE 110870535 | {AD405CD0-0159-4CF6-B66D-D87E1CD73921}
MC KEE 110870535 | {41444F7B-0DEF-4E7D-BF1A-12A503159CC6}
MC KEE 1108XR302 | {41444F7B-0DEF-4E7D-BF1A-12A503159CC6}
MC KEE 1111247498 | {7D5CF815-4517-41ED-97D9-FB9721A1C53C}
MC KEE 1111711900 | {E158EBD1-D391-40F7-8D5C-4284F51B8199}
MC KEE 1112XR098 | {B0BB35CF-4475-436C-B6E7-59AB619EAF5A}
MCKITTRICK 11011639 | {0CBC2090-103A-4482-AE0F-2EF4734EAF78}
MCKITTRICK 11013043 | {5A307946-5CD5-4050-AB0D-2E455B17B341}
MCKITTRICK 11013092 | {5A307946-5CD5-4050-AB0D-2E455B17B341}
MCKITTRICK 1101CB | {5A307946-5CD5-4050-AB0D-2E455B17B341}
MEADOW LANE 2106970936 | {9C56F556-90B8-48FA-A28A-448032E1972B}
MEADOW LANE 2106C537R | {9FDBE41D-F5FA-4A91-8801-9FABAD55128D}
MEADOW LANE 2106C558R | {9FDBE41D-F5FA-4A91-8801-9FABAD55128D}
MEADOW LANE 2106CB | {71331D65-41F4-43C6-916A-15339389D82C}
MENDOCINO 110131322 | {DE700694-1BC1-42F0-BD3F-498F1D5E0950}
MENDOCINO 110137462 | {CBF297F1-D8F4-467D-B156-4EC62C764040}
MENDOCINO 1101450 | {8EF50422-5CB8-4728-A990-D408AE9FCE63}
MENDOCINO 110148750 | {EF680142-96BC-4632-8839-A0A3D923AC61}
MENDOCINO 110148750 | {ACEBC5C5-BAE3-4674-A040-F1DC8C4CB67D}
MENDOCINO 1101856020 | {20843552-BA63-4B51-9A53-4527FFEFC797}
MENDOCINO 1101CB | {D8D35F92-2CE4-473E-A048-B7A252678CA3}
MENDOCINO 1102CB | {988CA71C-AB6C-46A7-920F-6295BBF50876}
MENLO 1102151590 | {57607E85-0D9E-4982-8503-00EDF257DC69}
MENLO 1102154024 | {C583B40D-86CD-4D00-B0BD-8B42D03F7715}
MENLO 1102223286 | {ADCE2FC0-63B1-4997-AA36-C71BC01F8536}
MENLO 1102331044 | {86766416-7CB2-4969-8319-B838E7BDEB74}
MENLO 110235722 | {56AE0E26-A1EF-48A8-89D1-72A26BF969A5}
MENLO 1102362896 | {414B8FEF-04D8-45C9-AB62-09E735CC943C}
MENLO 1102560798 | {9F355D1B-96B2-4F1B-AC5A-69166E99F7CE}
MENLO 1102628458 | {8DAF1791-FC97-4AAB-A29C-384C99616E7D}
MENLO 110276134 | {6CA76C53-8C3A-4667-92BB-084EB68DB35C}
MENLO 11028952 | {56C84CD8-CFAF-4218-882A-B93134A396EB}
MENLO 11029018 | {D2B478D6-3AC8-4C31-9F67-86F64FEB69F8}
MENLO 11029092 | {CB7FED94-E514-4F6A-B3B1-FDD03272551C}
MENLO 11029110 | {2ADB84B9-4752-4713-BF49-15F96D94E1DF}
MENLO 11029110 | {4FA0951E-FDEC-4E9C-847F-B2E9B3A5118A}
MENLO 11029152 | {6B11615C-09AD-4BEB-BBFF-976212C3FB13}
MENLO 11029152 | {844542AF-23E3-4A9F-A1D2-E72C86286BF7}
MENLO 1102W80 | {82B72724-3F36-4DE0-AF4C-310E9BC3E997}
MENLO 11031721 | {6C22C535-7647-425F-9042-42388B8EC195}
MENLO 110358562 | {7E0C3FCE-17F5-4308-9D58-E63D0E2C9C4E}
MENLO 11037902 | {8A15255F-3865-4264-A6D3-8F9EE2AA73EF}
MENLO 11038512 | {8F9D0578-4CB4-4781-89AC-7B1C36D45FF0}
MENLO 1103866118 | {6C22C535-7647-425F-9042-42388B8EC195}
MENLO 11038982 | {122C7DAC-AC52-4005-A738-CAEFD4E1581A}
MERCED FALLS 110222774 | {A07075F3-76AA-4FC7-9158-0930DA76C5B7}
MERCED FALLS 110238748 | {E473F3E7-4790-4E95-BFB6-2DFAB51C8E70}
MERCED FALLS 11024000 | {8DA8BDD3-B9B9-42D9-AC7D-1174537479B6}
MERCED FALLS 1102482838 | {A07075F3-76AA-4FC7-9158-0930DA76C5B7}
MERCED FALLS 11027006 | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
MERCED FALLS 11027905 | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
MERCED FALLS 110285002 | {9E750160-198E-4DE4-9B67-A39CCFF98BD9}
MERCED FALLS 11029460 | {0E4DE50B-9CB6-46AA-9EAF-66A90C70B824}
MERCED FALLS 11029470 | {C35DFEFE-AAAB-47B8-ACD8-3B6A331D2855}
MERCED FALLS 1102CB | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
MESA 11016111 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
MESA 110187454 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
MESA 1101CB | {C61DB78B-3364-4B90-90AD-4E89668B63A7}
MESA 1101M86 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
MESA 1103126697 | {431342B2-8FA7-4C4E-B028-5E0C383A0588}
MESA 1103198354 | {E778BF74-7BEA-4E28-9448-C0888C04BB6B}
MESA 1103206794 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
MESA 11038647 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
MESA 1103M62 | {A1CF0EFC-4EE4-402B-B14C-F1C9D9E90F01}
MESA 1103M64 | {88268CAB-906C-4CD2-A318-8F214ED37905}
MESA 1103M68 | {A25F3E5B-484A-4624-AB7F-2585CAD6EACC}
MESA 1103M70 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
MESA 1103M72 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
MESA 1103M72 | {1D9768AD-9367-4361-8E84-3FE59F96E5B9}
MESA 1103M90 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
MESA 1103M92 | {2DBCA866-9F0D-46E8-B9B3-4863FA94560D}
MIDDLETOWN 1101128648 | {B7C3ED67-9905-41F0-81DC-45B8DE5466D9}
MIDDLETOWN 11011314 | {6605C9B9-1E01-4CAA-B9F4-139E3DFEC103}
MIDDLETOWN 1101171414 | {4E6A64C0-71D5-4A3E-830D-222E13830247}
MIDDLETOWN 1101352182 | {AEB7C7BA-C773-4591-86C0-9A5CE1531025}
MIDDLETOWN 1101433160 | {335DA010-DDD8-4033-B175-13202F25D46A}
MIDDLETOWN 1101439572 | {30AF65A1-8215-4D53-AAD5-8454B0E2F1C0}
MIDDLETOWN 11014646 | {9CD0DE6C-67D0-4975-9926-0CEC6137D8E0}
MIDDLETOWN 1101481876 | {218A19AE-6FB1-4AFF-A311-4C487EC96852}
MIDDLETOWN 1101548 | {F67E867C-FC38-4763-8DCC-25139EFCB73A}
MIDDLETOWN 1101614 | {8C7E457A-F935-48E0-AE77-B73661F39EFF}
MIDDLETOWN 1101644756 | {ADE0CDA9-E9B6-443E-8AB2-EB2705916002}
MIDDLETOWN 1101644756 | {D8404B1C-6CCC-4D8B-B9BD-7DBA7207B8E8}
MIDDLETOWN 1101644756 | {67FA5D3B-5BFA-40EE-AABA-659446964531}
MIDDLETOWN 1101829164 | {2CB71B6B-D27A-41C2-BF19-6EE1B740E120}
MIDDLETOWN 1101872796 | {BEAAD6A3-94CD-4A11-9128-481E49933A68}
MIDDLETOWN 1101932140 | {50574C53-8D5E-4BF8-9D16-15E783D9947A}
MIDDLETOWN 1101959140 | {7B530842-C667-418B-ADA6-859E3E2891D3}
MIDDLETOWN 1101CB | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
MIDDLETOWN 11021312 | {EAE1C088-E6A0-4B00-80D2-C64BBF575702}
MIDDLETOWN 1102414 | {01278228-324E-4DE9-A0E4-67F4CFACFDAB}
MIDDLETOWN 1102620498 | {D18513DF-0BE1-400C-9F93-B0C29A8ABBA4}
MIDDLETOWN 1102632616 | {AB543CBF-7DF0-478A-B296-EEDA3DC9B71E}
MIDDLETOWN 1102878 | {41D0BC1C-9410-4D80-BAA4-E58808DC7687}
MIDDLETOWN 1102998 | {5F8C3D5E-6EE2-44BA-8DAB-1423918270D0}
MIDDLETOWN 1102CB | {7E69B413-A223-4CCD-AF98-CC3C74EA7FDA}
MIDDLETOWN 1103248100 | {BFCA66E2-7174-4D82-9BEB-7987B154BF74}
MIDDLETOWN 1103762090 | {32E7D0CF-C321-47A0-BEF1-9DB8DDDC7A60}
MIDDLETOWN 1103CB | {EF7692CE-6490-45CF-89E0-AAC63F03AECA}
MILLBRAE 1104217 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
MILLBRAE 110453676 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
MILLBRAE 11045521 | {29B1D2E9-693D-479C-A160-99B72B4A4B3F}
MILLBRAE 110465748 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
MILLBRAE 110480106 | {BCA1AB36-1D1B-41D7-93BD-733AB9EA3274}
MILLBRAE 110810045 | {D144CF0B-F99D-4FA8-AE9A-F2C7682917BD}
MILLBRAE 1108639978 | {8FFF56B3-5742-48DE-8779-85060D8D7011}
MILPITAS 1105CB | {CA512FE5-1127-458F-8A35-7AA6286C673F}
MILPITAS 1108342498 | {89380520-9418-4EBF-BBE0-5B16221F5D8C}
MILPITAS 1108819378 | {CEA38244-9552-4630-967D-EBD8BC18D96E}
MILPITAS 1108CB | {7055FF43-DD9D-44C9-B3AE-9B73AF61A173}
MILPITAS 110913377 | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
MILPITAS 110962157 | {9C37E848-C9FB-4404-B824-088800AAA1AF}
MILPITAS 1109903328 | {6577B24E-0FC5-4239-89A4-458F673DCDA9}
MILPITAS 1109CB | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
MILPITAS 1109XR044 | {AAFA242E-CE7C-45BF-A927-201DEB4735C4}
MILPITAS 1109XR208 | {1C76A5CB-14FE-4796-B246-F53503C2A0BB}
MILPITAS 1109XR370 | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
MILPITAS 1109XR372 | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
MILPITAS 1109XR374 | {0C3DEB50-B6B5-4438-9654-82B0930BBF12}
MILPITAS 1109XR524 | {648B5D01-67D3-492E-989C-FF81490722DD}
MIRABEL 1101116 | {1FA8A5B8-216C-48A5-8B5C-D037DBE66063}
MIRABEL 1101228 | {42913E65-3605-4DBB-8857-B0B0965C9EAC}
MIRABEL 1101254 | {E6BD4324-CEC6-41E3-9006-EBD82C1FE66D}
MIRABEL 1101298 | {6A524B23-035A-4EEE-9B4D-9C835025E39B}
MIRABEL 1101298 | {1B23A4BA-CD57-4FC0-AB6D-FA127475AD96}
MIRABEL 11014859 | {1B23A4BA-CD57-4FC0-AB6D-FA127475AD96}
MIRABEL 1101688780 | {47D4786A-45B9-45D8-AF62-3522AA9D4ACB}
MIRABEL 1101774276 | {D2D7F3DD-F11E-4D5D-B608-61ABEEEF3513}
MIRABEL 1101774276 | {403F76F2-1613-4EA6-AE9B-C646D2E770BD}
MIRABEL 1101CB | {8146354A-DBE2-49BD-B0E6-646A6C01C7BC}
MIRABEL 1101CB | {0DAF681A-D0A6-472F-BDFE-814CD10BFA9B}
MIRABEL 1101CB | {27F10E9B-AFB8-46BC-9219-36028EB8F5A3}
MIRABEL 11022043 | {76DCCACD-E9DC-40E0-8CEA-2EC1A63EA736}
MIRABEL 1102206 | {3FDFEE62-2564-4B56-8AC9-FC80D427FADF}
MIRABEL 1102332 | {98884EB6-8FFE-4527-976C-FBFB7D667FB9}
MIRABEL 1102334 | {0A4816B0-BB69-491B-8E9D-476A9DF6F15C}
MIRABEL 110238514 | {76DCCACD-E9DC-40E0-8CEA-2EC1A63EA736}
MIRABEL 110238514 | {7C9E0EEA-95C0-41CC-9185-303F6237320D}
MIRABEL 110238514 | {A5155BE5-9970-4D8F-96F2-81F9FC945582}
MIRABEL 1102503000 | {02C10BAA-6FFF-4F80-AE34-8D1403D92CC8}
MIRABEL 1102503294 | {F1ABA083-74D1-4C3F-BF47-7B099CCA3C8E}
MIRABEL 1102524356 | {93EAC16B-EBC7-4B14-81C7-36C500A3A6BF}
MIRABEL 110257840 | {BDF5B432-76F8-4E7C-875F-0CD4088812BE}
MIRABEL 110286326 | {F24A6BFB-F462-4C79-8226-3FA35A366957}
MIRABEL 1102976908 | {EFEDE1C8-AA0B-47C4-96EE-71FB2C33E43D}
MIRABEL 1102CB | {C5E1652A-2EB6-4FD0-B328-E1AC1FDEB33B}
MIWUK 170110600 | {38AAAE1F-7053-4022-8941-265790AA8F13}
MIWUK 170111800 | {CA297791-685C-4EDD-BB53-30F381A39ACF}
MIWUK 170153038 | {AA9722DD-9A20-411C-A91B-FCD027C3242A}
MIWUK 1701767890 | {BB39A9FB-82F3-4CEE-812A-8BCB11B79244}
MIWUK 170179118 | {7A676B71-51F1-4DF0-A596-B3D6F63218D3}
MIWUK 170193062 | {B18F77BC-A9DA-4B29-AB14-C0D1FCA97447}
MIWUK 1701953336 | {778380F2-BA49-477B-8F0F-740FAC39A283}
MIWUK 1701992162 | {8E98014F-A627-491D-9EDE-59105F8979E1}
MIWUK 1701CB | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
MIWUK 17021808 | {F7C0AC68-FB70-41DD-B222-3064175EA9BE}
MIWUK 170236888 | {5E0E9C3F-102B-4736-867B-523AEBC69611}
MIWUK 170238218 | {ED3657AD-4222-47A8-B914-D4A507DC3692}
MIWUK 170247143 | {976CA043-61DE-4F22-87BA-0696E25C4DF1}
MIWUK 1702531976 | {29DBEF63-7B51-4C6A-A786-292EB9177451}
MIWUK 1702576504 | {0C4CD1BE-E231-46BA-AA07-10AAA7A9A5DB}
MIWUK 1702667248 | {A068179F-B6CC-4678-A4EC-AF469032942C}
MIWUK 17028130 | {BED4FF87-AC4B-4CCF-ACF6-259B2364BA72}
MIWUK 1702823548 | {DE713724-4753-42EE-87B5-64C0693236F8}
MIWUK 17029270 | {AA0F2742-8D52-435A-9889-3CD8160159B6}
MIWUK 1702CB | {5DE457D9-5E7A-46A3-820A-688DCA33A9BB}
MIWUK 1702S2247 | {ED3657AD-4222-47A8-B914-D4A507DC3692}
MOLINO 1101128824 | {3F3D20C0-ACFF-4762-8BCF-531C75A983F8}
MOLINO 1101152 | {366DDD05-C36C-4018-8E0C-E1718F820EB6}
MOLINO 1101277292 | {73A79C1D-983A-4279-A3FD-02A1B497A62F}
MOLINO 1101322 | {87C4E1DE-229A-456D-853B-731F9308D34F}
MOLINO 1101324 | {AA518DB7-54A4-4551-9B95-ACDCCF557961}
MOLINO 1101338 | {4502A0E5-A181-4FD0-A72F-EAB91B5F9EA1}
MOLINO 11014900 | {5231DB16-86D1-4843-83D5-814DD0192BCB}
MOLINO 11015034 | {5092CF9F-9D4A-405D-A02E-8142B89FC3A4}
MOLINO 11015042 | {D0E3F376-32D7-44BE-A845-A1142386C6AA}
MOLINO 11015042 | {D5D881FC-5E37-43D0-8EE8-25189C47D57C}
MOLINO 1101600112 | {561785C2-9342-42A6-8DBE-3ACD64E05D9A}
MOLINO 1101891 | {3F3D20C0-ACFF-4762-8BCF-531C75A983F8}
MOLINO 1101CB | {F8D0A5CD-F859-4FB9-9BDE-10A27882B6F9}
MOLINO 1102104 | {6BDF733D-8276-4FAC-977E-D46B41E69D11}
MOLINO 1102104 | {7D5BEB0A-06FF-4975-900C-BDCD4AFAA92D}
MOLINO 1102111666 | {2D9442B3-0FEF-4574-B297-2133787A6E1D}
MOLINO 1102178 | {E011217D-F6B4-46C8-AC6E-B5F7ADEBD850}
MOLINO 1102178 | {52846ED2-3EF3-4ACD-B861-D51B3045E38F}
MOLINO 1102318 | {937FE0BF-1949-4B31-99B0-C96DCB7F5DAB}
MOLINO 1102318 | {DB92DEC2-EF43-4597-BEB8-09E6C81EAC35}
MOLINO 1102344 | {A98FD5E2-DDE3-4E25-9F0F-483626AE2A81}
MOLINO 1102381468 | {60856F33-F69F-483D-A29E-5E684F09BD0B}
MOLINO 1102384 | {7FCADEEB-07B1-4335-8044-26A9BB50B5B5}
MOLINO 110241392 | {447B8131-1050-400E-81F0-E893F64CB384}
MOLINO 1102485246 | {19FDD057-3D59-40B5-B132-CF89CB4144D2}
MOLINO 1102495692 | {38F7A409-B733-4A66-AD23-141CCDD939A2}
MOLINO 1102509516 | {1740079B-33AB-4B93-9EE4-D9DB46F4F893}
MOLINO 110251788 | {E88FFA7F-5F70-49D0-8DB1-373E7BB1124C}
MOLINO 1102535 | {3827F6F2-326F-4FCC-9EC1-DB4311EC910A}
MOLINO 1102613993 | {2F38AE04-1F96-44F3-B945-95C6CEDBB2B8}
MOLINO 1102658 | {08F3C995-4373-4EBD-A7D7-6CA08BB9F56E}
MOLINO 1102658 | {F138D9D4-46B7-40FF-98A4-3E0C55CB9A57}
MOLINO 1102658 | {3D43B11F-E0A3-42B9-AA78-A5A3D2CA62D8}
MOLINO 110266006 | {4AE7AB5F-C633-47AF-9F7F-61FE17B35998}
MOLINO 110276066 | {8614D223-F481-4626-858F-622D47A98A6F}
MOLINO 110279306 | {B81A8616-55B2-41F9-9829-B699E6A06290}
MOLINO 1102905231 | {96DF56B4-09D9-4632-A84A-99B69DBE4320}
MOLINO 1102CB | {3827F6F2-326F-4FCC-9EC1-DB4311EC910A}
MOLINO 110313219 | {81938758-C680-45F4-959B-309DC169CCCA}
MOLINO 11034676 | {81938758-C680-45F4-959B-309DC169CCCA}
MOLINO 11034682 | {81938758-C680-45F4-959B-309DC169CCCA}
MOLINO 11034894 | {AC40E023-4A81-4908-BE46-066808454E49}
MOLINO 110381008 | {81938758-C680-45F4-959B-309DC169CCCA}
MOLINO 1103CB | {81938758-C680-45F4-959B-309DC169CCCA}
MOLINO 1104186 | {95E199CC-8537-4A38-8A02-CCF54B07F2E5}
MOLINO 11043281 | {5465105C-2E1E-47CE-8A44-120776A3EE22}
MOLINO 1104368158 | {4E9FB77B-2DAB-4C16-84CB-10ABD5B12CA4}
MOLINO 1104380 | {5465105C-2E1E-47CE-8A44-120776A3EE22}
MOLINO 1104468882 | {8788BBFA-A2B3-4787-825E-E3E47FE6B9D7}
MONROE 210290988 | {0EBA2BBA-1703-4B1A-B59D-EED82556C743}
MONROE 2103408 | {D546C25E-2665-4E0F-83E6-19A6D0D70A7D}
MONROE 2103848530 | {AD6C9BC3-922D-4820-9E11-0EE6E0677452}
MONROE 210392868 | {18B04DCD-9DDD-4C1C-AC8D-731B4880D7B2}
MONROE 2103CB | {D546C25E-2665-4E0F-83E6-19A6D0D70A7D}
MONROE 2107380760 | {744357E4-A039-4634-8800-C090FE5B1DFD}
MONROE 2107428720 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
MONROE 2107434 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
MONROE 210765424 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
MONROE 210781174 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
MONTE RIO 1111140 | {D0D0E128-BFAA-40E9-9195-426CE62EA884}
MONTE RIO 1111240 | {561B7435-E1A2-417A-BAD2-8DB925A728A4}
MONTE RIO 1111256 | {7E7B289D-4C56-4E03-B7F0-62BB352D64F7}
MONTE RIO 1111292 | {E76F208E-D030-4954-AE4B-2E5BE9D9580C}
MONTE RIO 111137520 | {C0868086-2AE3-4A05-90EB-BF1D6E5F34F7}
MONTE RIO 1111506 | {C4F8319D-D897-4280-8AA8-30DB11490475}
MONTE RIO 111159046 | {96597AB7-8D9B-480E-B290-054AD97D3E7A}
MONTE RIO 111164758 | {173229A0-9A6C-4AB5-8BBC-51112D47DF20}
MONTE RIO 1111969182 | {00ACF5D2-3F52-4898-8741-EAC69506A35F}
MONTE RIO 1111969182 | {CFD49D25-5A97-4913-B570-E644DBC2B01E}
MONTE RIO 1111CB | {149DEC4B-D1C4-4F4B-922B-9B5C5A4AE0D1}
MONTE RIO 1112120 | {A3E8D9EB-1B5A-4CFD-AE2F-C1E7C6E04114}
MONTE RIO 1112120 | {70E55192-7CAB-4C64-83AD-55CAA307DD8A}
MONTE RIO 1112212 | {C70CA0FD-CD6F-47B4-AE85-ADF07161D721}
MONTE RIO 1112387984 | {EB3C763F-69B5-439D-A5E0-81FC232FC4F9}
MONTE RIO 11125040 | {2864C93C-BF52-4E0B-A5D1-FA5019DBF7C4}
MONTE RIO 111264682 | {DD8BA615-FFBA-48E9-84EA-5D20532CD959}
MONTE RIO 1112938174 | {D361D503-3790-453C-B66D-A7A3345502F7}
MONTE RIO 1112CB | {78AB2FDD-E1CA-4DC9-8362-0759A43BD212}
MONTE RIO 11131067 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
MONTE RIO 11131313 | {2E6DCA70-6B36-4F65-B853-AA4AC3CF0E30}
MONTE RIO 1113180 | {15C2C6AB-DE9A-4E17-8C2D-97DC9B78100A}
MONTE RIO 11131989 | {EA690835-9E38-4D73-A546-B5676BCE1BEA}
MONTE RIO 1113202 | {06C5DDF3-68CB-4362-94D6-24163B7FDD9B}
MONTE RIO 1113250 | {F3C44BD4-C837-40EB-9584-B17B6404063F}
MONTE RIO 1113320 | {EF630F9A-72E2-42EA-B074-23D3C9859856}
MONTE RIO 1113346 | {EA690835-9E38-4D73-A546-B5676BCE1BEA}
MONTE RIO 11133970 | {53EC2261-1200-4127-A3BA-F52DA74219E3}
MONTE RIO 1113477 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
MONTE RIO 11135020 | {C3FAC8CF-A105-47CA-BAFD-6A205D726950}
MONTE RIO 11135024 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
MONTE RIO 11135026 | {2E6DCA70-6B36-4F65-B853-AA4AC3CF0E30}
MONTE RIO 1113524 | {8C8983C8-884C-4E70-BBB6-36F59CD80D78}
MONTE RIO 1113532 | {3A330D41-F506-49D1-A8AC-21EA6FC6FDFA}
MONTE RIO 1113539938 | {3188B2E2-9541-4BE0-B86F-D0DD55D6F8F8}
MONTE RIO 1113652 | {1A58D4D4-08C9-4897-B970-7F34BB31F59C}
MONTE RIO 1113678 | {3C769364-EC40-4452-9AEF-32B476BC5146}
MONTE RIO 1113678 | {F763F6AF-FC97-4F89-AD25-F9455AF541C2}
MONTE RIO 1113CB | {C3FAC8CF-A105-47CA-BAFD-6A205D726950}
MONTICELLO 1101130412 | {50BA7E67-5EAD-4941-88EC-76A715C41286}
MONTICELLO 11011589 | {9EBC498A-4473-4FB2-A278-0770D844069B}
MONTICELLO 11011780 | {4904A78C-4F30-4D7A-889F-B688535D7066}
MONTICELLO 1101256640 | {50BA7E67-5EAD-4941-88EC-76A715C41286}
MONTICELLO 110137384 | {9EBC498A-4473-4FB2-A278-0770D844069B}
MONTICELLO 11014360 | {5B3909F8-EEF1-46D6-9827-15D3DCA91BD0}
MONTICELLO 110152910 | {151C0216-83E8-4EAF-9D71-0D50917A8A0E}
MONTICELLO 1101630 | {EC7479AE-9F4D-4362-8AF7-E7B5EDC2ECC7}
MONTICELLO 1101654 | {11F49F82-D386-49B9-BCC1-D0FA0566ECA0}
MONTICELLO 110165454 | {9E39C048-EF22-4DAE-9CE9-DEC0330A8321}
MONTICELLO 1101666 | {5E2D609D-433E-4CA6-9935-5DD068ECF7FE}
MONTICELLO 1101718 | {CFFE2061-0111-499A-9D10-C50262E92A10}
MONTICELLO 1101720 | {07BF8128-F528-4070-AA6F-0E3ACF3A793A}
MONTICELLO 1101909026 | {4FC73DDB-01A4-4D9E-A572-5B8425E298AC}
MONTICELLO 110193384 | {D1302290-4599-4ADB-94B8-46B42AAD5681}
MONTICELLO 1101CB | {CCC05F57-600B-48FA-93EA-7CC307C90265}
MORAGA 1101108540 | {372C45CD-D068-4E6E-9903-0ED38EA6950C}
MORAGA 1101121620 | {27593588-F872-4832-9B66-0B2A2D32D4A3}
MORAGA 11013442 | {5E439C6C-9351-476C-9634-FD9D0D59EEC5}
MORAGA 1101532246 | {5BBA7E94-488D-470E-9522-5BF71768AFC8}
MORAGA 1101669542 | {4AEACE31-C42A-4851-9933-308B9CD449BD}
MORAGA 1101669542 | {B9A70335-64B1-4C3F-8843-DB3BDADB4C77}
MORAGA 1101772406 | {B68800AA-8665-4562-B46C-56262DD45B63}
MORAGA 1101822414 | {B2892C66-0456-410A-AA55-6BB01132F335}
MORAGA 110183424 | {E1CFB432-A326-40CC-8BB1-1B7A06DF46E8}
MORAGA 1101CB | {6B23A69C-24B9-4566-AFFA-1FAEC2B2E50D}
MORAGA 1102161484 | {BF062587-F543-4494-9BCB-AB97B3FA4161}
MORAGA 1102221914 | {1B687BB2-4458-48CF-B4BC-EAC2F2DF6A24}
MORAGA 1102CB | {882C20B1-4F53-4E74-914C-118DECC8B0F8}
MORAGA 110381146 | {F07F88D2-F88A-4EFC-8A75-AE6FED02438E}
MORAGA 110381146 | {14C57C49-3FAA-493A-A967-CDA87ADFA83B}
MORAGA 1103838598 | {693F18CA-6E41-44D8-B1A1-17EC2030AA07}
MORAGA 1103880425 | {4E1314C0-96F2-46DA-A3A3-635E5ABAFDCD}
MORAGA 1103CB | {D9DC241F-0994-464E-87CB-1A64D6E40D7E}
MORAGA 1103CB | {A7850717-18DF-4BF5-B934-11A86FF92EB5}
MORAGA 1103E510R | {4C3B8436-25B4-4A62-8D40-AF9B1B8FB54A}
MORAGA 1104750618 | {D6B675EC-0BB2-4404-B1DC-E66B91C5F9F8}
MORAGA 1104CB | {65BF29A6-90D7-4E9D-9D0F-0B463AE68E56}
MORAGA 1104N532R | {8FCB98A6-A5C4-47A0-A545-FF069C01B16A}
MORAGA 1105116034 | {52D8B49E-A907-44B9-9C80-969531571B5F}
MORAGA 110531512 | {412508C2-76EC-400C-8C7E-53EB1141C78F}
MORAGA 1105553110 | {ED0CCE67-C6E8-4C9F-AA31-59CE0E37A31D}
MORAGA 1105829530 | {7BAB3DC6-3A7A-45FE-9661-6992831DBB83}
MORAGA 1105CB | {40049C8F-DAE2-4759-A9B6-0D8AA42C6AC2}
MORAGA 1105E512R | {D2286737-B438-4EE0-BE89-B719D260A085}
MORGAN HILL 2104152774 | {425217ED-9250-4ACE-9F11-E30531EC148C}
MORGAN HILL 2104CB | {107D0CE4-0125-4C25-9DF3-3408566B030B}
MORGAN HILL 2104XR018 | {98ADBEF9-BACB-4586-BAAB-FCF78599AE57}
MORGAN HILL 2105345099 | {80793A2F-4CDD-4126-A553-60CE126AE8B0}
MORGAN HILL 210542348 | {2DBAAA9C-8985-4692-9A1B-CC370D239D9B}
MORGAN HILL 210542348 | {8A3AD693-3871-44A7-A81A-4DD472A3967C}
MORGAN HILL 2105CB | {CB70A94C-2E5D-4322-8C8C-C227D17BDEDF}
MORGAN HILL 2105CB | {30C139BA-309C-45BA-85AD-14DDE6598AF6}
MORGAN HILL 2105XR070 | {D4E598FB-500D-4E86-913F-DD1E461E4E23}
MORGAN HILL 2105XR152 | {91E130A2-6B12-4607-8077-CCA3F4CE535A}
MORGAN HILL 2105XR176 | {33647C9D-A594-482D-97B0-F9F1AC5928F8}
MORGAN HILL 2105XR268 | {4F22013A-C8F8-4C93-9CF0-829946636F4D}
MORGAN HILL 2105XR312 | {03C8F227-2007-4B73-A689-5FDF30542245}
MORGAN HILL 2105XR494 | {128A7030-B8D8-40F8-90A4-700AFA9E547C}
MORGAN HILL 2105XR564 | {002F00BF-AB7A-4582-A318-84DD2A6C3219}
MORGAN HILL 2105XR578 | {534A451C-57DA-44B8-B8BC-2F5C24A553D0}
MORGAN HILL 2105XR602 | {DF06274D-82A7-4C1B-8F47-D036189DB7AF}
MORGAN HILL 210653992 | {92AC711D-1F72-4B85-B43C-96526CED20CC}
MORGAN HILL 2106CB | {2C56B704-0B48-474B-86AD-67CE86231708}
MORGAN HILL 2106XR002 | {2D5D4B5A-C41C-47E0-8A3E-3313CAAFF1F2}
MORGAN HILL 2106XR224 | {2C56B704-0B48-474B-86AD-67CE86231708}
MORGAN HILL 2106XR324 | {2C56B704-0B48-474B-86AD-67CE86231708}
MORGAN HILL 2108CB | {4DF45F56-E0C5-4EB4-A8CE-218D259985D0}
MORGAN HILL 2108XR328 | {D422348E-558F-4EA6-B8E7-CD115687A21D}
MORGAN HILL 2109145998 | {DE740AD5-7224-4449-BB36-490304754B67}
MORGAN HILL 21094145 | {DECA5724-8C2D-4F8F-80A8-75B013DC4D0B}
MORGAN HILL 2109CB | {40746EE4-53DF-4A3F-B597-DD5CDFE06F6F}
MORGAN HILL 2109XR104 | {DECA5724-8C2D-4F8F-80A8-75B013DC4D0B}
MORGAN HILL 2109XR246 | {601835A0-060D-478B-8A86-7129055F5CF4}
MORGAN HILL 21103093 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
MORGAN HILL 2110654924 | {674F8E15-1E29-4545-B316-3ABCD054D65C}
MORGAN HILL 2110716210 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
MORGAN HILL 2110CB | {E4018ACB-C125-496A-B5B0-B421A786B3CA}
MORGAN HILL 2110XR164 | {11D639D0-BAAC-4BDC-B7F6-D7D6C9CC18B0}
MORGAN HILL 2110XR326 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
MORGAN HILL 2111123422 | {AC835E08-6C41-417C-9DCE-0F2F64530550}
MORGAN HILL 2111419718 | {40B38A4F-7054-4A4B-BF09-F440B1202801}
MORGAN HILL 2111919856 | {9425E865-2193-4800-9F65-36F91B76A0A9}
MORGAN HILL 2111997000 | {60A77C46-059F-42FD-9344-179C8ED541A4}
MORGAN HILL 2111CB | {C53CEE9F-7D61-4CE9-9445-195D1FBA8C9E}
MORGAN HILL 2111CB | {8D6AF672-1092-41FD-91A5-035B7D768884}
MORGAN HILL 2111CB | {38524ABF-273D-46D3-B737-CC26E3F4D5B4}
MORGAN HILL 2111XR292 | {7A50E1CD-B005-4744-BD76-86E8006C9FCE}
MORGAN HILL 2111XR354 | {8D6AF672-1092-41FD-91A5-035B7D768884}
MORGAN HILL 2111XR398 | {C3FC7DAB-5E2B-4C00-BE86-ED9552703F1E}
MORGAN HILL 2111XR398 | {42CC2054-54F9-458D-A9CD-C912CAA60A36}
MORRO BAY 110187487 | {DC1CD14A-C73E-417C-A65E-B1AE2FBC8341}
MORRO BAY 1101V64 | {02238211-B668-4889-9A10-D952B009B264}
MORRO BAY 1101V66 | {DC1CD14A-C73E-417C-A65E-B1AE2FBC8341}
MORRO BAY 1101W04 | {102F8E07-1864-431F-B2B2-B6070F04A552}
MORRO BAY 1101W20 | {F3373B43-A9DC-45C9-B2E8-745D10B70AD6}
MORRO BAY 110247584 | {BC93D19D-B18C-449B-8A15-8B2CED2656F7}
MORRO BAY 1102CB | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
MORRO BAY 1102V80 | {C6CF638E-9C90-41DD-9ABD-A01972E6D396}
MORRO BAY 1102V84 | {C6CF638E-9C90-41DD-9ABD-A01972E6D396}
MORRO BAY 1102V86 | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
MORRO BAY 1102W22 | {52C280BB-FF66-4850-B734-B05EEFB600B7}
MORRO BAY 1102W24 | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
MOUNTAIN QUARRIES 21011102 | {4F7ECBF9-F29B-4CC1-9A4D-006B1538826F}
MOUNTAIN QUARRIES 21011130 | {F71097AE-E6F3-430F-8B2D-241E8D88F4AE}
MOUNTAIN QUARRIES 2101117452 | {F6FC9A10-626B-4FC0-AEAB-599AAB0F4A9C}
MOUNTAIN QUARRIES 21011180 | {32A5B84F-F8E0-4F0E-B3CD-BEC3B55A0617}
MOUNTAIN QUARRIES 21011184 | {955B96CF-04BC-4DDA-A99C-F3551BD93482}
MOUNTAIN QUARRIES 21011346 | {B959CC4A-E894-449B-BBA9-D2734BD80359}
MOUNTAIN QUARRIES 21011350 | {6752B4B6-FF0C-4C57-ADC9-D57090816B6D}
MOUNTAIN QUARRIES 21012422 | {D7F1D14A-5B2A-48EF-B12A-9197AE3BCA5E}
MOUNTAIN QUARRIES 21012504 | {3A3CE7E6-6AA4-47AB-A29B-08143EBEB1C1}
MOUNTAIN QUARRIES 210135466 | {F283C4DF-68EA-4D46-BF4A-0E3EBCA0E4FA}
MOUNTAIN QUARRIES 2101486682 | {C012B9A5-7963-4E6A-B877-46101FFAFAB7}
MOUNTAIN QUARRIES 210151584 | {0BE1E4C9-DDDF-49C0-980B-2AA7763D326F}
MOUNTAIN QUARRIES 21016953 | {6752B4B6-FF0C-4C57-ADC9-D57090816B6D}
MOUNTAIN QUARRIES 210192474 | {B1828264-E942-4507-AD5A-E7D1D60A066A}
MOUNTAIN QUARRIES 2101979598 | {BD8F3E9A-E4BA-4240-B5BB-1CCE7EBD3EAE}
MOUNTAIN QUARRIES 2101CB | {D8BA8AE4-C717-4377-92D2-0F59CC0A31DF}
MT EDEN 1112MR365 | {A5398856-385B-4671-B566-17D8F81D2C22}
NAPA 11025039 | {CBD8A59E-6463-47E4-AF46-087923E514DE}
NAPA 1102561208 | {12961FC8-2125-43B0-A892-045A87E2B620}
NAPA 1102942 | {CBD8A59E-6463-47E4-AF46-087923E514DE}
NAPA 110549856 | {A567CC7C-BB96-40C6-B54C-7AC9DFF3A542}
NAPA 11121302 | {605680BF-CE15-4E43-86C0-2D915CDAFCDB}
NAPA 1112315244 | {91380486-2659-460E-8E8C-74182A1F6A64}
NAPA 1112850068 | {B5EEBD8D-5229-462C-9EA8-5264059F4EB6}
NAPA 111289474 | {D8230112-C16E-4959-B193-6B3851D10773}
NAPA 1112919436 | {0CCAD7CD-FF20-472B-B1AB-23DFD98C4B6F}
NAPA 1112943158 | {C39D5E34-C18E-41D1-A210-D8B55CE52048}
NAPA 1112CB | {C2E68366-657D-4902-BBD7-D59A6C76C29A}
NARROWS 21011202 | {63551680-2169-45C3-BF85-1608C868FCAF}
NARROWS 2101CB | {7B0321EB-AC29-4857-8514-66B11EFDEF70}
NARROWS 21022220 | {15BB893C-861D-4514-BB53-2456F70C5D54}
NARROWS 21022718 | {81AACB66-94AE-4D98-92C9-EDFFCF82F0F9}
NARROWS 21022728 | {1F33AC4D-BB0A-424C-BF6E-423FE06FB054}
NARROWS 210242584 | {BB1737E9-F6A8-464E-B585-0852853AAD83}
NARROWS 210248484 | {F3B439DF-7706-4C2F-8999-BCA70EF18266}
NARROWS 210276952 | {070E580D-ED42-47CA-BF5A-6C96D8E39FC5}
NARROWS 2102CB | {30B38EC8-F2E7-47AF-8BC7-D7EB75673131}
NARROWS 2104CB | {F4FF7575-EB60-4F06-920B-F33332AB37E0}
NARROWS 21052216 | {94CC379D-BE20-48E1-8496-01F284C7FE9E}
NARROWS 21052228 | {460117C5-52D5-4539-942E-65301ACAACE9}
NARROWS 21052426 | {8D49CCC1-AF4C-4146-915D-64772DC7F3D1}
NARROWS 21052748 | {EEAC938D-675B-4361-87B7-7942FA5DF8E7}
NARROWS 210551582 | {D508D44B-0B7F-43CB-B9DA-F37161CA8F62}
NARROWS 21057203 | {8D49CCC1-AF4C-4146-915D-64772DC7F3D1}
NARROWS 2105CB | {2611646A-C593-4185-9486-0AA063D164D0}
NARROWS PH 1151CB | {3969D241-789E-4335-9A13-4750E3876C2B}
NEWBURG 11313446 | {8A80C7E5-86DA-415B-A0BF-702ACAC61E9A}
NEWBURG 113137512 | {BE4D7FC4-1B1E-43C1-A168-77B9EA7D5DB3}
NEWBURG 113190242 | {3A3BBF86-310F-432E-A06D-A8536237FB4D}
NEWBURG 113190644 | {51231194-526E-42DD-B60A-6D3E3BD144D9}
NEWBURG 1131CB | {C04ABA60-50E1-4D28-B0FC-7F9C72775B5F}
NEWBURG 11322074 | {144E92CD-CA71-4B28-86FC-662A80108717}
NEWBURG 11322074 | {61AD59B6-3DE5-4155-9391-74B53A84E200}
NEWBURG 113237494 | {8092EAEA-5E3D-45F7-849A-BB9EC224C0C6}
NEWBURG 113237494 | {61AD59B6-3DE5-4155-9391-74B53A84E200}
NEWBURG 11326576 | {2C9C3EB7-00FC-4934-A962-9B300983DC9F}
NEWBURG 1132665674 | {F0A8EA1C-5D25-4DA2-A0EA-6346825293B2}
NEWBURG 11326982 | {61AD59B6-3DE5-4155-9391-74B53A84E200}
NEWBURG 113277894 | {80EB220B-EDCA-49B1-8388-856A3CF42050}
NEWBURG 1132CB | {2C9C3EB7-00FC-4934-A962-9B300983DC9F}
NEWBURG 113397612 | {1B3C973B-E8C8-4CCB-9A5F-D4D21840CBA9}
NEWBURG 1133CB | {DD9AEFE6-8781-45D2-A01C-A8D7D2CCC603}
NEWMAN 110542128 | {AD5BB80F-100E-443D-B968-9FD3EF2DDDC6}
NEWMAN 110590430 | {AD5BB80F-100E-443D-B968-9FD3EF2DDDC6}
NORTH BRANCH 110111158 | {441CFEC9-1CA0-48DF-94A7-C868FF359EA8}
NORTH BRANCH 1101207256 | {744E490C-4B9D-43E3-89F3-EC14E8D89F45}
NORTH BRANCH 1101236904 | {AA91F175-103A-4979-B706-C1296ED60D2F}
NORTH BRANCH 1101750010 | {7465C87A-2B17-44E2-A07D-3F978BE2E64E}
NORTH BRANCH 1101752104 | {13E5BBB0-001E-4A48-B4D2-914C2E42F6A2}
NORTH BRANCH 1101769000 | {5BEB7DB3-3BFD-435F-AD8B-9A82CD60EDEF}
NORTH BRANCH 1101CB | {BE4CA008-D653-4EED-9B85-D4D7237516F5}
NORTH BRANCH 1101TS1115 | {441CFEC9-1CA0-48DF-94A7-C868FF359EA8}
NORTH DUBLIN 2101CB | {298F8E6C-8C4E-4458-91EA-603E3295125F}
NORTH DUBLIN 2101MR333 | {298F8E6C-8C4E-4458-91EA-603E3295125F}
NORTH DUBLIN 2101MR765 | {436DC1C4-F56A-4204-87B1-78F6DDDDA501}
NORTH DUBLIN 2103248212 | {1315E3CE-6D47-41FF-A139-336A7A702069}
NORTH DUBLIN 2103248212 | {51ED7259-EE7B-43FE-8146-EC616D86F161}
NORTH DUBLIN 2103248212 | {A9FADF54-D8A8-414A-9A42-DC0268771F29}
NORTH DUBLIN 2103727584 | {7713D0FD-BB09-40ED-B7D7-E260577647D4}
NORTH DUBLIN 2103CB | {7713D0FD-BB09-40ED-B7D7-E260577647D4}
NORTH TOWER 2101CB | {17DE99B2-61AF-4462-979F-1C1B612D667F}
NOTRE DAME 11022038 | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
NOTRE DAME 11022420 | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
NOTRE DAME 110287268 | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
NOTRE DAME 1102CB | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
NOTRE DAME 1103317782 | {E54B3868-C992-4672-B01F-A1BD60263D71}
NOTRE DAME 1103407486 | {611B5D12-B194-497D-815D-46B8449CCF48}
NOTRE DAME 1103CB | {E3ECAAF0-99B5-4E63-AE53-35BCAA42BD12}
NOTRE DAME 11042028 | {68FC6E44-EFD8-4B52-B283-8EF4B688F460}
NOTRE DAME 11042028 | {392D3426-D861-489B-B7E0-006CE5D68867}
NOTRE DAME 11042408 | {BE4941E8-75D1-4DE2-AD8F-78922C143536}
NOTRE DAME 1104937710 | {3CF079B2-DF24-4674-AF57-026F1C1899BA}
NOTRE DAME 1104CB | {4C7176B3-82BB-4EC7-9074-E6E03166E224}
NOVATO 1101180632 | {E700FD05-F82B-4C09-AFA4-140066127996}
NOVATO 1101180632 | {8092C842-CB66-429C-A93C-3CE6A8BDBBDF}
NOVATO 110387834 | {F95FECA9-BE51-4923-A755-70AE69DDB475}
NOVATO 11041282 | {3B8D2573-46CC-4384-8812-825E9555364D}
NOVATO 1104422246 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
NOVATO 110449280 | {DFA09063-555C-4B48-ABDD-D054FE284D1C}
NOVATO 110455398 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
NOVATO 110456282 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
NOVATO 1104676060 | {64CF78D9-1536-455F-B223-A7030F2F7FB3}
NOVATO 1104889406 | {B0ADA7D3-946E-4D87-A626-5D6D71C05975}
NOVATO 1104904966 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
NOVATO 1104CB | {1842CB75-05D4-4BC6-974F-EF96026B2FE8}
OAK 0401772122 | {FED570EA-6E71-451D-82BC-E09C185F668A}
OAK 0401R7252 | {0F16EE83-C04F-42F2-82FB-83FAA303C2EB}
OAKHURST 110110090 | {8E59087F-9FB7-4FCF-A3C3-5164FC72FB46}
OAKHURST 1101352740 | {F41A5EF2-D553-405E-908D-16E9BE751BB3}
OAKHURST 11015490 | {19617CFD-32A5-4AA4-9E54-43F64E95D667}
OAKHURST 1101618380 | {3BD097D6-9F24-4589-8A9B-760186FAF7A5}
OAKHURST 1101636114 | {C6D08398-1977-4CDB-B9B0-E15E9BAE5667}
OAKHURST 1101910120 | {544CCA12-ED7E-4449-A067-A7C3370A6363}
OAKHURST 1101CB | {2CDF7848-B063-4FC4-9C52-AE29AA49D3FF}
OAKHURST 1102333062 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
OAKHURST 1102538042 | {CD5EC07C-7621-403E-BE45-2B4B105F5053}
OAKHURST 1102963056 | {62CEF957-71A2-4F8F-B3B6-2E1C79BBD67A}
OAKHURST 1102CB | {D0015396-1CC9-4783-A5A2-48EC4AF3208B}
OAKHURST 110310140 | {9D3389CA-CFE2-49B7-8B13-3D1B7ACB399D}
OAKHURST 110310190 | {15EFA531-A43D-4849-828D-DC9485A13753}
OAKHURST 110310570 | {3D247DD8-C725-4A26-BE65-60FA26890CB2}
OAKHURST 110311900 | {0DA18697-929C-4AB7-9F79-F379F7D7D5E9}
OAKHURST 1103464622 | {E28BFF8D-F8E2-40AB-836D-4CDEF3E6FE3D}
OAKHURST 11035120 | {36CCC1E6-2517-4B50-80DA-A74340CF2F3A}
OAKHURST 11035480 | {194E4857-C055-4CC4-9616-06A060725A90}
OAKHURST 110363334 | {778182E4-2AE7-465E-B2C9-C1ED6A0D9207}
OAKHURST 1103719490 | {0997B2C6-B46C-4942-8B54-4BA0035375E3}
OAKHURST 110377384 | {B3D10DC1-455E-4DDF-8795-B604423C3B61}
OAKHURST 1103CB | {0FC43676-7F71-4151-8B57-A856F18A7815}
OAKLAND D 0407CB | {D6B258F1-A023-49ED-A291-5DC1514DFA3F}
OAKLAND D 1112775616 | {E3949547-B886-4AC0-B818-1825176C1A10}
OAKLAND D 1112775616 | {F53A9D7A-8AE8-4A2D-A636-4553F02D4DA3}
OAKLAND D 1112775616 | {79081478-9874-4F61-AC27-C396B53B5EAB}
OAKLAND D 1112CR192 | {D247477D-6B8D-41FB-AD66-DBEF58C5249C}
OAKLAND J 1102126740 | {977D131F-B0F9-4D49-AC55-AA0EFBCDE0F0}
OAKLAND J 1102159816 | {859F64C2-C27C-450D-B243-6E6F38B09662}
OAKLAND J 1102208294 | {3968E6D1-D5B2-4B61-BDB8-C346AFC38AF0}
OAKLAND J 1102951816 | {F44E0750-FE39-44A0-8598-B8A75709D6C1}
OAKLAND J 1102CR102 | {0FCC4668-DE07-42BB-BC4D-4288336A5D5A}
OAKLAND J 1102CR250 | {FD5FE64E-C40E-49F6-A1B2-6062B4E7CFF6}
OAKLAND J 1102CR252 | {FD5FE64E-C40E-49F6-A1B2-6062B4E7CFF6}
OAKLAND J 1105153228 | {FD68B15D-2380-4995-ADA8-EF407A4F9E9B}
OAKLAND J 1105CR132 | {99760D35-3D8A-43D4-9A8C-B787B6697406}
OAKLAND J 1105CR150 | {B40886D4-E154-4D0B-BB2B-061EFDC2739B}
OAKLAND J 1105CR256 | {FA7AC1D5-82AB-4E51-B874-C59D71756955}
OAKLAND J 11067867 | {4808F0D1-7684-45A4-AA78-2B2D6EF06890}
OAKLAND J 1106CR164 | {4808F0D1-7684-45A4-AA78-2B2D6EF06890}
OAKLAND J 1116CR328 | {38D3BFB4-B810-445A-BCA4-713A479E6C8D}
OAKLAND J 11181846 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
OAKLAND J 1118CR198 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
OAKLAND J 1118CR332 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
OAKLAND K 1101462782 | {D4279E0E-8AFC-48EB-B37D-23D4BBC72C16}
OAKLAND K 1101CB | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
OAKLAND K 1101CR170 | {8CEAFBDA-9CAF-47DF-A93A-B3DE193C02EB}
OAKLAND K 1101CR172 | {2F486204-BB5C-45FC-9D31-305D5B069E7B}
OAKLAND K 1101CR174 | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
OAKLAND K 1101CR178 | {3AC71A95-3DF9-478B-ACCE-8AC300269CEA}
OAKLAND K 1102172340 | {D34997DF-D716-4F24-A200-9AE2C7E61290}
OAKLAND K 110217430 | {02500171-BA04-46CD-BDC9-060AD340AEF8}
OAKLAND K 1102378866 | {09828EEB-C0CE-4488-A95A-E404C7913B2A}
OAKLAND K 1102CB | {D1E9CD4E-4BC6-42D5-802C-68BF9527A1E0}
OAKLAND K 1102CR014 | {AAFDB0FF-2AD9-4FDD-A8E9-43792701F2AF}
OAKLAND K 1102CR014 | {B5EF99C1-ABA3-48FB-9EE2-B54D16D47CE4}
OAKLAND K 1103CB | {9BD2CCED-08C0-4120-A490-E52866AF5C8D}
OAKLAND K 1103CR188 | {C758376E-2F53-4EBD-9E43-CD37C030EEDD}
OAKLAND K 1103CR202 | {9BD2CCED-08C0-4120-A490-E52866AF5C8D}
OAKLAND K 1103CR422 | {834BDB9E-9A30-4D9F-8424-760E012D4EC8}
OAKLAND K 1104432850 | {14CA8224-5AC7-4834-81C3-26558D7F85B9}
OAKLAND K 1104CB | {3C8EEA5A-CE4E-4740-9897-693B2E67E957}
OAKLAND K 1104CR204 | {A0999EEF-D902-4C4C-8260-3134A0D51FA5}
OAKLAND K 1104CR206 | {FDBE20C4-A243-4218-824C-85EFE8D9D967}
OAKLAND K 1104CR208 | {61E67233-CD4F-4206-8138-63FBDA895D1D}
OAKLAND K 1104CR210 | {5D6DF9FD-08CF-4E49-97A3-2B3AF27CC711}
OAKLAND K 1104CR326 | {993BD642-B43F-4A07-B618-DAD20FD40FEE}
OAKLAND X 1101688681 | {E90D0A12-25D6-498C-BFBF-9356BC38B8E9}
OAKLAND X 1101688681 | {4D72F15F-C15D-414E-839E-18266D63B84A}
OAKLAND X 1104391688 | {CE464302-D75F-4110-A0B1-1E7596A4CF84}
OAKLAND X 1104438648 | {51A41992-B3B3-41BA-BF69-679DAA3E243C}
OAKLAND X 1104CB | {14DC5424-B005-4065-8948-2B6A676B0C25}
OAKLAND X 1104CR022 | {2A115028-6F68-4B14-BB47-6F364E8C5941}
OAKLAND X 1104CR101 | {0E163071-14D9-42E7-B9B8-B27ACF143A75}
OAKLAND X 1104CR214 | {A4D00FB7-3066-4764-B528-AB78985E682B}
OAKLAND X 1104CR288 | {E0AFB0D0-4FAA-4A38-B181-558E89FECB34}
OAKLAND X 1105184672 | {274ECA5A-0B48-43A3-88F5-9E1AB810108B}
OAKLAND X 1105528554 | {D8A3F73E-152F-405F-9A1C-7432AB4CBB0C}
OAKLAND X 1105CB | {44B8C422-CD6C-4697-80AE-EEAF985A6D84}
OAKLAND X 1105CR242 | {4B545AE9-A885-48BD-BBDD-C323FFCD6AA5}
OAKLAND X 1106121588 | {93028691-B011-4DD4-9BFD-411C56E1FD61}
OAKLAND X 1106735592 | {7014D81C-BAD9-4B89-B142-06674CDB91D9}
OAKLAND X 1106950688 | {AF2EF2E2-3FD9-4033-9703-73840E59FAC3}
OAKLAND X 1106CB | {FEA3C3F3-959E-472A-9376-926585E20D05}
OAKLAND X 1106CR008 | {A1C4F4D6-01EE-430E-BE68-0AE547BD756D}
OAKLAND X 1106CR020 | {6992E765-02F8-45C7-B571-2F9E479DE26D}
OAKLAND X 1106CR266 | {9B2F70E2-3822-4ABC-9A9F-F92985EE671F}
OAKLAND X 1107CR428 | {44E2AC7C-1F72-42EE-8609-62087EC4A35D}
OCEANO 1102749231 | {8546FDA1-23F8-40F3-9B1E-5EFFE01FDD01}
OCEANO 1102847440 | {45F26A7D-9F54-449D-A121-9094CE2E38B8}
OCEANO 1102862544 | {C1E44C7D-7EA2-436F-89F7-DC91E773D74E}
OCEANO 1102CB | {53EA2B69-06B5-416F-96AE-9EC7627A84C5}
OCEANO 1102M60 | {DCC941F4-38E3-4AD8-A417-5C522DBC4598}
OCEANO 1102V56 | {6A98D8AD-262A-4E43-B52C-E7FA164E1E31}
OCEANO 110376678 | {2258BA59-F952-4D7E-A5B4-7204CE2B68CB}
OCEANO 1103839302 | {7E0AB3E6-06DD-4E76-83F1-F36EBF375722}
OCEANO 1103V22 | {77F4F191-CCC6-4075-AD1D-AD57A94CE7F5}
OCEANO 1104104102 | {6F967F18-8991-4C9D-8139-526CA500F4D2}
OCEANO 1104891294 | {D8E625A6-002E-4883-8F5B-8B2346405940}
OCEANO 1104CB | {EF084BAC-E8B6-45D7-885C-1A50430DEB23}
OCEANO 1104Q04 | {EF084BAC-E8B6-45D7-885C-1A50430DEB23}
OCEANO 1104Q08 | {D6547032-0BCE-40E6-B529-0CCA8B7E9C38}
OCEANO 1104Q10 | {FB18C056-8E7F-47BF-BAE4-63685AFB3AD7}
OCEANO 1104Q12 | {1F61853A-FECA-4E03-86FF-C3BDC269D699}
OCEANO 1104V36 | {612579F3-BEE6-43F6-ABF9-9C9C3F31A5CF}
OCEANO 1104V38 | {F2D88342-EA4A-4DE6-A5A2-0FD601C586EE}
OCEANO 1106442156 | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
OCEANO 1106CB | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
OCEANO 1106V26 | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
OCEANO 1106V28 | {5A21115A-46BA-4632-AD7D-E9A81D89A695}
OCEANO 1106V32 | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
OILFIELDS 110241992 | {30F0CC79-17F2-4C3C-8FCB-5EFF56537510}
OILFIELDS 110293788 | {207F72FF-9E9B-497E-A35C-453C13449996}
OILFIELDS 1102CB | {59A6DBF3-2585-475E-ABD4-6C09185E8D33}
OILFIELDS 1103233424 | {D1CD6BAF-3C2D-48BC-989C-18A0A5CF3122}
OILFIELDS 11032757 | {63E72A21-A36A-4936-B748-71270400CC57}
OILFIELDS 1103451760 | {4983E6BE-3B0D-43DF-9F14-94B620236C4F}
OILFIELDS 11037006 | {28C87B96-17F1-4B77-AC44-88E083C74B6C}
OILFIELDS 11037064 | {8A139B57-6162-459B-9D12-F430854EC2EB}
OILFIELDS 110383158 | {B2FF44F5-E554-4874-9716-21C58C3BA291}
OILFIELDS 110387034 | {FB7AE1AC-8576-424E-830B-24A6DA8C1F01}
OILFIELDS 1103CB | {BEB06E83-3CCD-4D08-B66B-707C171E4243}
OILFIELDS 1103N04 | {011DA57D-3361-4E85-BC2A-97718564E64F}
OILFIELDS 1103N40 | {5FF9C387-FCBA-4CB4-A5E3-8021D551E54B}
OILFIELDS 1103N42 | {CDC6585C-22C0-4542-A949-CDEE5502EA22}
OILFIELDS 1103N44 | {47FD814D-36E3-4524-B471-B70B44EFD5A6}
OILFIELDS 1103N48 | {63E72A21-A36A-4936-B748-71270400CC57}
OLEMA 11011200 | {A8B14B0D-3BCA-44F1-B75C-F9F858D43D86}
OLEMA 11011252 | {46D411EC-386C-4DB1-B30F-D2D2AC060A49}
OLEMA 11011318 | {48696EF7-D14F-4A4B-98EA-50D58AFE2188}
OLEMA 11011686 | {701C0938-AA90-48C8-9BEF-CBE33E0DD08B}
OLEMA 1101320 | {53821A46-8FEE-4585-B4C8-79B31D43CD6A}
OLEMA 1101334 | {A82D843B-628F-4D51-ABE5-7DA46EAA8FF0}
OLEMA 1101337220 | {92ED973C-FC6F-4281-87E0-2EC9DA3D68C7}
OLEMA 110137074 | {117C09FD-AE60-4D22-843F-8781BD8BA585}
OLEMA 1101416 | {ED6FC814-3841-4AC9-A379-44E5BC33C241}
OLEMA 110149756 | {818B580F-3855-41D8-9229-869A2B79816E}
OLEMA 110150396 | {F7C05161-6A07-4797-A2B5-C7A055E43654}
OLEMA 1101512 | {818B580F-3855-41D8-9229-869A2B79816E}
OLEMA 1101602 | {B7FC1F3D-8C95-48C1-8180-E56EBBA37A96}
OLEMA 110175686 | {702CCB2B-B1B0-4591-B980-760D81375AFB}
OLEMA 1101758594 | {EB266F6D-17EC-430D-AF10-380B2A2664C8}
OLEMA 1101CB | {BE6F7E5F-020B-49FB-90DC-2F40A691D506}
OLETA 11011208 | {5372D86A-A2C3-481F-93D2-142C67A2BDD1}
OLETA 11011217 | {266221BA-D2B4-4469-81F2-F0DF035CF024}
OLETA 110113478 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
OLETA 1101239062 | {266221BA-D2B4-4469-81F2-F0DF035CF024}
OLETA 1101296804 | {85FEEB3E-959D-465E-A93D-BA3999C78268}
OLETA 1101440008 | {48819BBF-C51C-4808-9256-D6B2FDBB4492}
OLETA 110151740 | {FCFE42BE-9C18-409B-9916-4C477F3B3051}
OLETA 110163500 | {869A17D4-9B8C-44A5-B65E-B210B8E19AC7}
OLETA 110163500 | {1E9F707C-392D-4DC5-A731-022ADCFFB715}
OLETA 110163500 | {0DE3898A-1208-4EC8-ABE1-FA05111C0DC6}
OLETA 1101754718 | {F9BCD513-5384-4FF0-AB87-CE22E82C21EE}
OLETA 1101928252 | {5B6438FA-7C7E-4451-8180-245B9388E3EE}
OLETA 1101994386 | {7A7D8413-3009-4325-865C-5FBA4CE9F269}
OLETA 1101CB | {3D156343-1F71-46EE-A300-26BD3EB64071}
OLETA 11021204 | {946E6116-FB8B-4590-A386-CB8F9AFD8BF3}
OLETA 11021228 | {944D67B9-350E-45E5-9370-1645B5E16FDD}
OLETA 1102186326 | {A68CE267-B165-491B-AEAA-6DAE490DB1B3}
OLETA 11022642 | {2ADCBD92-66F4-407E-9ADA-EA48C32C4604}
OLETA 110241396 | {6992FFBA-72E0-4D3C-898B-1A95BB5A0A16}
OLETA 1102793776 | {9DAE8EAF-539B-42A9-B23A-753111FFCF66}
OLETA 1102799924 | {B8897444-5751-4E50-98B6-2ADB95C6C270}
OLETA 1102CB | {23616425-EB34-423E-9DF9-30BB0AE7795F}
OREGON TRAIL 11021382 | {5E999E0A-FF01-4E2B-B970-E4BD7149EAE7}
OREGON TRAIL 11021584 | {9B681776-A90F-48BB-B082-3611E27763E1}
OREGON TRAIL 110249144 | {C5CBE785-E536-4CC4-8B58-7E4F16DB8A71}
OREGON TRAIL 1102CB | {D8B4A6F8-9874-47E2-910D-F4C8426E6854}
OREGON TRAIL 11031448 | {0C0482CD-DD8D-411C-9735-C68EC442433B}
OREGON TRAIL 11031500 | {31065709-9564-4E9B-B7A7-65368041A59F}
OREGON TRAIL 110335002 | {E6157D99-E31C-4483-8F6B-FEB133AE35BB}
OREGON TRAIL 110346860 | {4F1FF48F-FF8A-488F-A383-0E93A88F3890}
OREGON TRAIL 1103CB | {57A4B509-FD84-475C-B34A-463055A0DAF6}
OREGON TRAIL 1103CUS391 | {E6157D99-E31C-4483-8F6B-FEB133AE35BB}
OREGON TRAIL 1104128100 | {ADD91A04-63E3-48F4-ABF3-81ABE34C691A}
OREGON TRAIL 11041574 | {6C99A7DB-F466-44F8-AE24-87D735D842AA}
OREGON TRAIL 11041634 | {6281842D-96D3-4641-90CC-4C58A4D89E7E}
OREGON TRAIL 11043310 | {DC4CEBC1-24E2-4325-802B-4D3154343BA7}
OREGON TRAIL 1104CB | {8048141D-B1E9-414C-85DA-8DE818EBAD4F}
ORO FINO 11012022 | {81205B01-8688-4570-8F47-B08F18EDCF16}
ORO FINO 1101CB | {4F055C2B-F555-47EE-931F-D64958E5EDAE}
ORO FINO 11022090 | {D1240401-ECAA-4BD1-99E5-871723028078}
ORO FINO 11022236 | {C813897C-7FF0-4426-960C-CC77387AFFF1}
ORO FINO 11022556 | {6018A7D7-F178-44F7-B593-CA41A45039FD}
ORO FINO 110239154 | {2FC41A94-8141-4836-94D8-D074E279E487}
ORO FINO 110239154 | {A0DF0310-E76F-4503-848A-EC07BD6D9878}
ORO FINO 110239154 | {A92F717F-76F6-4DE3-9FB1-FEA02A2BC227}
ORO FINO 110239154 | {B0E99E01-0D27-4597-A594-1741A25A99A7}
ORO FINO 110239154 | {B1149BFB-EDFA-46D1-B822-44352980F037}
ORO FINO 110265932 | {EE93E5CE-FD33-44EC-A329-FBA8C511073C}
ORO FINO 110265932 | {5618B278-348E-4F2F-99ED-BBEB44B38F25}
ORO FINO 110276008 | {EEE4445E-754A-4610-952B-CBD9BE00EDE8}
ORO FINO 1102787504 | {5292D5EF-8994-4D5E-873A-57C44F72ACD1}
ORO FINO 1102805744 | {DBAC8922-D1AB-4A69-B731-70E9382F5DF4}
ORO FINO 1102CB | {4BB60C53-9CA3-4098-8B28-FE44C4ECF9D3}
ORO LOMA 11063650 | {E12EEC5C-3034-4448-A5AF-CECE82A0BEF6}
ORO LOMA 11069790 | {C28605C3-668C-4B5C-ADA0-9056DAF39EFD}
ORO LOMA 11173740 | {C820BB58-E1B1-4D66-A2E0-22C9B53183CD}
OROSI 1102617446 | {38342D33-FCBD-48C5-A427-7A9D99AAC119}
OROSI 11027948F | {283D946E-F745-4F7C-ACE9-D6EB2A3744AC}
OROSI 1102CB | {283D946E-F745-4F7C-ACE9-D6EB2A3744AC}
OROSI 11037901F | {029EB0AA-88F8-4BF4-93B1-3A5396293CB7}
OROSI 1103CB | {029EB0AA-88F8-4BF4-93B1-3A5396293CB7}
OROVILLE 1102434320 | {010ABE92-9760-4A20-97C4-698DB24D3E2F}
OROVILLE 1102CB | {581D49A7-9F4F-4C9A-B76D-C943A94B162C}
OROVILLE 11042588 | {6CD595E0-0633-4F8D-A21D-706EDE410B88}
OROVILLE 1104CB | {DF8BB72F-C21D-4A12-8CBC-5B84FF3140AA}
ORTIGA 11063770 | {F76B220C-9B12-4060-8FD5-AA7B30439772}
OTTER 11012052 | {ADEA2AA0-7D11-4F36-AA83-95B5C9DEA776}
OTTER 11012052 | {E3F93E31-1671-42B2-A17F-FBDD23B44199}
OTTER 11012052 | {64CB4C99-55F9-4CDD-8DE2-173258603853}
OTTER 1101440 | {9B3F8B66-8E8D-4C3E-B30C-F806C7A06324}
OTTER 1101CB | {BB161BB9-B628-4038-939A-BDBCD448B75E}
OTTER 11022002 | {BF5568ED-9C16-497C-B05F-AE0C967E64B7}
OTTER 11022012 | {5B008FE4-7524-4C11-8819-B0F9661FD099}
OTTER 11022166 | {C47B4B77-9CC6-4665-96AD-097EBCE52988}
OTTER 110263868 | {11A5B6DF-81F1-427D-A78C-DE7EF2F392AC}
OTTER 110298036 | {05EEF29D-5376-4D63-9244-FB865CD63617}
OTTER 1102CB | {D42BED5F-FA94-4772-B8B5-334F2629EC25}
PACIFIC GROVE 04222608 | {45F66B28-3708-48B3-AEFE-0F1CE66015AD}
PACIFIC GROVE 04222614 | {45F66B28-3708-48B3-AEFE-0F1CE66015AD}
PACIFICA 110110067 | {2C30988A-F66E-4A90-B5B0-67ED6781F8F5}
PACIFICA 11015001 | {4118C23A-F427-46E8-85D2-FD56A1055C29}
PACIFICA 1101CB | {0685C5F8-0970-41C6-89BD-EFB0337B96FB}
PACIFICA 1102267868 | {275774F1-4908-4480-8C4A-1E1AEF9EEB75}
PACIFICA 110252715 | {9452BDE0-DE70-4463-B819-B9B0CA79D823}
PACIFICA 1102660408 | {002FC16A-D8E0-4EC1-BCF1-D174F5CB0D0E}
PACIFICA 110266732 | {2E2285AC-DBD4-4A01-BBCE-F25D437434C6}
PACIFICA 11026783 | {19E4E8D4-9C4C-4C6B-8FB5-CC59DB118DCE}
PACIFICA 1102934870 | {CFE1B2DE-63B7-4084-B6EA-A58F62A2EB56}
PACIFICA 1102968736 | {6BD2C65D-7217-43E0-B7BC-E7737DB1CECA}
PACIFICA 1102CB | {3BE78651-BE87-4B28-8A48-F46DBB91FDDB}
PACIFICA 1103915474 | {572B383E-2937-4EFC-BA24-50423EE8A457}
PACIFICA 1103CB | {5EC3A666-1799-428B-8C0E-2A981579542E}
PACIFICA 110410195 | {C0B7FBD5-C48E-49C2-A7B2-8E06D90A6C57}
PACIFICA 1104230272 | {233FC7C5-A8F9-452B-B547-9495E8EC73B6}
PACIFICA 1104CB | {EC3F19B1-655E-438D-8AA0-F3D32FED5878}
PALMER 110198478 | {68615336-79DC-4EC6-9727-806E7A643D26}
PALMER 1101CB | {EC1B6C10-3B8B-426D-86D3-39EE85F08618}
PALMER 1101CUSTREC | {EC1B6C10-3B8B-426D-86D3-39EE85F08618}
PALMER 1101M82 | {51B50550-2616-4B8D-8593-9330C414F251}
PALMER 1101M84 | {F73EB641-FFE0-4811-B0D3-9263F0EA89B1}
PALMER 1101M88 | {A85BAC06-7F10-4768-B721-E152D18C46EA}
PALO SECO 0401450678 | {CA3D00F3-FCB7-4F7A-9ADF-E9E789C26B1E}
PALO SECO 0401CB | {0E3E2146-50FB-4065-BA86-A817B98C8BBE}
PANOCHE 1103107270 | {9F8F9B54-61D9-473A-8686-65EC8068C547}
PANOCHE 11034008 | {0C7E1298-8ED7-4AF4-8E12-9D89E23F7125}
PANOCHE 11034010 | {8C4CDF18-070E-4712-A105-26C4CB39CA5E}
PANOCHE 11034036 | {AD986AF1-07AD-469F-94A3-573792C7B7E5}
PANOCHE 110390540 | {2A3253A4-EBC1-4720-AE66-B68045C8C594}
PANORAMA 1101713592 | {70311009-6B82-4803-BF61-8884A737A669}
PANORAMA 11019092 | {18BCFDD7-AD26-4B95-9A8E-1B5EFFBCB7AF}
PANORAMA 1101CB | {39175FAF-A6C7-4043-8D47-1A655E22AF59}
PANORAMA 1101CB | {9B056DF9-5520-41DF-AC7A-220983243590}
PANORAMA 11021249 | {6303BED6-9051-4E72-A1E9-A3825361F885}
PANORAMA 11021342 | {6303BED6-9051-4E72-A1E9-A3825361F885}
PANORAMA 11021526 | {D4F4CD74-DB1C-49F4-9D89-1A434E6A2652}
PANORAMA 11021632 | {CE87ED54-B441-462F-AE1C-C4DF9A1FDFBB}
PANORAMA 11022009 | {A631613E-AC26-415F-BA05-B8776DE457AF}
PANORAMA 11023320 | {A631613E-AC26-415F-BA05-B8776DE457AF}
PANORAMA 11029762 | {C1937D12-32A7-40CA-876D-66A02478084B}
PANORAMA 1102CB | {BF983BB2-B79A-4F98-B895-74C5BCEB2BA3}
PARADISE 11032486 | {5B855AD3-6AFC-4928-AA0B-CD83074FF6CB}
PARADISE 11032534 | {5CECBD86-FB53-4749-ACB8-FF49C0BE2397}
PARADISE 1103CB | {48AC6062-842E-4704-B9FE-79DC1EDEBB68}
PARADISE 1103CB | {916B572F-25AB-43E4-8DCE-50B2436F4EE2}
PARADISE 1103CB | {A11645D5-03E8-4973-8D5A-775ED452B101}
PARADISE 11042034 | {F797DCB1-C578-4B28-B5FA-B1147A5E9141}
PARADISE 110439214 | {1CCA13E6-0B87-4BF0-8C65-1F382E0EC595}
PARADISE 110439216 | {7AEC9581-2505-41E3-BEE2-C11F0B787970}
PARADISE 1104920400 | {1341CA63-432E-4CD8-BB46-467A27C9C55D}
PARADISE 1104954322 | {E166525C-A57D-4F06-BD7C-C2B52E2E9B6B}
PARADISE 1104CB | {60D04F67-B0A9-4BD6-8DCF-759CBE65FF11}
PARADISE 11051212 | {3A3C4FDA-6EA3-4A05-AE15-F95A09F30BC3}
PARADISE 1105121988 | {BE2BD7AC-D920-438D-9D8D-1EC5AAEC4CAF}
PARADISE 1105828400 | {4E875C07-9BF0-416D-8352-B1380CD2F62E}
PARADISE 1105829194 | {DA9F7CD6-6FE2-485B-BB50-5251F27CEFD7}
PARADISE 1105878870 | {4F7F1505-2A84-49CE-A88A-5D1C68BB7B5C}
PARADISE 1105960434 | {4F7F1505-2A84-49CE-A88A-5D1C68BB7B5C}
PARADISE 1105CB | {4E875C07-9BF0-416D-8352-B1380CD2F62E}
PARADISE 1106CB | {54AC0ECA-BD93-49A2-9B30-909ADBE15177}
PASO ROBLES 110195810 | {EDB8367F-06AF-4145-97CC-734EE720D9A7}
PASO ROBLES 1102R64 | {B7E49A70-A833-4F14-A4E0-7628D7D12C4C}
PASO ROBLES 1103351084 | {8A0F9F4E-D4AB-4BFD-A1BC-FC8BA1E7A461}
PASO ROBLES 1103540954 | {54C33D76-49ED-4047-86CC-E79A7FB4D790}
PASO ROBLES 110355374 | {7E3660A3-92BC-4694-A2D5-248E2793B9A8}
PASO ROBLES 1103CB | {5A5ABA2D-583E-4687-9FE8-7872A20C2CCC}
PASO ROBLES 1103N02 | {75A395F4-172A-4FF6-844A-F6A1B941CE83}
PASO ROBLES 1103N50 | {382A16B7-3BCC-4C59-941A-61838BC92D6A}
PASO ROBLES 1103N52 | {35122D11-1E93-423C-905C-FD3596B054C4}
PASO ROBLES 1103N54 | {3D8A845E-016A-4676-A95E-AFB35541512A}
PASO ROBLES 1103N58 | {ABB59667-7D2C-427E-8CD5-70D7C7F4474B}
PASO ROBLES 1103P08 | {1FA86F64-861A-4311-896C-8F2E15FE3A38}
PASO ROBLES 1104998752 | {FBC10DA3-7702-4FA4-B763-5E3BEB4D8D94}
PASO ROBLES 1104998752 | {330F1436-5F6B-47F8-9E18-2B1C20154586}
PASO ROBLES 1104CB | {ADE2AF2F-AC34-4AA3-BF28-71F3B3370640}
PASO ROBLES 1104R12 | {4348EB98-7F3C-44FD-A7F0-CBA935871986}
PASO ROBLES 1104R14 | {8D8A441E-1C9B-4D22-BCF5-1C9794F2F9D9}
PASO ROBLES 1104R56 | {3A535F79-B416-456C-A3C1-BEDA8326FF1E}
PASO ROBLES 110638682 | {931CA1B4-3667-4C96-9792-EB8AF0018AF4}
PASO ROBLES 1106CB | {569EC071-DD47-42F2-9569-DF5DC93512CB}
PASO ROBLES 1106R70 | {931CA1B4-3667-4C96-9792-EB8AF0018AF4}
PASO ROBLES 1107164828 | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
PASO ROBLES 110764703 | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
PASO ROBLES 1107826368 | {3681E2B2-3C69-41BC-898C-6BA327012404}
PASO ROBLES 1107CB | {F753CFBD-929F-4059-9A39-67C517F8ED5B}
PASO ROBLES 1107CB | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
PASO ROBLES 1107P22 | {1C337801-E008-421B-9399-975B6DF38CC5}
PASO ROBLES 1108P28 | {674E461B-DF8C-43E8-8C03-AA3C3BF037C3}
PASO ROBLES 1108R10 | {F6C975A3-F727-462F-BF14-05FA1E630EB4}
PAUL SWEET 210212850 | {F743E5C1-4CE6-4D65-B6FE-D0B8E82E2CBD}
PAUL SWEET 210216006 | {ACD82200-9A89-4E0D-B5FF-D276794568F7}
PAUL SWEET 2102168368 | {720DB739-6D0D-4A39-B396-1773770EDF72}
PAUL SWEET 2102337544 | {593613BC-2474-4D8A-8E89-2D049FCAFE94}
PAUL SWEET 21025291 | {ACD82200-9A89-4E0D-B5FF-D276794568F7}
PAUL SWEET 2102774760 | {494C5866-0CBE-4898-9CD2-71A0E0DFEC0C}
PAUL SWEET 2102777828 | {F548DBEB-2204-4D4F-9EDC-F093EA4A006D}
PAUL SWEET 2102CB | {E84E756D-50CD-4E19-9CC3-E6F7306D45B8}
PAUL SWEET 210335240 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210349370 | {751E8B54-6492-47D2-8237-81A7BF27A640}
PAUL SWEET 2103811390 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 2103CB | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210410916 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 2104273794 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 210437482 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 210438286 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 21045394 | {D6E3B990-3B6A-4843-9D6C-590EB1D40E85}
PAUL SWEET 2104867374 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 2104885736 | {9BB76603-65A7-482F-A2CE-E72536A0A1DF}
PAUL SWEET 2104CB | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 210510290 | {33AE2657-6F42-4109-A970-89EF5E991C73}
PAUL SWEET 210510918 | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
PAUL SWEET 210516008 | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
PAUL SWEET 2105197474 | {33AE2657-6F42-4109-A970-89EF5E991C73}
PAUL SWEET 2105893980 | {33AE2657-6F42-4109-A970-89EF5E991C73}
PAUL SWEET 2105959032 | {DC6678BB-B73F-4EC1-B958-DDA4A1A4DD5B}
PAUL SWEET 2105CB | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
PAUL SWEET 210612828 | {35A821AF-CADB-4929-9F1D-038A70D8EFD3}
PAUL SWEET 21065178 | {7E071814-6E26-47AC-8D93-17E4616D1F83}
PAUL SWEET 21065178 | {CC7AE606-3471-46F7-B0D5-980B87C65360}
PAUL SWEET 2106607772 | {5CFD19E5-804C-4EC5-B475-DE099B6B0FA7}
PAUL SWEET 2106974130 | {69E6957D-6712-43BD-9A8F-B645CA82F0D2}
PAUL SWEET 2106CB | {20C18C61-423B-413F-AE41-A93513864053}
PAUL SWEET 2106CB | {3E23A7A3-C33C-44B7-A4F6-DB4402C4D050}
PAUL SWEET 210710986 | {281B3385-4F71-4EC0-B77E-390E15EC23C1}
PAUL SWEET 2107179744 | {F171F536-3218-49C2-B438-37B0DF63D0C5}
PAUL SWEET 210737234 | {137C6E91-EFA6-4F4A-9FB1-51BD0ED5008F}
PAUL SWEET 2108467366 | {62614D7C-C46B-4061-8F81-503DEACC476D}
PAUL SWEET 210855904 | {62614D7C-C46B-4061-8F81-503DEACC476D}
PAUL SWEET 210875588 | {62614D7C-C46B-4061-8F81-503DEACC476D}
PAUL SWEET 210878006 | {62614D7C-C46B-4061-8F81-503DEACC476D}
PAUL SWEET 2108CB | {62614D7C-C46B-4061-8F81-503DEACC476D}
PAUL SWEET 210910216 | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
PAUL SWEET 2109634576 | {270FCA15-092A-4BC1-985F-1AAFCAC44027}
PAUL SWEET 210980246 | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
PAUL SWEET 2109CB | {7FCFEDBD-6985-4E47-ABA1-988C2AB4CA93}
PAUL SWEET 2109CB | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
PAUL SWEET 2109CB | {12F9217C-0E98-4CB6-8403-4C09E1874A0F}
PEABODY 2106CB | {369633AA-CFA4-4128-87F4-3265F391CCA6}
PEABODY 210813402 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
PEABODY 210818182 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
PEABODY 2108CB | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
PEABODY 2108CB | {ADE1D1FD-7F67-452E-9E37-895B8A824D56}
PEABODY 211340336 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PEABODY 211357908 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PEABODY 211375820 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PEABODY 2113CB | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PENNGROVE 1101170 | {1A72E14C-38B8-4F2E-A8C3-6BC5686CFD94}
PENNGROVE 1101190 | {FC0AD92E-E9B6-43B4-B87B-301D88F19DDA}
PENNGROVE 11013476 | {9D558E42-88D5-42F3-808F-02B4EF74376D}
PENNGROVE 1101554 | {29853D86-D10B-44F9-9B31-548850DBE0F0}
PENNGROVE 1101554 | {992D79E1-6AF5-422C-9178-CF16A35823EE}
PENNGROVE 1101730740 | {A0067835-951C-4E33-B8BA-E12B7D0FE2B4}
PENNGROVE 1101950828 | {B6A14AF2-2E92-4A8B-A025-34671BE1E9DE}
PENNGROVE 1101950828 | {320376BC-0C55-4C2D-ABA9-F531E017D7D4}
PENRYN 11032198 | {15328E03-B147-4A5F-A6DD-FF57B3032B26}
PENRYN 110351658 | {9E584244-489D-49B0-8EC4-8B40DD374169}
PENRYN 1103604 | {E0C71142-0733-49C8-8AA5-49865B61A687}
PENRYN 1103660 | {E80D319C-D01D-4A69-9210-7A23DDD13D1F}
PENRYN 1103CB | {87180880-8EB9-4F8B-82CC-028E4C7029F0}
PENRYN 11051342 | {C5308B22-07AE-4998-BAA1-CBC87B70637B}
PENRYN 11051378 | {1E1BA976-38CE-4912-807F-3A5F3BFF5CD1}
PENRYN 1105154362 | {A58D8351-9C68-4CA5-80CA-5BE208F9F034}
PENRYN 1105168616 | {91345D7C-F3FB-4825-B072-AFC3A521036D}
PENRYN 1105196418 | {C6ED3044-D174-430F-8880-19A3EDFC2300}
PENRYN 11052406 | {A6C70D14-E593-46FB-BE1A-9881978863D6}
PENRYN 110550548 | {00BC1CA8-06FB-48A4-95C2-0F674B5818F3}
PENRYN 110550550 | {38FA411E-5935-4516-9773-4CAD949A1A2A}
PENRYN 110550550 | {D349A8E8-4CB0-4AF5-8711-156EA1F6C1E8}
PENRYN 110550550 | {E8C857BD-8FA0-4293-8DF8-8699935C5887}
PENRYN 110551676 | {6FA4A1F6-3AB8-4114-8002-DF4E0174192B}
PENRYN 1105CB | {52904CB5-03B8-4344-8C19-2DFFF3E5223D}
PENRYN 110651674 | {2BBB97CC-A78B-43EC-BEB0-66A2E29BC2E3}
PENRYN 1106980728 | {1524F2FC-2DED-4951-9267-9B0CA2F011FD}
PENRYN 1106CB | {C3E0B410-F242-443E-BF4E-9C519E692FDB}
PENRYN 11072410 | {88D11C1E-94DA-491E-B166-BE630EDE0741}
PENRYN 11072704 | {3C765F3F-8878-4C34-98CF-2D3F31F6AD44}
PENRYN 11072706 | {A3F26B0A-1692-42C7-87B6-33C42D499946}
PENRYN 11072708 | {B656F43A-A721-479D-8405-E771FFE89131}
PENRYN 1107346 | {CD96B61F-E4EC-4F93-8ED7-3657DC7B6074}
PENRYN 110790970 | {9DF5CB55-1623-4B4B-9F53-43CFDE7622F1}
PENRYN 1107CB | {44D8E601-5E0A-4B0D-A783-27A4770DE5A5}
PEORIA 1701169700 | {E1710560-8ED7-4937-8CD5-CC64CD263529}
PEORIA 17013186 | {52FB3514-9C62-49DD-A158-2A9A7CF95D5B}
PEORIA 170169124 | {8AAD3A20-76BA-4DD7-9403-7AA47644DC04}
PEORIA 170176030 | {CF97D77D-981C-448C-B149-87042BADEDF7}
PEORIA 170184318 | {CB8A5610-26AF-406C-A01C-6D3A6199376B}
PEORIA 170190090 | {CA1036D4-6988-4718-9A58-7F114C1260AF}
PEORIA 1701CB | {3B5F2B21-B073-4B15-A884-38AC36D267F6}
PEORIA 170411232 | {320BFDAF-F5A8-4096-BB62-ECF18634253B}
PEORIA 170413490 | {D6A9F596-51F2-4D36-A52E-B2F47C72F950}
PEORIA 170413494 | {1EA8CF8C-ECB4-4CEA-BCE6-3A74137F1411}
PEORIA 17041837 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
PEORIA 170449256 | {F440C80E-DEF5-43B1-88DC-EE268B4D5DB0}
PEORIA 170459596 | {73788ED7-3EB0-46BC-B768-F67E7458E32E}
PEORIA 17046090 | {7EE01833-70BE-4E5D-9E9A-D8D904929AC9}
PEORIA 17048040 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
PEORIA 1704877670 | {2FC56DAF-3BEA-4D4D-AF4F-08FDD13FFBA2}
PEORIA 170488630 | {6F5293E8-A883-45E5-9872-AC9FAE469C47}
PEORIA 1704CB | {57BF0C33-990B-4465-98B9-17EDC5A10F72}
PEORIA 170510580 | {59D5B837-86E5-4FF6-AEF5-91D544FDF3B9}
PEORIA 17051834 | {843F968C-C902-4C08-BE12-AD0D025C5DF3}
PEORIA 17056697 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
PEORIA 170567898 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
PEORIA 170570198 | {21D2A9B2-3258-44D7-A4FD-EDFB8BC88DE8}
PEORIA 170575274 | {EA8957E8-4D9E-4768-B294-C26CA1256456}
PEORIA 170587222 | {08C43BB5-02C4-4FB7-9500-39371503D9F3}
PEORIA 170590374 | {8B476FB2-9EFB-4231-AA3D-ADAA150B87C8}
PEORIA 1705999 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
PEORIA 1705CB | {7B5B2CF8-2901-483C-B55E-83E22B23519F}
PERRY 1101200598 | {F3BB7464-D4D3-443C-A678-902DB9A05DA5}
PERRY 1101618168 | {253D76B4-3BD5-4865-BAF3-63AA6DE45924}
PERRY 110179696 | {240D21FA-CC4D-471E-B74F-148F84FE5FB1}
PERRY 110185870 | {EA98B02D-6B86-41AE-8783-1ADC45A8F561}
PERRY 1101925053 | {6549D8C5-85D8-4805-BE3C-6F965C4F0199}
PERRY 1101986322 | {C7DAE941-6DB3-4215-863D-56303A6DD35B}
PERRY 1101CB | {30D7373B-D31B-4D5D-82BF-42F5B4929DAA}
PERRY 1101V74 | {03363AA4-45D4-475B-A70A-74AAA6293936}
PERRY 1101V88 | {081215BD-B859-40D1-BF5E-3B29C95FC4FD}
PERRY 1101W10 | {E1CC4B8A-EEA0-444B-A148-93C085F63A52}
PERRY 1101W12 | {743AA0A1-467D-436E-BBF0-31F00EC2544E}
PERRY 1101W26 | {07DF4B2B-054C-4E25-84AF-DE6FF88C6FF3}
PERRY 1101W52 | {EFFF9048-E08F-4C22-B5E1-9B1A32E0D054}
PERRY 1104CB | {76CD31FD-354B-49BF-B176-66B8A5AE25B4}
PETALUMA C 1108208 | {D6A4485E-AC24-4E5F-8B68-E6B52EAE7CCB}
PETALUMA C 1108233646 | {380213DC-12AF-4B84-9312-495B969AE9CC}
PETALUMA C 1108296 | {87D8E969-EF8D-4B9C-90F3-5A57DD740C7C}
PETALUMA C 110835448 | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
PETALUMA C 110835452 | {D67283F3-E166-4B71-B1F9-990D049050F3}
PETALUMA C 110856774 | {E5F8D630-F65C-4493-B471-181129A51D2B}
PETALUMA C 1108594 | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
PETALUMA C 1108600 | {8BF925A0-2A0D-4680-BAEA-CDD0149B229D}
PETALUMA C 1108600 | {B9E22F01-648D-4F6F-B1E0-311BE99AC492}
PETALUMA C 1108618 | {F9D85BA5-F081-4C89-8A4E-6F66CE119492}
PETALUMA C 1108630 | {707F90B6-29D2-416E-88CB-4A65D150CEBD}
PETALUMA C 1108632 | {276EDBF0-4288-4842-B2CC-B94871DC6986}
PETALUMA C 1108636 | {BE0D8CE5-BE7F-4D94-B792-C4D840A2819E}
PETALUMA C 1108883512 | {177BEE80-A728-4F61-A7CE-6DDABA69C9A9}
PETALUMA C 1108CB | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
PETALUMA C 1109128 | {003177BD-8A4D-4A57-8E37-AC044D50D3EA}
PETALUMA C 1109259100 | {CBE2D558-4F9F-4EDA-8260-3A87B72F1065}
PETALUMA C 1109270 | {3706FF29-9CD7-48BA-89F8-13A11ECD321F}
PETALUMA C 110948000 | {762F2724-D687-4C14-8C14-CCCD968810AC}
PETALUMA C 1109664732 | {485D794E-EDB7-4779-A265-326DD68DD55C}
PETALUMA C 1109738866 | {0A86DDE1-72D3-4AA4-946A-5E91F4735FDF}
PETALUMA C 1109820458 | {E3B7A6D0-5E5C-4112-ADBA-8CB389502FA6}
PETALUMA C 1109857148 | {3A66DE77-5865-4829-AC80-A8B849C71DE4}
PETALUMA C 1109CB | {42F8D929-F3A9-49A8-94C4-A1A9328D939B}
PHILO 11013700 | {1642E076-5F84-4CD5-A49F-E61735A3F10D}
PHILO 110137222 | {B4EDF571-A5E6-4473-9456-D58C67AB0D1F}
PHILO 1101CB | {A45E0124-BCF3-4DBF-9317-CD21317A326D}
PHILO 11021308 | {EADE9BC7-FA33-4E78-987B-E6772CEF7A88}
PHILO 11022600 | {3CE6E0FA-7B27-4ECA-8734-864D34B81F8D}
PHILO 1102920 | {BC0A2CA4-638F-47ED-8CA5-834F5A792974}
PHILO 1102928 | {946F4845-815D-4480-AA93-F475D8FE739E}
PHILO 1102CB | {95C075DB-0A6D-41A1-A6CC-0BF07BF73E40}
PIERCY 2110866388 | {901C47B4-25C2-4C9B-9657-50A16616D760}
PIERCY 2110CB | {6C9416AC-4CC1-4577-A462-96F88C7F1AEF}
PIERCY 2110XR258 | {EB657CB8-596F-4421-86E3-2C8A72D44EE1}
PIERCY 2111CB | {F69D714C-099F-426C-95FD-DACECE33C433}
PIKE CITY 11011720 | {07E52C28-7426-408F-9FC2-C4593A9ACBA6}
PIKE CITY 11011730 | {5771C40B-154E-478C-BBED-0818A68D33F0}
PIKE CITY 1101935730 | {CAA18DED-EAEF-41E1-8550-BD2B57FEC276}
PIKE CITY 1101CB | {1B4AEF1E-3888-4CF0-B5B2-91A85959940F}
PIKE CITY 1102CB | {C855B1F9-E043-4F7B-B17F-9A4E0F007042}
PINE GROVE 11011021 | {5E0ECFE9-34C5-4F2B-8405-6E29B71598DF}
PINE GROVE 11013166 | {FB4870D6-B142-4F5B-9D0C-2C983965E8D9}
PINE GROVE 11013170 | {207F56DE-FF3F-4FB6-9F25-8FC555D28285}
PINE GROVE 110152088 | {1330A2A7-6F05-480E-914F-CD520FD996F9}
PINE GROVE 110194936 | {0F46298C-BD7C-494E-910E-FE65C6C90770}
PINE GROVE 1101CB | {5E0ECFE9-34C5-4F2B-8405-6E29B71598DF}
PINE GROVE 11021222 | {B84BB2A7-38F5-4777-ACCF-AE61211F946D}
PINE GROVE 110213438 | {D284AD02-1208-4AE0-8968-E88D8134BCC9}
PINE GROVE 11021765 | {B84BB2A7-38F5-4777-ACCF-AE61211F946D}
PINE GROVE 1102269286 | {163AD319-AD93-4675-83CD-83770D9870B7}
PINE GROVE 11023168 | {EAFDD43F-F7FF-4388-8EDB-D22261F3737C}
PINE GROVE 11023172 | {0A126708-7779-4E45-A8D5-6CB2B8C285C8}
PINE GROVE 110235576 | {C8B6F5A4-B7EB-4267-93EF-866DFF4F4584}
PINE GROVE 110245292 | {EB0CF7B2-4A78-45DE-8AED-51D903B9E71F}
PINE GROVE 1102467560 | {0D3BE776-7F21-48C6-8A4E-A95714C0EA5F}
PINE GROVE 11026080 | {B48DDE03-609C-4554-A3F2-3D029A190740}
PINE GROVE 1102696442 | {7DC1A977-4A68-4FDA-A273-23C4AF2AACBE}
PINE GROVE 110283098 | {6F523CC1-7B62-49B9-AAF8-BD03742BA043}
PINE GROVE 1102CB | {29253623-89FE-435D-961C-4E4487404246}
PINECREST 04011818 | {D8E71690-B481-4860-BE72-8B484DD0017D}
PIT NO 1 11011552 | {47AA609B-0BD3-40D9-878F-3D1F5D334A7D}
PIT NO 1 11013312 | {603720E6-C08C-4450-9A1D-FFFC2D98E7C9}
PIT NO 1 110170952 | {8AC91F5C-D86E-4B8D-B342-7C652EFA0FA1}
PIT NO 1 11019702 | {240B9597-FDF1-4E00-A581-05E13375E11A}
PIT NO 1 1101CB | {185974AB-4212-4B5F-B111-C93E97C24964}
PIT NO 1 1101LR-RC-A | {240B9597-FDF1-4E00-A581-05E13375E11A}
PIT NO 3 21011360 | {060881A6-D014-4A68-9103-99AC74B02ACB}
PIT NO 3 21011386 | {4A0A56A3-602B-4EA0-9D5D-4F9EBD3DE945}
PIT NO 3 21011480 | {E236376B-9C17-4833-888F-1B5788910DB2}
PIT NO 3 21011482 | {23C4AB75-7BD7-4D2C-8DD3-FAC1E53F0F0D}
PIT NO 3 2101CB | {5C4A4B21-8DC0-4DD4-BD69-EB88E21328E5}
PIT NO 5 11011614 | {1BEC31F5-3F54-4C7C-921A-7E6673591BD6}
PIT NO 5 11011618 | {83B8DDA8-0AE6-4FAA-9DFB-D57952CAA5C2}
PIT NO 5 11011658 | {B21A40B5-551B-4708-A4A5-34576C3781E9}
PIT NO 5 11011660 | {06EBCEE6-C636-4CF7-B3B5-D5C157499FDB}
PIT NO 5 1101884224 | {3B84F04D-9352-4AA9-91C7-0899748ED548}
PIT NO 5 110190846 | {B00B32D2-7E6B-47E8-9895-8153D924AA94}
PIT NO 5 1101CB | {B85628F4-AFE8-455E-8E14-4DB09FEDE759}
PLACER 1101106534 | {62739046-02AD-4CE7-A6F9-18132F783A35}
PLACER 1101208930 | {53E235AC-648B-4E69-8BA8-94C5D0F7B09F}
PLACER 1101CB | {D36692F8-5845-4D8F-B564-14537DDF3E03}
PLACER 1102CB | {498BEDF6-2946-45C8-8A10-174F646330D4}
PLACER 1103284874 | {390506AD-DEF8-4149-9470-E4570BC394B3}
PLACER 1103429574 | {3FC818D4-1421-4E7E-A0F8-41C3D62E44F8}
PLACER 1103CB | {E0134993-C6C7-47B2-B903-8846B3C865A5}
PLACER 1104426944 | {A52EC61D-8C7F-4197-8472-76105B9A8A93}
PLACER 110451732 | {F20DF12E-C49B-40A8-AAFB-7DBBC88F8ED9}
PLACER 110451734 | {0E740EDA-2722-48A5-9962-250FDAF0A7CF}
PLACER 1104CB | {E502BFEB-ED5D-48C9-9524-9ECF207993E0}
PLACERVILLE 1109CB | {C4A51841-0308-49DA-9C27-2509F9C64A2D}
PLACERVILLE 111019582 | {1EC71CEE-6F35-4B51-874D-1E06DFFEACB0}
PLACERVILLE 1110421358 | {3AD84F54-48F7-4505-9D9D-4F3421C728D6}
PLACERVILLE 1110CB | {8F8EF18B-7E0A-4A9F-9597-8CCBE4E9FBDC}
PLACERVILLE 1110CB | {344FAF1C-9E94-492E-BF33-445657107626}
PLACERVILLE 1110CB | {396926B6-CE02-4BE9-83DD-75CE9B26FF68}
PLACERVILLE 1111610322 | {E8C6131A-05FF-4431-8BF6-8D1D5F5027F9}
PLACERVILLE 11118582 | {3783BA8A-4769-47A2-BDB8-6B31F03E9521}
PLACERVILLE 1111925936 | {EB7ACE47-AB6E-4D80-8A04-7B710C1A3A26}
PLACERVILLE 1111CB | {15D1F2F0-3D88-4B18-AFEC-B03FE833977B}
PLACERVILLE 111219712 | {E3DC7090-B1A0-4812-A562-44F0E2AEC108}
PLACERVILLE 111219712 | {5128CD77-421D-4523-A89C-F1FE4F36DCB0}
PLACERVILLE 111219742 | {CDEEAA53-79F0-44F1-8538-90E3C7AEC3A1}
PLACERVILLE 1112CB | {69C7055C-8321-466E-890B-DA1A435F5398}
PLACERVILLE 21061104 | {DC8F828A-9D78-4250-9936-BA54E6245EA8}
PLACERVILLE 210611132 | {23693049-039B-4514-94EB-4E3AE6138ACB}
PLACERVILLE 210619552 | {0286A39D-02E8-4B52-9BF3-B9BA1A908257}
PLACERVILLE 210619732 | {A0663868-57FC-4799-ACA3-0DE33205B8E0}
PLACERVILLE 21062224 | {BA672D72-863E-4FB8-9458-911126FD31A4}
PLACERVILLE 210623190 | {83B5D9E2-BFF1-452F-91D8-11E4F5A6B453}
PLACERVILLE 2106458188 | {A8CF9BF8-F4EA-4590-A57D-350C35CF2CAF}
PLACERVILLE 210658118 | {05083455-E6E7-4601-AC97-50C4B399F2D9}
PLACERVILLE 21067522 | {A7A5500C-8FAC-46D4-9BD4-7B5D3F1E7024}
PLACERVILLE 2106869108 | {D72E7887-E0C5-4F33-A9C9-A4C38BAA3F23}
PLACERVILLE 2106909258 | {BA672D72-863E-4FB8-9458-911126FD31A4}
PLACERVILLE 210692012 | {724A4FDA-4A16-48BB-BCFD-6B70230700BB}
PLACERVILLE 2106935216 | {2AFE09FA-88B1-4B78-BACA-DA079C6170B5}
PLACERVILLE 21069712 | {C89C3F78-8047-4151-A21B-FC3CD22D755E}
PLACERVILLE 2106CB | {2B2B5B0F-889E-4409-8E49-AFED501AA6CC}
PLACERVILLE 2106CB | {86E99440-83ED-4726-A6BC-38E34FEB5B33}
POINT ARENA 11011296 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
POINT ARENA 11012637 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
POINT ARENA 11013702 | {5DD49BEE-09C2-4674-9D89-3A76B7F55110}
POINT ARENA 110137426 | {92C865B2-0C37-47A7-A1CF-103D45B5F3C3}
POINT ARENA 1101474 | {89838C41-7EDA-4C42-BDDA-1698278E3E6F}
POINT ARENA 1101476 | {E7660F7E-BB9F-4573-B70D-C3EB843F48E4}
POINT ARENA 1101478 | {E4F90CB8-51CF-477D-BA6B-9F60A2DBE5A1}
POINT ARENA 110147952 | {6151271A-BC5B-476A-8700-C63C19F32AF9}
POINT ARENA 11014923 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
POINT ARENA 110183354 | {B01D0AA7-5805-4227-AB93-F941564BB56C}
POINT ARENA 1101CB | {72A22D65-E2E8-42C5-897F-8C8D23CE5089}
POINT MORETTI 110110726 | {F7013B1A-D0D7-4319-B5E7-A5441451D41D}
POINT MORETTI 110112122 | {9CD1A9B9-F6CA-4FBA-A861-B1CC3280E49B}
POINT MORETTI 110135874 | {0FEDAD4D-EB4E-4A00-90BC-1C811C4F991B}
POINT MORETTI 110136514 | {6B3803C4-78D9-4845-848A-F16561C51AFC}
POINT MORETTI 1101415734 | {EF958110-BB67-48F0-BCC0-A7C84F7DFFDE}
POINT MORETTI 11015074 | {744CBA45-CA46-417A-809B-2361EA738493}
POINT MORETTI 11015078 | {FA346406-A3D0-4066-8116-4806F77ED4DD}
POINT MORETTI 11015104 | {2D522AA5-8F8F-4B96-B755-D0E01134E6CB}
POSO MOUNTAIN 21011703 | {703579BF-EEA4-4200-951E-8470D02B6E41}
POSO MOUNTAIN 21012181 | {908C371E-60A0-479A-AB4A-419AF9711AF4}
POSO MOUNTAIN 21013990 | {00D1CA6B-BA0D-48A2-AF6B-44F02D16A6FD}
POSO MOUNTAIN 21014456 | {80FE859C-5651-4408-BF07-1945D67AD54A}
POSO MOUNTAIN 2101720132 | {D06620A3-21E5-4CBD-8A5D-D10ADF106C84}
POSO MOUNTAIN 2101730862 | {9DEB7641-86B6-4F2C-89D5-F69B09FFF284}
POSO MOUNTAIN 2101CB | {53C5BA88-884F-48FE-B87C-D7D9589897A5}
POSO MOUNTAIN 2103388671 | {B9DBC9F0-4947-4732-B802-049D3AB22FD5}
POSO MOUNTAIN 2103CB | {FFDB1F5B-AEE3-4CB6-9A6F-D3D25805592F}
POSO MOUNTAIN 210448268 | {59412086-F782-4166-B6FC-4A718057E9E9}
POSO MOUNTAIN 2104CB | {AA81189C-0FB0-446B-B000-4E0A59F32937}
POTTER VALLEY P H 1104546986 | {0F563298-4ED3-47AC-A822-118BBD6BD4FC}
POTTER VALLEY P H 110495878 | {8D4490B9-6B4D-4F2D-8A60-88D879FECDA8}
POTTER VALLEY P H 11051904 | {E5533EF6-8C9C-453F-A4F6-7E2D2F1E338B}
POTTER VALLEY P H 11051904 | {99C448A1-95CE-4373-846C-DC41955DCE78}
POTTER VALLEY P H 110537476 | {216E9E12-5043-456A-946D-A8BF7CCC2C71}
POTTER VALLEY P H 1105640888 | {DDBE967D-510E-4AA9-8699-FA1CD4531A33}
POTTER VALLEY P H 110564118 | {8488C210-9205-46DA-B608-037FFFBDBA9E}
POTTER VALLEY P H 110576498 | {0A0C5F0B-CE32-47C8-9E33-CC208CAF8F95}
POTTER VALLEY P H 1105990354 | {18F7A415-6C0E-4E68-A9B1-1EAFDA3A8A3D}
PRUNEDALE 110722232 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PRUNEDALE 110722448 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PRUNEDALE 110725695 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PRUNEDALE 11073062 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PRUNEDALE 110736920 | {3866DD60-BF41-471C-88D6-BF070A4B7C9F}
PRUNEDALE 11073712 | {9CE15D70-9BD3-4411-955B-AE06E56BCA8C}
PRUNEDALE 1107CB | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PRUNEDALE 111020059 | {CE89D4FD-128E-4AE3-8F53-291BB3498CD8}
PRUNEDALE 111022104 | {EA4AEF31-2B29-42E0-BD25-BED069AD0B05}
PRUNEDALE 111022160 | {55A8BEF6-0A82-4DF2-9C14-9045CBA42576}
PRUNEDALE 11103080 | {CE89D4FD-128E-4AE3-8F53-291BB3498CD8}
PRUNEDALE 11103716 | {7B756F98-069D-434F-A340-DDF69576DD23}
PRUNEDALE 1110557716 | {04E59C2E-5AE7-4E98-9896-7EC6B1A16205}
PRUNEDALE 1110607060 | {A8CB8177-0C64-42D1-A7A3-6215FC559483}
PRUNEDALE 1110826224 | {664C5E09-6BFA-4699-B652-D7925B82EDA0}
PRUNEDALE 1110CB | {43A69DC1-4C36-4A90-B444-3F421C39E759}
PUEBLO 110247720 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 110256136 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1102662 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1102671 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 110298730 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1102CB | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1104105708 | {56D5B737-FEFA-47EB-AD6B-EFAA05EC398B}
PUEBLO 1104105708 | {F4390A92-E1EF-4E00-AAD7-21DFA3AD530E}
PUEBLO 11042802 | {EB87F1B0-DF58-4672-B521-8B7DD265BE37}
PUEBLO 110447912 | {C8E61154-612A-4546-9186-D3C997DC10CD}
PUEBLO 1104536006 | {EB53C457-3734-430A-A35B-404EF848B72E}
PUEBLO 1104580658 | {9B7A438C-25F0-43CD-AA1E-F241960C452C}
PUEBLO 110459106 | {A4183870-AFD5-4FAE-BBEF-716EC88D1AB1}
PUEBLO 1104640 | {425E28B1-6940-4649-A8D4-A58D56D174C1}
PUEBLO 110475462 | {937DE59D-E2A4-4423-B890-4B26446D8098}
PUEBLO 1104968601 | {17489714-54AD-404A-B125-398990CB9745}
PUEBLO 1104CB | {065E1455-5FE2-4E00-BCA8-63E4665BA32B}
PUEBLO 11053022 | {6A034A59-B030-4B42-9C02-B5134DF1FD0A}
PUEBLO 1105348368 | {CC4E6B7C-3A75-42D2-8AEA-EBA3500E2172}
PUEBLO 1105419634 | {D8943DC9-C3F8-4085-8F3C-401265EC905F}
PUEBLO 1105426584 | {B12F894A-AA1B-44DD-A0B2-C56DB14BFA67}
PUEBLO 110548264 | {2AEE294B-FE8D-44F1-8029-584BDB7857EF}
PUEBLO 1105637242 | {76F5AEE6-B528-46EE-B628-BA0E8A65C596}
PUEBLO 1105642 | {2AEE294B-FE8D-44F1-8029-584BDB7857EF}
PUEBLO 1105684564 | {97C6787C-1A07-4147-A43F-2ED249921F2B}
PUEBLO 1105696 | {78AAB710-6DDE-407F-827D-71666B977FA6}
PUEBLO 1105716 | {A6A5315D-8A62-41D0-A9DC-ABFF612B9C6E}
PUEBLO 1105CB | {88C9735D-F7D9-42F3-A471-0E595E4AABD3}
PUEBLO 21021326 | {F776B1CF-724B-4DB6-A87F-FF45F4D5AD0B}
PUEBLO 2102279478 | {8B54D8DE-AFC7-4F5A-B048-1B02D25789A8}
PUEBLO 2102378860 | {0747EA03-0104-4C39-B232-B182B2FD4D1E}
PUEBLO 2102391312 | {413AA2AE-389A-445A-BDEE-AA83E1C4150B}
PUEBLO 2102595938 | {3F0F141A-08D9-4BE0-A763-3CF7287B44A5}
PUEBLO 2102600010 | {C5942BEA-FB0B-4F3F-A02A-15F17AB72955}
PUEBLO 2102618 | {2D821F7B-3CD2-4C8D-9060-9FD2240F0305}
PUEBLO 2102656 | {95F0930E-F4E9-4090-B429-18E6DA1F891D}
PUEBLO 2102698 | {EFBE7067-1C69-45D8-A9C8-472AE1406928}
PUEBLO 2102769868 | {D239647B-6B20-452B-9F55-A164C653DDB1}
PUEBLO 2102773926 | {F9DE541A-2DEB-4CE3-95CE-87C59E155BAE}
PUEBLO 2102850102 | {5456D4F0-1D4A-4239-AAEE-AF57D0A5D9CB}
PUEBLO 2102895310 | {C669F706-9156-43FF-93FE-C8CD4A8C9FE9}
PUEBLO 2102943820 | {BC3FC9AC-589D-48EE-984C-94B4C353EDD1}
PUEBLO 2102CB | {EB7314AB-7754-4D90-B11B-A641443B251F}
PUEBLO 21031970 | {6032ABA6-AF20-49E5-AB8C-90F3BD669D29}
PUEBLO 21031970 | {D374E70A-F10D-42BF-BFC9-DC52D8E99DC6}
PUEBLO 2103253312 | {D97500C1-9AD3-4748-953B-EC7E95FBED39}
PUEBLO 21033020 | {5A0D0FE3-BCFE-4A12-87C6-884B98130563}
PUEBLO 2103489964 | {5AAB74F0-F546-46F3-9229-78031722C605}
PUEBLO 2103678 | {2B71AD28-97C6-40FE-8942-41E801469F28}
PUEBLO 2103678 | {57474873-8703-48A2-B4C1-3A3164040E5C}
PUEBLO 2103678 | {80E79C4D-3B76-415E-BA02-A8236360DA4C}
PUEBLO 2103694 | {6D5E4552-6F62-4C84-BA40-091D03218161}
PUEBLO 2103694 | {37307117-7712-4B70-890E-D9B3D42408D3}
PUEBLO 210375612 | {0A48EF8D-B34A-44FD-9901-4812541B4E91}
PUEBLO 210378504 | {EDE87926-F33E-4FF5-A8C5-E53D4266C7FF}
PUEBLO 210398394 | {49549F40-A326-4458-963A-8F0223D6E156}
PUEBLO 2103CB | {BBAA1B5B-10DE-4ADA-9508-3668952B4672}
PURISIMA 1101104948 | {9148C0D8-07A2-46DD-848B-3477C31F1CBB}
PURISIMA 110149394 | {3CCA61DC-2699-479D-8396-73463C6B90FD}
PURISIMA 110154728 | {B456B97B-6207-41D3-9457-CFE202A63FCC}
PURISIMA 1101CB | {72519E2E-220A-434F-A310-3B8078E34E61}
PURISIMA 1101CUSTREC | {0E276FF7-E726-49F1-899E-4DA4E59DCF2F}
PURISIMA 1101Y40 | {0E276FF7-E726-49F1-899E-4DA4E59DCF2F}
PURISIMA 1101Y44 | {867AA1B1-4446-48B6-9D80-8E314456C23F}
PUTAH CREEK 1102202158 | {305442B7-01C9-4B14-8BEC-02CC707E6339}
PUTAH CREEK 110242982 | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
PUTAH CREEK 110246012 | {8A0CE410-7B0B-44D2-93E6-B3B628B03752}
PUTAH CREEK 110258340 | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
PUTAH CREEK 110264044 | {17B7D6FE-5F00-4D1F-ABC4-4972705BA2FB}
PUTAH CREEK 110267858 | {14F48B8C-8A8F-4490-B11D-9FE802AC416A}
PUTAH CREEK 1102710384 | {807BE66E-A7AB-4BA1-B8B2-4ADCA53B3B50}
PUTAH CREEK 11028352 | {89E381E1-F842-49C9-837A-CF37A4D6EF66}
PUTAH CREEK 1102CB | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
PUTAH CREEK 11033783 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
PUTAH CREEK 11033783 | {DC819193-AC84-4B68-B90F-9360B8F647B7}
PUTAH CREEK 11038362 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
PUTAH CREEK 11052777 | {D437F6E1-386B-4A56-A527-2C85C72A2065}
PUTAH CREEK 110546162 | {B44C5067-6D0E-4713-9558-13070DEDA962}
PUTAH CREEK 1105617260 | {3FECE4A6-EA4F-4BAE-A132-55F5821EF41C}
PUTAH CREEK 1105748272 | {6B7B9ED0-0961-41C2-AC06-403CFA67D331}
PUTAH CREEK 11058812 | {D437F6E1-386B-4A56-A527-2C85C72A2065}
RACETRACK 170310850 | {56B3B60A-49BB-43A9-9EE8-443CF9005AA3}
RACETRACK 170310870 | {2C817939-22E6-4D0A-962C-2F9F458E8593}
RACETRACK 170311270 | {502CBD17-B1A2-4DA5-B36F-93229EF4E9F0}
RACETRACK 17032553 | {155070BB-C96B-485B-99BD-6B770FC28FA3}
RACETRACK 17036014 | {97ACC61C-80B7-431D-B04B-B9076E222D13}
RACETRACK 1703759144 | {BD9AA387-4336-4A73-8479-F487626759F8}
RACETRACK 17038120 | {B167BE1C-A9FE-47A6-A4DC-3662D3CE2EC1}
RACETRACK 1703CB | {155070BB-C96B-485B-99BD-6B770FC28FA3}
RACETRACK 170455798 | {7E0EED7A-2775-40CE-B357-57739361FC2E}
RACETRACK 1704CB | {128383E7-96CF-4707-8041-13E4B9B7C999}
RADUM 1105420576 | {87051ACA-C17E-4D55-A6B8-1444F89F63EA}
RADUM 1105806392 | {597A5CEE-82F6-4D96-ADE3-E225B0B39A15}
RALSTON 1101100040 | {803AEA1D-DC84-436D-9016-11A398DCA769}
RALSTON 110148936 | {EA4820C6-602A-444A-A1BC-AC0CC345F5D7}
RALSTON 1101836528 | {D07EF46B-1212-40DA-B007-3854AE9B04F4}
RALSTON 1101CB | {C5ED9BB6-82EE-4A74-A509-3A42E5E8C396}
RALSTON 11021601 | {EF774119-F7FE-47E7-8D97-134D999F3AC9}
RALSTON 11022028 | {24F66B4A-94A3-4B18-925C-2BF0060C2435}
RALSTON 11029126 | {EF774119-F7FE-47E7-8D97-134D999F3AC9}
RALSTON 1102CB | {A920E716-9436-4401-AAF8-C3A905DCBD43}
RALSTON 1102CB | {9D20FBB5-A64F-4DAB-A67C-F85E7D67E017}
RAWSON 11031486 | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
RAWSON 11033314 | {7BD4E626-0623-483B-B7FA-C43993C96595}
RAWSON 110385334 | {4FE71C2A-D73C-4875-8301-3BC6248AF0F6}
RAWSON 11039052 | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
RAWSON 1103CB | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
RED BLUFF 11011334 | {0CEFEC1C-E5A7-4802-97C4-53CDE555B5DF}
RED BLUFF 11011556 | {4D690574-08A4-46C5-A589-9057A98DE023}
RED BLUFF 1101453972 | {02EE82C7-BB67-4B4A-8D7D-2704317B6250}
RED BLUFF 1101718428 | {DBFC2760-2222-4664-B92A-F340A001584C}
RED BLUFF 110176020 | {737A9C64-4C75-4B29-81A5-32595FB9B2D8}
RED BLUFF 1101CB | {DB04D68A-27FA-4FDB-A3B9-5AB0FF58478F}
RED BLUFF 1102CB | {C7F1169F-7F4A-4C3C-8022-D0BF917F0199}
RED BLUFF 11031702 | {A3CC161F-1B95-41A3-B30A-2B1FE8B4155F}
RED BLUFF 1103CB | {7FAC2369-AB0B-45B1-8121-0A58A05D1C75}
RED BLUFF 11041302 | {D6DFAF59-685A-49A8-AAFF-CFC87952A858}
RED BLUFF 1104135854 | {34D16F6F-D35F-44EF-AB3E-A4D9BCAF8509}
RED BLUFF 1104135854 | {7A5937DD-12B9-45A4-A4A3-79E6F1361431}
RED BLUFF 11041566 | {EFAF3860-6049-4F8E-AF4B-3D1B6758C8FE}
RED BLUFF 11041630 | {89D48A42-926D-430B-837E-EDF8AFB821B9}
RED BLUFF 110451238 | {E9A98F80-2CD6-4193-969F-CD417879D03A}
RED BLUFF 110451238 | {A009EB05-74B9-408F-92A3-F0FECB371AA0}
RED BLUFF 1104CB | {2E1FA774-5A9F-4570-9AF6-F0EFBD272BA5}
RED BLUFF 11051564 | {9D2C06EE-ACC3-496B-9742-675775229618}
RED BLUFF 1105161818 | {31D1DD7F-CFDD-44BD-88FD-B9B13228B34E}
RED BLUFF 110529222 | {F0D0C191-AC63-4C53-85CC-9DDB5D220867}
RED BLUFF 1105494814 | {E1B190FC-1EE2-469D-B651-D7219D666721}
RED BLUFF 110585632 | {2E98A968-0F7D-44C0-B9F5-8D4D032F12CD}
RED BLUFF 1105CB | {FEC690E3-0920-4E0A-BCDB-0BA1BA1CD1E2}
REDBUD 1101323962 | {9F8ACCEF-B036-4FB1-850C-B401BE3A4651}
REDBUD 1101400 | {928EDF6A-AE60-4D52-BF0A-EE27518314CC}
REDBUD 1101454 | {ADA3ACDD-1F23-47D9-8D0C-75E817018764}
REDBUD 1101558812 | {D899F1F5-45AB-4336-87CB-D9FAA637B64B}
REDBUD 1101708166 | {3492968E-3545-4212-B771-A444F5766479}
REDBUD 1101754544 | {084CA147-3467-4FE1-A862-8038A9834EE2}
REDBUD 110191960 | {44037CD8-DFED-4315-85FD-100A68145FAE}
REDBUD 1101CB | {3ED5FB3A-A2CD-4F13-ABBF-430305FFB318}
REDBUD 11021212 | {5D4D8690-5B01-4EDA-9ADD-A0F82EE8F0D4}
REDBUD 11022013 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
REDBUD 1102432 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
REDBUD 110244119 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
REDBUD 1102510 | {01484F25-B16D-4119-BFC6-A19899DBC158}
REDBUD 1102523244 | {6D1DA35B-F9DF-481E-9974-60E83F30F3F5}
REDBUD 1102922 | {4E034B59-FA2C-499F-8D52-06EA3D1E77EE}
REDBUD 1102CB | {5D4D8690-5B01-4EDA-9ADD-A0F82EE8F0D4}
REEDLEY 1104218022 | {CFE218EA-E766-4A80-8978-21707A20B8F1}
REEDLEY 1104243924 | {15D80CB3-430C-4D10-9907-2D2A3FAA2A64}
REEDLEY 1104274990 | {1B9CB438-3D64-400D-8827-441645AF1444}
REEDLEY 11047892F | {1B9CB438-3D64-400D-8827-441645AF1444}
REEDLEY 1104887932 | {DE4A3F35-1098-43E3-AFD1-E0057FBA11D6}
REEDLEY 11067270 | {549C94F0-8520-4315-9A40-1509DB31AB52}
REEDLEY 1112226548 | {C2478E24-1A2A-421D-B2B6-2DBB6FC30E5C}
REEDLEY 1112477952 | {EE0E49AF-2EA8-49CD-B4D9-4F587BDF49BA}
REEDLEY 11127240 | {0ED60982-9EAF-4A20-AAB0-618C5740E1E9}
REEDLEY 11127919F | {0ED60982-9EAF-4A20-AAB0-618C5740E1E9}
RESEARCH 2101D576R | {06DF90B3-08E5-4846-BD76-E525F02721A2}
RESEARCH 2102183888 | {0695BA0D-172B-47D5-B979-B42944990BF9}
RESEARCH 210263274 | {8B10C5DA-98B0-4CF4-9701-AF65D62D25BE}
RESEARCH 210263274 | {17B0EA25-D73F-4786-903D-45184AAF8053}
RESEARCH 2102644462 | {27A7DE88-D994-4126-81BF-F7729B85F967}
RESEARCH 2102CB | {16057A1D-A77A-4434-99E8-5E9C232075A4}
RESEARCH 2102D537R | {748A5B81-A79F-4986-90A0-2D101111DB07}
RESERVATION ROAD 1101370948 | {0D34A135-9DC9-4BFA-B08B-5EA1A68C4D2C}
RESERVATION ROAD 1101383718 | {1ABACE31-DB52-4FF0-A8F2-ED3023CBC398}
RESERVATION ROAD 1101586340 | {1DF65F8B-4121-4333-A1ED-1B97DCAFF9C3}
RESERVATION ROAD 1101975548 | {F1FA9138-E071-404A-A9E5-572EE0A580EB}
RESERVATION ROAD 1101CB | {D8F287F2-9F47-4079-84BA-BB2B78537313}
RESERVATION ROAD 110222136 | {C1E68105-3858-4273-9D69-DD27BF248870}
RESERVATION ROAD 11023030 | {B5391BD5-06CA-49EB-98DD-175A1FD20C36}
RESERVATION ROAD 11023032 | {966AAD61-7205-4A6B-9491-7F1C72E1ED94}
RESERVATION ROAD 1102303870 | {EC6A2D53-31D4-4E66-874C-302D8025180C}
RESERVATION ROAD 1102CB | {FE25DCBF-8FD2-4D0B-8589-850A3EE5ED4C}
RIDGE 0401CB | {A69D2BA4-3D74-416C-A5CD-5CA28C67DFB5}
RIDGE 0402199970 | {FE7862FE-E265-47C4-88F2-7778C84DCCC4}
RINCON 1101146053 | {3AEF342C-12B8-4583-92B0-7B9C6AC3A567}
RINCON 1101576 | {F4C78492-32F9-47FB-AA37-4818CAE3C60E}
RINCON 1101576 | {F2BD1A32-60A3-49CF-8B6A-1E7442C97021}
RINCON 1101576 | {10BF1DCF-F31C-4230-BD34-98A3E060927C}
RINCON 1101580 | {45DAEF94-8CBC-41FA-B3AC-23C4DF1DF209}
RINCON 1101839669 | {C0A31C4D-93ED-42DB-A4BA-1A3FEE5BD36B}
RINCON 1101CB | {F102360D-42FF-446F-88B4-F431C95B2DC4}
RINCON 1102228730 | {A2A06826-B5AC-4037-94EC-F135DC826294}
RINCON 1102640 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
RINCON 1102644 | {A2A06826-B5AC-4037-94EC-F135DC826294}
RINCON 1102644432 | {AE3754A4-9F35-4D54-A758-926320A19A34}
RINCON 1102666 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
RINCON 110275816 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
RINCON 1102782389 | {06E2A336-248D-48CA-909C-FCEA57AB6ED4}
RINCON 1102CB | {5988784C-46D2-4999-AEE8-C136D520A366}
RINCON 1103198 | {7F16B5BC-4060-4BCC-9EE1-D9EAFE5FD541}
RINCON 1103198 | {8F98E58F-9114-4DF1-BE64-986306B23E37}
RINCON 1103472 | {003E8DD3-C7CE-4179-B86D-B637E24AA54E}
RINCON 1103474 | {6A5817A5-7FC3-45B7-8DC9-2BBA0FD82034}
RINCON 11035152 | {1D81D8F5-A042-428A-8894-895D8E08C89E}
RINCON 1103568 | {A91227FD-6BAA-4D3E-82C2-58CC21F46A65}
RINCON 1103649194 | {2A534FE3-EF17-402C-9700-8C33AB455C66}
RINCON 1103655192 | {40BB98CB-5E98-49A0-9B1A-45D346011806}
RINCON 1103925054 | {A6030DDB-D47E-40D8-89FA-641FC9E29ED5}
RINCON 1103CB | {2A534FE3-EF17-402C-9700-8C33AB455C66}
RINCON 1104207458 | {1E4D7366-24E5-4493-933B-743F7C171401}
RINCON 110499918 | {93D64AED-6AD4-4AFF-BDFB-1B1DAAB3072F}
RINCON 1104CB | {DDE06CFF-C1C8-453E-9DCE-C51203C62E9C}
RIO DELL 11011504 | {6F9BA8E0-5DE1-4B25-826B-D7A1564B0177}
RIO DELL 110138332 | {A95F636D-9823-4D40-A219-A36C35F660D1}
RIO DELL 11018768 | {F40CB029-270F-46C5-9305-F30A68FC7241}
RIO DELL 110192712 | {56AAB81A-EA84-498C-8B2D-C89BEB9CDBC9}
RIO DELL 1101CB | {6FEFE5FA-547D-43B0-B009-E716079C25C4}
RIO DELL 11021504 | {6F9BA8E0-5DE1-4B25-826B-D7A1564B0177}
RIO DELL 11024230 | {83499CD2-C0F0-4DE8-A7FA-CECB9345AEE8}
RIO DELL 11026151 | {68D3E51B-D82F-468F-8693-722B02390473}
RIO DELL 110270960 | {B2A085D5-4C4C-4026-B04B-46CF38E6CB2B}
RIO DELL 11027124 | {AA9B3AC3-107D-4281-A065-CEC882DC5747}
RIO DELL 110275970 | {C155999E-0638-4738-B652-2E7910103A63}
RIO DELL 11028768 | {F40CB029-270F-46C5-9305-F30A68FC7241}
RIO DELL 11028852 | {5E0A571A-4E57-4C9B-881D-B7EA8F011B21}
RIO DELL 1102CB | {68D3E51B-D82F-468F-8693-722B02390473}
RISING RIVER 11011530 | {BE242D62-FFF6-4E73-8F41-DCC9F0527F50}
RISING RIVER 11011532 | {D3F18D5E-2734-47E6-AA3E-0F1256C05891}
RISING RIVER 11019032 | {8F4CC463-393C-4538-A842-1BB0282A8F17}
RISING RIVER 1101CB | {9F15BDD3-391E-4F68-AFF5-FA940D11CF0D}
ROB ROY 210410298 | {F407D1C7-AF54-4B98-B726-B5AC300E0031}
ROB ROY 210410714 | {0A7E84D0-9946-4059-AC56-BD0EC9107E3A}
ROB ROY 210410930 | {6FDB7B55-5D84-4478-9719-37334B4F5477}
ROB ROY 210410954 | {A588ED32-95D8-43A3-8FC4-5077DBA91F77}
ROB ROY 210410960 | {2E6975B3-903D-45C9-9C7D-960FEDF8E472}
ROB ROY 210412582 | {9F9A8C20-EA90-4789-ADB1-26DC34BBE385}
ROB ROY 210412596 | {272F711A-D76D-479D-B7FF-5C57D964944A}
ROB ROY 2104464844 | {ACE07E60-A85A-44BA-8598-8AD2924EF583}
ROB ROY 21045304 | {B079AC67-F69E-4839-9DB7-69A2C23DFB56}
ROB ROY 2104588930 | {E4D9306A-AB16-4DC5-A47E-93AFEF1B142A}
ROB ROY 210467520 | {4F244FE6-F52A-45B3-B8F6-00E33F844A26}
ROB ROY 2104974520 | {A306B6A6-F4A4-47EC-B2AB-9B74651A417E}
ROB ROY 2104974520 | {F68F51A7-51CE-4FB5-9F0F-4256CB67D688}
ROB ROY 2104CB | {869A1D07-AF0C-4C1B-B4FB-3299F6D51C09}
ROB ROY 210511028 | {FFC04C14-5557-4FC3-9795-3587569ECB50}
ROB ROY 210512474 | {FFC04C14-5557-4FC3-9795-3587569ECB50}
ROB ROY 210512586 | {ABFDD865-4FD2-4A37-B95C-CF3A9E9EFA30}
ROB ROY 2105439972 | {C5524593-3C0F-436B-8CBC-A27F9517C316}
ROB ROY 21055090 | {97F0E264-6757-4E01-B858-9C73FC0BF875}
ROB ROY 210571630 | {7097C41D-4FD9-4503-BEF9-0B96E72F7C88}
ROB ROY 2105796388 | {239842ED-B895-435E-91C3-BDF520C0114A}
ROB ROY 21058281 | {ABFDD865-4FD2-4A37-B95C-CF3A9E9EFA30}
ROB ROY 2105931192 | {1C63E144-CC28-45E6-852A-59F6783E5E65}
ROB ROY 2105CB | {65F8EE18-25DB-48C0-8EE8-63D74E373DA3}
ROSSMOOR 110136572 | {DFEFEF45-5177-43DB-BC8B-7506E80A5515}
ROSSMOOR 110168920 | {167EB25B-4A6A-4910-B109-DED2BEFF695B}
ROSSMOOR 11018132 | {71494031-9F05-4CC0-A953-4E31E51E28B7}
ROSSMOOR 110181770 | {4CA94395-6849-4C23-B9A9-BA346C47AF36}
ROSSMOOR 1101CB | {E76B2183-0811-41C5-8C57-31DB4D93EC1E}
ROSSMOOR 1101L501R | {192A3563-130E-4748-AE0C-092D67B95727}
ROSSMOOR 1101L503R | {93932C89-B87A-4F1E-B65E-D8FDB2772713}
ROSSMOOR 1102457174 | {1EF93EFB-6EC5-43CC-BDCD-9E975921D8A6}
ROSSMOOR 1102CB | {92F6E341-F0BC-4716-8F01-EF905EEF4BF1}
ROSSMOOR 1103CB | {A42F88CD-4606-4D31-BD89-060DAE686890}
ROSSMOOR 1103W514R | {D9FD5122-71C5-470A-9067-11BD4B38DBDB}
ROSSMOOR 1104305926 | {E7EBB058-9B4D-4CDE-B87B-5DAAEF3E4493}
ROSSMOOR 110479146 | {DE1365E8-AE71-4371-B78C-316604B54A0D}
ROSSMOOR 1104892332 | {ADD4BDEC-74F1-459E-86A1-4DF14021647A}
ROSSMOOR 110493664 | {D2330A0C-459B-4F6C-BE3B-0AABB85A2AF8}
ROSSMOOR 1104CB | {2B644C8A-1232-4056-B6E3-B09CD0D7D415}
ROSSMOOR 1104L530R | {2B644C8A-1232-4056-B6E3-B09CD0D7D415}
ROSSMOOR 1105CB | {2CF05CCD-DA30-4E66-88FB-8AE7485C3DA7}
ROSSMOOR 1106166550 | {4AEDCE3D-BF5C-4D21-A955-F5F1D5680D0E}
ROSSMOOR 1106384042 | {7E910363-02B7-4903-815B-B702BBD4A69D}
ROSSMOOR 110639424 | {12C41010-8690-4E2B-AC58-964769362CF2}
ROSSMOOR 110665858 | {DE34AA94-F995-444B-B0E9-519FC6F293D6}
ROSSMOOR 1106841730 | {A6B74454-D4C1-496B-84A9-0B2166285148}
ROSSMOOR 1106CB | {2DB57022-ABC5-45C1-B548-D5C0C8717502}
ROSSMOOR 1106CB | {DFA21900-F572-4D0B-90D6-E67080E9EF87}
ROSSMOOR 1106CB | {419AC994-D5ED-4F03-8570-4744F2BAF12E}
ROSSMOOR 1106L522R | {35E6FC31-93E6-466C-8E12-BDEF19C3F3E9}
ROSSMOOR 1106L541R | {F81A28E8-7235-47FA-8A4D-F6D87B334C4A}
ROSSMOOR 1106L552R | {52DEF6FB-138D-4E67-B717-53642F74F0D5}
ROSSMOOR 1107857172 | {82E77E65-B48A-4043-92C4-BD82ECD8745E}
ROSSMOOR 110798488 | {748E6AB1-94A7-498F-8F09-FF430BCD1517}
ROSSMOOR 1107CB | {DC54959B-747A-4CC9-B9A5-4B8CDE5FA47E}
ROSSMOOR 110845268 | {7DDF8536-9630-4E95-BAC2-3F8D7B68665E}
ROSSMOOR 1108543356 | {9FF00501-65FD-4E14-AFDC-F4B11FE19B4B}
ROSSMOOR 1108CB | {812F7F32-99CA-4B11-A2F5-E536332A91A6}
ROSSMOOR 1109266602 | {C56741FC-B98A-4CE9-A61D-A05F5CB14F16}
ROSSMOOR 1109724062 | {80876183-ECA7-4120-8036-545B0D2B5AC8}
ROSSMOOR 1109724062 | {2D5FE1CC-7A21-49C2-BCB1-D308E91FC77A}
ROSSMOOR 110982962 | {72BC10DA-E2B4-4F9E-B1C6-B2A54D23C7DA}
ROSSMOOR 1109847274 | {3141710D-4E1F-480A-88B2-BC542204BF63}
ROSSMOOR 1109847274 | {03879870-FD7D-4E28-B553-CE6842933DB3}
ROSSMOOR 1109890534 | {24E172FD-D392-49B4-BDCF-9D27B2C7E92E}
ROSSMOOR 1109892648 | {07D08030-E53C-4555-923F-76DCDA7152BE}
ROSSMOOR 1109961536 | {6DCAEE0E-EF55-4731-9878-3906C6B80014}
ROSSMOOR 1109CB | {A19250ED-73EF-497C-80D4-3643AA1817C6}
ROUND MOUNTAIN 1101CB | {C6179221-3CD6-4B67-835E-943EE03CA383}
RUSS RANCH 110196276 | {35E834E5-9FE3-4B04-BFD2-7F38E4FACAB8}
RUSS RANCH 1101CB | {E22153F3-5B56-4AEB-89D0-5F7BDC6E5F58}
SALINAS 11043018 | {37BE6D71-E3BC-4DC2-9D89-ECD973BA9436}
SALMON CREEK 1101194 | {4BB38AE8-B760-4E43-B459-E75BDA0EF348}
SALMON CREEK 1101196 | {05737260-3AA4-4F7E-BF36-A5BD94AF80DD}
SALMON CREEK 1101242382 | {196179E3-0F18-4F79-A1AB-13E8430D60AE}
SALMON CREEK 110137368 | {5DC6F02B-24BF-4504-9E01-B7C3B166BE28}
SALMON CREEK 1101571972 | {AC8C3E38-A041-499C-9BB2-FE26BAA0252C}
SALMON CREEK 1101654 | {FFF2586F-2F7B-403E-A22A-6FE170AFE85E}
SALMON CREEK 1101660 | {DD137AF2-2749-480C-8784-159970C4FC2E}
SALMON CREEK 1101668 | {4AA7E9BF-D824-42F7-B4F3-AF51F29BCC9C}
SALMON CREEK 1101676 | {4DCB6ED2-9B7F-4AF7-86F4-3A84466B49F2}
SALMON CREEK 110188998 | {2FFE3F5E-20F1-4C4A-B741-4DF0040A4D91}
SALMON CREEK 1101CB | {227E29C2-4875-4BDB-945B-C5CAEB5F0B81}
SALT SPRINGS 210110416 | {3B618A90-1F99-49FA-8702-76A28A158E81}
SALT SPRINGS 21011216 | {CFBBFBB1-419F-4DD9-BB1F-9B2617993BDF}
SALT SPRINGS 21011232 | {9EF30C64-8412-466B-8695-929E20570E0C}
SALT SPRINGS 210117012 | {6DEB16A6-E94C-4F55-B525-DA7D39192AB7}
SALT SPRINGS 21013116 | {DE9905F1-4C65-4778-858E-371103A18BB4}
SALT SPRINGS 2101TS4913 | {9EF30C64-8412-466B-8695-929E20570E0C}
SALT SPRINGS 21023118 | {56415AA1-122C-4BC6-8C7D-172F2B1EFCC0}
SALT SPRINGS 21023142 | {31EFB8EC-9037-4E2A-A03A-16D15C4387DC}
SALT SPRINGS 210237300 | {635F8134-C2A6-4C23-A242-6F5A1291D1C6}
SALT SPRINGS 21024796 | {3283BC52-8DC8-4138-8A4A-A54B9DB31F1C}
SALT SPRINGS 21028442 | {02C4638B-890A-4131-8AEF-2E0622DB34D6}
SALT SPRINGS 210297924 | {77733CA8-C469-4656-B2CC-06892BE8F14F}
SAN ARDO 1101650772 | {B23131D9-B581-40FA-88C0-EEDBAEACA625}
SAN ARDO 11017094 | {A9BAF716-D950-4219-B81C-E6209F590D56}
SAN ARDO 11017632 | {05828C1E-8E18-466B-88E7-9FC0E3CD182B}
SAN ARDO 1101CB | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
SAN ARDO 1102502 | {DAB3BC36-43FB-41D1-88AE-89CBCEF6CBDB}
SAN ARDO 11027030 | {531BE6B3-C431-4299-B6F9-340C07FC847B}
SAN ARDO 11027066 | {8AD3688B-AF38-466D-9653-33A0316A94CF}
SAN ARDO 1102896438 | {2EE6ABE7-4F0E-471D-A95F-6A7A117EE231}
SAN ARDO 110291894 | {3A8CC481-FD54-4503-B6C3-B374A7E06AA7}
SAN ARDO 1102CB | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
SAN BENITO 2101295566 | {02E6ABF5-EA12-4934-8526-CDD1BECA0A7E}
SAN BENITO 2101310344 | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
SAN BENITO 2101355426 | {309BC145-CE1F-4552-9344-E193E2F32C60}
SAN BENITO 210136912 | {26DCF52C-88DB-4369-A95E-5AA543DE6A37}
SAN BENITO 210136912 | {90A67B0B-7B04-4738-A6BC-63EA48062380}
SAN BENITO 2101506268 | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
SAN BENITO 210192468 | {309BC145-CE1F-4552-9344-E193E2F32C60}
SAN BENITO 2101CB | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
SAN BENITO 210275262 | {5F376FC3-2A9D-4ADF-B538-90322F89F684}
SAN BENITO 2104785888 | {A0912651-34EB-4686-B7CD-51CC5436D4BA}
SAN BENITO 210488772 | {1ED2FD17-894E-4836-A934-5237FD5BF8EA}
SAN BENITO 2104CB | {BECA105B-BD3C-4CFB-85DF-E12EFB68ADA7}
SAN BERNARD 1101438074 | {BF5DD9D5-AD1F-4BC7-AC27-542684EB7C5A}
SAN BERNARD 1101641042 | {46FF504D-69DB-445C-A616-F2DCD009D8E4}
SAN BERNARD 1101830398 | {0FCD66A3-9E49-49FB-A934-531E12B8CE6F}
SAN CARLOS 0402CB | {5D32D1B4-08FE-48B9-8413-A6C8374335DE}
SAN CARLOS 0404CB | {997E35A5-4F56-4E03-9F74-715398B359A5}
SAN CARLOS 0405CB | {55F8A6BE-5507-412F-A65C-4CFD7B83CA1D}
SAN CARLOS 0406CB | {E4554E11-1488-4093-BA83-414508537E1C}
SAN CARLOS 1103313472 | {5D822BC7-216C-455F-A29D-9BF065B0A46B}
SAN CARLOS 11039148 | {976CCE27-9CBA-45DD-8002-F8BFB98C14D4}
SAN CARLOS 11039148 | {2AF16592-8ACF-4420-875B-6CA353988F31}
SAN CARLOS 110436864 | {9E2BE648-1876-419E-9EA6-9561CF55CBC8}
SAN CARLOS 1104699632 | {29D0150D-9878-4E59-901F-2306DBADDF8B}
SAN CARLOS 110475210 | {30A0D7F0-FF87-4B5E-B98B-6A0711429281}
SAN CARLOS 110479774 | {84501BB6-0E8B-48DF-8950-A9E642A52FF8}
SAN CARLOS 1104833770 | {184D8D5D-E270-4177-8D06-41B2ADC4598A}
SAN CARLOS 11048846 | {4B35CC98-8B7D-4556-87A5-A4000634AA4A}
SAN CARLOS 11048942 | {7C12A412-D2AF-4E21-A226-597936BFB6C3}
SAN CARLOS 11049010 | {98FA686F-C0FD-4E53-94B4-4278583D2FA4}
SAN CARLOS 11049052 | {3B6CB851-40C4-4A4E-8C82-B4A7B88943F2}
SAN JOAQUIN #2 110310320 | {6E730337-737F-4AF4-89D0-F209BD78A056}
SAN JOAQUIN #2 1103157026 | {5512EE79-F6AF-4543-8A7B-B7E11740B6C7}
SAN JOAQUIN #2 1103CB | {65F04F88-77E2-416B-8718-E84D34A90738}
SAN JOAQUIN #3 1101673480 | {1AD6607D-F312-473D-9241-E313EE11C5E3}
SAN JOAQUIN #3 1101751914 | {3E893698-E7EF-451C-8E5C-76F173901057}
SAN JOAQUIN #3 1101CB | {5A8D30A3-8AE5-4F6B-B53A-735A17ABC0FB}
SAN JOAQUIN #3 110210342 | {F2F4DFE2-A71E-4AEB-AA05-9FF7D56E28F8}
SAN JOAQUIN #3 1102CB | {F2F4DFE2-A71E-4AEB-AA05-9FF7D56E28F8}
SAN JOAQUIN #3 1103403515 | {4CAF538D-CE7F-452E-B2C8-DD5DB29918D4}
SAN JOAQUIN #3 1103403515 | {FF81549D-0FDE-4FB3-A90C-3283E1A7D150}
SAN JOAQUIN #3 1103CB | {A6A3BCCC-F462-4ECA-85D9-4927341E1902}
SAN JUSTO 110136902 | {37C0E6FA-9A39-4134-9B6F-8111077BFC3C}
SAN JUSTO 11014002 | {3BA4B8C1-556E-4444-9F96-4ADCA52FD345}
SAN JUSTO 1101CB | {6AD7BBB4-B1FA-43B0-AA8E-62099AF74BBC}
SAN JUSTO 1101CB | {01D6D09A-4701-4A4A-B6BC-8E8154C01835}
SAN LEANDRO U 1109936988 | {B5DBD0A3-C077-4EF4-BE1F-A5BF965893FA}
SAN LEANDRO U 1109CR002 | {0A0CA719-3BA2-4B10-8DAF-28B4D94E2A5D}
SAN LEANDRO U 1109CR182 | {A2C189F4-1155-43D0-9466-3E701D18918E}
SAN LEANDRO U 1109CR284 | {42064D42-EDBF-4ED5-8222-65863B241E1D}
SAN LEANDRO U 1109CR344 | {D888F259-DA4B-44A5-A254-AC7BF27B35F0}
SAN LEANDRO U 1114213524 | {A807698D-F940-498F-A1CC-0E26E202721D}
SAN LEANDRO U 1114415780 | {5532AE5B-2A9C-4A33-8635-E69715765EC3}
SAN LEANDRO U 1114458451 | {968A63FA-7805-450A-99C2-EB254D5B48D8}
SAN LEANDRO U 1114501762 | {C98515D1-8118-4F7F-9133-7ABF5BE205C0}
SAN LEANDRO U 1114523960 | {20F07900-C28C-40F2-BFE8-574E1CE64E6E}
SAN LEANDRO U 1114653758 | {535694D1-FE48-4344-BC96-5C27E6A571BF}
SAN LEANDRO U 1114MR544 | {399AB5C7-22B7-4F32-8432-A7E05E9E2D06}
SAN LEANDRO U 1114MR545 | {4B9E4541-F21D-43AC-ADB7-3A92CC33D20B}
SAN LUIS OBISPO 1101483444 | {6095BEE0-0C36-47E1-939F-BFF38B2ABD81}
SAN LUIS OBISPO 1101592368 | {6095BEE0-0C36-47E1-939F-BFF38B2ABD81}
SAN LUIS OBISPO 1101CB | {AD6746AA-B778-4E12-B7CD-DBCB8C9B3412}
SAN LUIS OBISPO 1101V12 | {D3B095E1-F799-4165-8E63-ACB7F609DF06}
SAN LUIS OBISPO 1102357407 | {607A19A7-FE06-4D0F-B488-D2CD33F1131A}
SAN LUIS OBISPO 1102597518 | {22E96A5A-3667-455E-A58A-C0A9770DDF94}
SAN LUIS OBISPO 1102V96 | {9A70A0FE-6E60-48F9-B727-E7F0BBC33E9E}
SAN LUIS OBISPO 1103153199 | {47D9D526-74AC-4FE6-92E3-2FC62834180F}
SAN LUIS OBISPO 1103191498 | {53668CA1-F0BD-426B-87AA-933BC191323C}
SAN LUIS OBISPO 1103365572 | {AF070101-B27C-4E73-95B1-32ABEB0162BE}
SAN LUIS OBISPO 110342344 | {EB029C6B-1104-4127-A12F-6B1C6DB20B5A}
SAN LUIS OBISPO 1103486690 | {EB029C6B-1104-4127-A12F-6B1C6DB20B5A}
SAN LUIS OBISPO 1103CB | {E103D78B-3107-47BD-87A1-E99667F6EAD2}
SAN LUIS OBISPO 1103CB | {80BB619F-1520-4563-BF62-E97585F4D6B9}
SAN LUIS OBISPO 1103V82 | {FCC7352B-1F1B-4520-9419-DD9582012EFB}
SAN LUIS OBISPO 1104236895 | {C973CDEF-EC23-4057-BBA7-53EE9EC7C18D}
SAN LUIS OBISPO 1104350030 | {5E4CECE6-B405-46DF-AB3E-BC23B1171AD2}
SAN LUIS OBISPO 1104721823 | {CD120F30-B41B-4ECF-BCCF-D7752F5F6E79}
SAN LUIS OBISPO 1104777686 | {4B433B40-0A9F-4E4A-AD28-C0C25FE24FB2}
SAN LUIS OBISPO 1104982992 | {48D82405-914A-45BE-AD86-2A9FA02155BB}
SAN LUIS OBISPO 1104CB | {1E7B350B-AD4E-4AFC-A31E-0B3A3DCAB1B5}
SAN LUIS OBISPO 1104CB | {12F1A144-2063-4E28-8860-F6ADF2052849}
SAN LUIS OBISPO 1104V10 | {553967E8-15E4-4695-8C2C-6D609687BE1B}
SAN LUIS OBISPO 1104V14 | {25830136-A5D5-4A08-9B85-05018D7569FD}
SAN LUIS OBISPO 1104V40 | {84A17C4B-1356-4E5D-9790-C7A137661BEE}
SAN LUIS OBISPO 1104V46 | {02896B1A-0763-4C6D-956E-B1F4B47D7741}
SAN LUIS OBISPO 1105796050 | {1A101991-3846-4FAA-AA28-18EF626C5B54}
SAN LUIS OBISPO 110596874 | {5F18F1B6-CBB8-4C1C-BF98-6DFB5D98EA76}
SAN LUIS OBISPO 1105CB | {81973749-CAB3-49C6-B105-0C3D389524EF}
SAN LUIS OBISPO 1107136678 | {20AA80FC-38F3-451E-A79F-A0EADE4A8B5E}
SAN LUIS OBISPO 1107248566 | {93AB4944-1A1F-422D-B748-968CE7493B5C}
SAN LUIS OBISPO 1107456456 | {FE7ADF6B-5FAD-4650-8E18-1F81A8FDEE84}
SAN LUIS OBISPO 1107834556 | {4DD1224C-2170-47BC-A673-A91A93C1B650}
SAN LUIS OBISPO 1107CB | {FE7ADF6B-5FAD-4650-8E18-1F81A8FDEE84}
SAN LUIS OBISPO 1107V02 | {1413E321-0BD6-4E14-989C-C8FF6A4A6DD1}
SAN LUIS OBISPO 1107V18 | {B173AA79-0772-4E9C-A86B-1D2E09D38BFA}
SAN LUIS OBISPO 1107V58 | {3B54DCC0-9E34-4A0D-BB42-D31181D2C4D7}
SAN LUIS OBISPO 1107V60 | {331D14B2-6B0F-4273-9F56-8DD687C4B860}
SAN LUIS OBISPO 1108144690 | {FA97EBC4-7DF7-4291-B59F-FFD92DA4891B}
SAN LUIS OBISPO 1108337126 | {F9425320-A467-49B9-AA89-B48ACFF8F012}
SAN LUIS OBISPO 1108497078 | {7DD2FB96-8661-407D-BF49-CB7A6FA878DF}
SAN LUIS OBISPO 1108CB | {BB99A914-387F-48D8-919A-BB8BCFE90D9F}
SAN MATEO 04048554 | {5D607F0F-481D-4D2A-862A-231FF7901489}
SAN MATEO 0408CB | {72F4A567-A9CD-48CF-9E88-AA2F9E6053A6}
SAN MATEO 04109068 | {5F8605AA-7B64-48E3-B49A-133A5E452602}
SAN MIGUEL 1104954082 | {D0A5F575-D022-443D-85F2-E2AC3A537B53}
SAN MIGUEL 1104CB | {D0F2F587-0747-4792-A057-16325E08E5A6}
SAN MIGUEL 1104R54 | {44EB9D6F-C95C-4275-8EE8-1FAA212EEB1F}
SAN MIGUEL 1104R58 | {5D373241-D81F-4822-B649-3A4A39407074}
SAN MIGUEL 1104R66 | {3F83E7A1-428B-491F-A667-31D49B0E1C27}
SAN MIGUEL 1104R66 | {D2A5E177-BE75-4C23-A08D-DCCEBD7AADF8}
SAN MIGUEL 1104R88 | {C7BB1503-DD28-48B3-9C96-3F6DD2B88AD1}
SAN MIGUEL 1105765824 | {5DAC96E6-D800-4242-8BE0-8DEA9CB14558}
SAN MIGUEL 1105CB | {9DE0BAA2-B8C4-4631-BEBA-CFB3AF750506}
SAN MIGUEL 1105CB | {E94610AC-EC7D-49B9-AE54-6AEAB572BD2A}
SAN MIGUEL 1106428314 | {44EE4AB8-A105-4D73-948F-79D5A2357B21}
SAN MIGUEL 1106605393 | {AE0302DD-E961-46A4-9A94-0278CDDD5E25}
SAN MIGUEL 1106CB | {DC9AC6DA-C366-497D-A431-13D5888CCACE}
SAN MIGUEL 1106N34 | {19CBB8DD-B0DD-40C9-99D6-9DC6A38717ED}
SAN MIGUEL 1106N38 | {7351BABC-DA39-4A67-B463-17C1BA8F0959}
SAN MIGUEL 1107CB | {9AFFCF48-B4BB-4816-B96D-D0BF56E32579}
SAN RAFAEL 11011210 | {C15D2B27-11D0-43EC-9B15-374D2297640F}
SAN RAFAEL 11011250 | {0DD641FC-11BF-40FB-8EF7-3A88160AB0B4}
SAN RAFAEL 1101310 | {1A3DCF6A-D8D9-4366-A0A3-6456AFF85AD5}
SAN RAFAEL 1101312 | {559ECC42-B403-4A94-88A4-68DFDA9F0CD1}
SAN RAFAEL 110139156 | {332AA22A-A859-478E-AF82-419A23B67FF8}
SAN RAFAEL 1101546438 | {D3437865-FD72-4BD7-976C-C052BE1AC57C}
SAN RAFAEL 110168970 | {0E23B264-3DB8-4CEC-B1FE-F1CB20A30CF5}
SAN RAFAEL 1104802 | {E7743FFE-2947-47FD-B4E6-A754209900CE}
SAN RAFAEL 1104CB | {33CCC2F4-F827-4C07-9171-27096EF33E3C}
SAN RAFAEL 11051278 | {DF15C3A9-3287-472A-8D42-2F8516FD478B}
SAN RAFAEL 11051806 | {3E85D65E-30F3-42DB-9ECD-6ED09FB2A985}
SAN RAFAEL 1105344 | {73B969AA-9422-4313-8799-666FFF6134B7}
SAN RAFAEL 1105408 | {25A73CC9-0B81-408B-9142-F5D6802BB119}
SAN RAFAEL 1105534 | {6C0139D5-EF28-447A-8798-DD6F8DC2F6B3}
SAN RAFAEL 1105645362 | {CC6A4E26-740D-42F4-A649-35571E3A45ED}
SAN RAFAEL 1105CB | {CAD39F6E-68B6-4287-AF02-0FE0584C53BF}
SAN RAFAEL 1105CB | {BA67EE88-1E6D-48B2-9DBA-46721926CAE7}
SAN RAFAEL 11061230 | {3CC0B2ED-4CCD-4757-94A4-43056A68F6C1}
SAN RAFAEL 110648752 | {768B2119-8E04-4A0B-9516-B163D4D61FBB}
SAN RAFAEL 110648752 | {85056666-4A2B-4DAF-B399-DC93301E78AA}
SAN RAFAEL 1106588020 | {93B83BF6-0390-40F7-ADB3-1AD8B7256ABB}
SAN RAFAEL 110668694 | {A5DF76D9-626E-4A2E-8281-6888B77A577F}
SAN RAFAEL 110668694 | {8BF78D64-4A44-4B53-8AB6-8417D27FFB87}
SAN RAFAEL 110668694 | {71ACD594-F55A-4D07-9FE3-9B0665AF5F6F}
SAN RAFAEL 1106837 | {3CC0B2ED-4CCD-4757-94A4-43056A68F6C1}
SAN RAFAEL 1106910 | {97049330-0F64-4B73-9906-EB2DC1343DE8}
SAN RAFAEL 1106910 | {5D059BF5-F769-4312-8893-6A2C828C685C}
SAN RAFAEL 1106CB | {A84CB2C0-9849-4D74-A8E8-7B5529F6398B}
SAN RAFAEL 11071166 | {64A83390-336F-46D2-AA1C-9D91A30B0162}
SAN RAFAEL 11071276 | {78640A7E-4385-4C01-A0A7-78496A91C391}
SAN RAFAEL 11071415 | {AC6B2CFB-8470-47A8-8CFF-360D120857F5}
SAN RAFAEL 1107328 | {64A83390-336F-46D2-AA1C-9D91A30B0162}
SAN RAFAEL 1107434 | {7DB3B65A-9BC0-48E9-AEAF-56397C577A2D}
SAN RAFAEL 1107CB | {AC6B2CFB-8470-47A8-8CFF-360D120857F5}
SAN RAFAEL 11081262 | {B486F4D0-4246-4914-B521-4CE6A759247F}
SAN RAFAEL 11081457 | {9D9542F3-BF28-42DE-B61B-60FE0E01870B}
SAN RAFAEL 1108322 | {9D9542F3-BF28-42DE-B61B-60FE0E01870B}
SAN RAFAEL 1108516 | {F2E5D603-195F-45A5-9636-597C9B053516}
SAN RAFAEL 110863598 | {62B0F5C5-018B-42C2-9DA1-D8CCE6714B61}
SAN RAFAEL 1108CB | {8BC2020E-62FB-478E-A2C9-53FD6549A421}
SAN RAFAEL 1109418 | {466136A5-5029-445B-8434-F48A32643962}
SAN RAFAEL 1109535284 | {292E168B-A807-4BEB-8205-853DD377A6FA}
SAN RAFAEL 1109692576 | {324DF6E6-DDC1-4554-BC31-1F7629DC4812}
SAN RAFAEL 110991742 | {BFF521B9-A860-4F51-B554-94546E79EB8D}
SAN RAFAEL 1109CB | {B783060E-D866-4158-B26D-888D25122311}
SAN RAFAEL 1110189400 | {852F6C12-DBB5-4040-A2CA-B7AA0AE353A3}
SAN RAFAEL 1110854822 | {19311019-956D-4A95-87DB-92D336722225}
SAN RAMON 2101CB | {D5C8CF3A-0CA8-4CD2-870D-AC7D1B010386}
SAN RAMON 2102CB | {AFA2F3E5-5A6D-403E-A015-1BB8AB0D90BE}
SAN RAMON 2103MR279 | {EC3D5092-5EAD-44A6-A8B2-0227C409E453}
SAN RAMON 2106CB | {9140C526-29BF-4637-A62D-8BE823C11E2E}
SAN RAMON 2106MR285 | {BEA60D98-CFF5-4E7B-A41B-182A021D5BAE}
SAN RAMON 2107818336 | {772B9C3A-4112-4E6C-8E48-73C0CBC8A027}
SAN RAMON 2107824562 | {89815FEC-0F53-4C82-9066-992A709E730C}
SAN RAMON 2107CB | {772B9C3A-4112-4E6C-8E48-73C0CBC8A027}
SAN RAMON 2107MR284 | {1E4505DC-D80E-4F9F-A5C6-1B2DD1F7142B}
SAN RAMON 210853732 | {009FED72-F984-488A-870A-FBDD7926AC29}
SAN RAMON 2108CB | {B814E637-1BB9-4F04-B0A4-F99C92D5342E}
SAN RAMON 2108CB | {2A643A5D-A97F-4EE9-81CA-C352718D1D06}
SAN RAMON 2117CB | {C84D6789-7EC5-4B63-96CB-78D964DC0C39}
SAN RAMON 2119107418 | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
SAN RAMON 211995606 | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
SAN RAMON 2119CB | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
SAND CREEK 11037070 | {863BED83-C87B-4B95-B9B9-262F78012E12}
SAND CREEK 11037110 | {D40D6BB9-1863-4357-9803-EF56709C4086}
SAND CREEK 11037140 | {2D5FBF93-4F75-44A4-A3B6-356A65A990D3}
SAND CREEK 1103799118 | {7DAACA3F-4C0E-44A3-94C1-301E31E8EF8D}
SAND CREEK 1103818064 | {904E4C44-1C98-4593-BD77-E458AD2081ED}
SAND CREEK 110397354 | {1C32E9CE-3898-49FE-891B-A309867CC97B}
SAND CREEK 1103CB | {E54C0E82-949E-4C90-9607-A30CD2E7D9C4}
SANTA MARIA 1108M122 | {144012D8-3B80-4D17-BAEC-5B5A7515DDFE}
SANTA MARIA 1108M16 | {31A32213-8989-4C12-A58B-F9184AC14DCF}
SANTA MARIA 1108M18 | {516D977A-EB39-4268-8E04-4AF0198F88DB}
SANTA MARIA 1108M80 | {D0FCA825-EE19-45C5-82C2-01947841A1DF}
SANTA MARIA 1110M04 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
SANTA MARIA 1110M138 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
SANTA MARIA 1110M44 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
SANTA MARIA 1110M76 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
SANTA NELLA 110111370 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SANTA NELLA 11013680 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SANTA NELLA 1101594884 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SANTA NELLA 11017200 | {54EB001A-C75B-4E5F-A364-1EC2210A8870}
SANTA NELLA 1101CB | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SANTA NELLA 1101CUS8000 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SANTA NELLA 11037200 | {54EB001A-C75B-4E5F-A364-1EC2210A8870}
SANTA NELLA 11043130 | {D412B745-D070-4998-9104-DFC87BB22A4F}
SANTA NELLA 1104611232 | {9B89E5D4-E3CF-421E-9973-405ECEC9F5B3}
SANTA ROSA A 1104173590 | {BF693435-FC48-417F-BBCC-18F887A0E298}
SANTA ROSA A 1104210 | {53C74AF7-2A69-47CF-8DFD-9E70E0E39334}
SANTA ROSA A 1104220 | {E0B89CB3-82B2-49F5-867A-BBE81476E709}
SANTA ROSA A 1104220 | {97A379E6-C657-4B3B-9AC8-B4B0F3BA119F}
SANTA ROSA A 110432180 | {B37312AE-80D7-4090-A893-C81D3025336C}
SANTA ROSA A 110439786 | {697A1F90-C46B-4A32-BA8E-838CA80BD5D2}
SANTA ROSA A 1104642 | {DA22FBE8-4AE4-4189-B8A0-D6F473C1FE0F}
SANTA ROSA A 1104716 | {F8BEFC4B-3D6B-4BB7-B77D-7582CBA169BE}
SANTA ROSA A 1104782496 | {7956CC24-117F-4724-9582-2E87B368DA45}
SANTA ROSA A 1104782496 | {54C3FF00-D613-4ADF-B3B7-FDD938F310A8}
SANTA ROSA A 1104991788 | {A7207572-E958-47AE-A2AE-E5F117C7F1E9}
SANTA ROSA A 1104CB | {BAA473AF-66C6-4355-8E90-0CDB40A98A03}
SANTA ROSA A 1107CB | {66A6713B-EEF9-4672-883A-89D2D2628FA8}
SANTA ROSA A 1108626 | {B916F1BC-FDC7-4604-9F1E-064F6D66F284}
SANTA ROSA A 1108626 | {B3F22D98-1F2E-4E30-9576-F5EA667C1327}
SANTA ROSA A 1110184 | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
SANTA ROSA A 111095984 | {116DE352-2E18-465B-A34B-4DEAE4404EE5}
SANTA ROSA A 111098988 | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
SANTA ROSA A 1110CB | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
SANTA ROSA A 1111147198 | {67140A91-07CE-4EA7-9BA4-49867563AE33}
SANTA ROSA A 1111526 | {77B8D94F-2EC6-49F7-A5A0-3C2CCD32D5EE}
SANTA ROSA A 1111758024 | {FFCF3ECB-BCF6-4D7C-80BD-D22A2A7318FC}
SANTA ROSA A 111179354 | {77B8D94F-2EC6-49F7-A5A0-3C2CCD32D5EE}
SANTA ROSA A 1111907192 | {F22F662E-FA91-4A27-BD1D-488EE11D41A9}
SANTA ROSA A 1111907192 | {4A84F814-6F3F-408F-ABCF-98294BC9307C}
SANTA ROSA A 111199050 | {4D91C141-515F-4F14-8290-C8268E13D106}
SANTA ROSA A 1111CB | {4D91C141-515F-4F14-8290-C8268E13D106}
SANTA ROSA A 1111CB | {86D21844-80CB-4D82-9997-89E0A5ECE9C1}
SANTA TERESA 2101CB | {7514A62B-2474-4201-A784-F02F06FF897E}
SANTA YNEZ 1101277014 | {C3C0680A-C277-44D4-BC9F-C389F4D7DF4D}
SANTA YNEZ 1101673618 | {AB14F8FE-EE00-4DB6-A9D1-E7044AA1EEF8}
SANTA YNEZ 1101980192 | {CCDAB0AA-FC42-4576-8856-F9CCAB22AC0D}
SANTA YNEZ 1101CB | {08A02557-738F-41D7-89E3-E3805DA8D735}
SANTA YNEZ 1101Y52 | {CDC11A25-DBD9-42BE-AA95-70647385571E}
SANTA YNEZ 1102320270 | {5627B063-B665-4EAB-9B4A-39C8A753C0BC}
SANTA YNEZ 1102CB | {248D5525-98DB-494D-8A88-8F5511E7C8B0}
SANTA YNEZ 1102Y18 | {CB331419-4415-4607-87D8-B05BBD8C7F9E}
SANTA YNEZ 1104117616 | {C577CDCB-ED67-4302-B33F-D351377518F3}
SANTA YNEZ 1104512912 | {7679D85F-4172-4810-B5B5-B8198D816699}
SANTA YNEZ 1104564710 | {6D4FB307-8040-4939-9E2E-40C3CC67F06E}
SANTA YNEZ 1104685160 | {D82CFC78-0AF6-4ED3-B064-C26DDC2F5970}
SANTA YNEZ 110477098 | {30375F5B-5F9A-4C1C-992C-DEDED43F1FC3}
SANTA YNEZ 110488746 | {3F797584-019D-48E0-A377-BC3C335B4E76}
SANTA YNEZ 1104CB | {36F02C24-D26B-4B85-8C08-B8C39025E135}
SANTA YNEZ 1104Y04 | {1E768305-B6AF-4963-B2D5-92FDAB6A5028}
SANTA YNEZ 1104Y28 | {D5DD389C-0EE7-4085-B05C-70F106F6B79D}
SANTA YNEZ 1104Y30 | {1B8DB8B3-1D13-4E12-A58F-43F8C34F8820}
SANTA YNEZ 1104Y66 | {B46D742B-3DDA-4738-A51C-19ABAD3AA23C}
SARATOGA 1103LC16 | {D8FA53F1-4F5D-4A3B-A2ED-DEA75FD0EA10}
SARATOGA 1103LC40 | {9D2E9787-9F58-4CCA-BF31-59BAA6A88EA6}
SARATOGA 1103LC40 | {A0069F30-9735-482E-85CC-36443E960AEF}
SARATOGA 1103LC40 | {8C0E6ED7-7018-4183-AAD9-66702B134D45}
SARATOGA 1103LC82 | {8DC14E6C-EC17-4B68-AA1F-34B2D141CBFE}
SARATOGA 1104209146 | {08103A51-41C2-42FD-9E38-357AC9FA03F6}
SARATOGA 1105431214 | {BC196764-5ADD-4C81-A2B3-C9F42938CD96}
SARATOGA 1105CB | {0AC2A538-D1DE-4BF0-89DD-0FB685A31962}
SARATOGA 1105LC14 | {D8F111B1-64B9-41D7-9211-8173FEC05653}
SARATOGA 1106340986 | {76A04BD1-4382-473D-8157-2FE1C012AABD}
SARATOGA 1106408318 | {01EC17A2-1468-4F09-861E-AAA869333E5B}
SARATOGA 1106CB | {D3EE6D7F-47FA-4D89-A2C1-869E892A4C05}
SARATOGA 1107167792 | {E731F6BE-8220-43FF-B403-4FCE65138051}
SARATOGA 1107413816 | {717BE6DE-1A86-4939-B958-630A186C1AF4}
SARATOGA 11075696 | {01343684-2E22-4CD1-B45D-70EFDFE53735}
SARATOGA 1107667000 | {1C6BB5A9-7570-409D-B67F-8C01502A28E2}
SARATOGA 11076867 | {1EECCE5A-2560-4A1B-BCA1-BF5B03357FA1}
SARATOGA 1107899344 | {BBDA6BAB-A6E1-4EF2-A377-B93BB222DBB3}
SARATOGA 1107899344 | {56A63DE8-C9C4-4C32-8EDA-118B87F13D85}
SARATOGA 1107CB | {1EECCE5A-2560-4A1B-BCA1-BF5B03357FA1}
SARATOGA 1107LC26 | {AB3D61A8-2047-43B4-8648-838CA93AAC23}
SARATOGA 1115463510 | {D41C5049-957B-48AE-B573-6564E214A3B4}
SARATOGA 1115LC20 | {3FC7657A-E97F-4835-8F9A-E34BACD9F92C}
SAUSALITO 0401CB | {FA2ACC7B-DB5F-4398-838B-151CA038E350}
SAUSALITO 0402CB | {5AB6048B-BE9B-45DA-8B88-CE5B5004DC6C}
SAUSALITO 11011270 | {D140947F-0C1B-40AD-B2F0-4E3897A9B1FE}
SAUSALITO 1101221834 | {89972505-5E8F-4A2D-AA5C-D59B16608028}
SAUSALITO 1101331806 | {8796524B-A1FD-4229-B2E4-3A9BEDC52EE3}
SAUSALITO 1101688590 | {FB370B4C-A340-488C-B2BF-3C5B30E54274}
SAUSALITO 1101CB | {89972505-5E8F-4A2D-AA5C-D59B16608028}
SAUSALITO 11021224 | {BE77E89E-D575-4124-AA7C-BF07ADE3CD3D}
SAUSALITO 11021268 | {8F1701AB-AC20-48A5-8989-61140107D373}
SAUSALITO 11021500 | {7E93EFF6-2E9C-40C7-BE6F-763B6DBD01F0}
SAUSALITO 11022033 | {F71841C2-A9F6-40EF-B1D5-2F1AAA2168CF}
SAUSALITO 1102410 | {535449DD-A4B3-4AA9-AB71-3DA62C691B7C}
SAUSALITO 1102678 | {F71841C2-A9F6-40EF-B1D5-2F1AAA2168CF}
SAUSALITO 1102758798 | {535449DD-A4B3-4AA9-AB71-3DA62C691B7C}
SAUSALITO 110284278 | {EEE9A4DD-4FFF-4813-917D-2CD2DA44AB21}
SAUSALITO 1102964592 | {EE9BA2A3-B7F1-4ADE-BF30-423061F0C66F}
SEACLIFF 040112946 | {9DDD43C5-588F-4D1E-AFA3-8A122C419F83}
SEACLIFF 0401929132 | {CEB85E34-A4D1-44F2-A797-167211118BF1}
SEACLIFF 0401CB | {4EF4529F-4E08-426D-A25B-A1F6BCFED593}
SEACLIFF 0402558727 | {46C46D9E-FFCC-4964-94A9-7BEF756B6617}
SEACLIFF 0402CB | {F85FD245-E951-4FD5-89D8-9A5F2519071F}
SERRAMONTE 110412705 | {5AC2A44E-A5CE-4631-A5D0-59B8F85FCDA2}
SERRAMONTE 11046055 | {5AC2A44E-A5CE-4631-A5D0-59B8F85FCDA2}
SERRAMONTE 110467957 | {5AC2A44E-A5CE-4631-A5D0-59B8F85FCDA2}
SERRAMONTE 110496308 | {36480117-C14B-4376-B54A-91AA33F690DE}
SHADY GLEN 1101145584 | {1877CBCE-9492-4F47-B598-89710F79592C}
SHADY GLEN 11012768 | {7B6835CB-0292-4C0B-96D9-CB73CB830193}
SHADY GLEN 110132726 | {486AA3F8-488C-4B89-9A1D-60C9962E4FCD}
SHADY GLEN 110151696 | {0FE524F2-DA0B-43E6-AE33-7B106122C864}
SHADY GLEN 1101898212 | {29EB973A-BC17-445F-AED1-F026327BAFBC}
SHADY GLEN 1101941844 | {5B17B94F-37DF-478F-8F5E-F2EC95447F5B}
SHADY GLEN 1101941844 | {D1463BB4-C6D8-4652-B8D6-F5D55EAF695A}
SHADY GLEN 1101CB | {2295C6B5-DB5C-485B-935E-32BBB76DDD81}
SHADY GLEN 11022232 | {362CB776-12CD-4A6D-89F4-5301B9D37C1F}
SHADY GLEN 110248894 | {1F323A0D-3C08-4F07-A424-801F7C955EF5}
SHADY GLEN 1102743098 | {47A636B8-C05E-4F5D-AB59-245CAE44CE68}
SHADY GLEN 1102CB | {A8C871E9-A558-4EBE-96DF-EF0BB9E9DE44}
SHEPHERD 2111537008 | {E96DE61C-94D8-44EC-B1DA-8923104268C8}
SHEPHERD 2111707358 | {043E8F07-84F7-4AE7-BB3D-18F6172375EA}
SHINGLE SPRINGS 11038752 | {4A6A0D61-C41A-479C-A0D9-3D6225EB935A}
SHINGLE SPRINGS 1103CB | {21717BF3-E14B-476C-94A8-5495C36BA027}
SHINGLE SPRINGS 110419502 | {68D0B16F-430E-46D7-92D4-FB0EB0D57376}
SHINGLE SPRINGS 1104556218 | {38C837DF-F86F-4C34-B834-12EBAE0AE6ED}
SHINGLE SPRINGS 1104CB | {40341932-C636-415B-BE6F-5D9D8CD0A383}
SHINGLE SPRINGS 210511172 | {91D53CD4-6008-41E0-B5BC-B59F60B0DDAC}
SHINGLE SPRINGS 210519522 | {8C6D6A40-340A-49FE-9A00-F50F1736F18B}
SHINGLE SPRINGS 210551738 | {82A82E49-B7B9-4B20-91CE-19896367619D}
SHINGLE SPRINGS 2105CB | {F8F7136D-4B7B-4975-BCB7-4503BD4299E2}
SHINGLE SPRINGS 210819622 | {95880633-835C-41AD-A217-FF4EBDC70BBD}
SHINGLE SPRINGS 210819762 | {37338E68-AEEA-49C6-B1EE-76E1EAD86B81}
SHINGLE SPRINGS 2108294550 | {F31C2ABF-BD69-44A7-B0D2-5CCC3426ACD2}
SHINGLE SPRINGS 2108449638 | {2803490A-7633-47C3-B696-C54B5F6A03E3}
SHINGLE SPRINGS 210851474 | {D915D781-6781-4960-807E-BD1A4FE75E6E}
SHINGLE SPRINGS 210851476 | {E8E1663E-363E-4F96-A961-F91861C11573}
SHINGLE SPRINGS 2108CB | {31F15014-5008-45D5-9481-1A850055776D}
SHINGLE SPRINGS 210911092 | {AE69F8EF-4AC2-40EB-85B9-DBE37E3684F9}
SHINGLE SPRINGS 210912392 | {B7DD70D5-00B7-466E-B95D-1B12C82EB1E1}
SHINGLE SPRINGS 210913322 | {C2386B39-9DEB-4629-9750-D5EE983424AF}
SHINGLE SPRINGS 21092679 | {B7DD70D5-00B7-466E-B95D-1B12C82EB1E1}
SHINGLE SPRINGS 210935598 | {4BF4ABD1-69F5-49AA-B8C3-8117FD378308}
SHINGLE SPRINGS 210961892 | {FE625157-4A14-40D2-B1D3-1A0A93F86C88}
SHINGLE SPRINGS 210981390 | {DF428FBA-A19F-4678-A15D-08B87DAE1997}
SHINGLE SPRINGS 210985766 | {762F5F25-9174-4408-84A6-399ADE39F207}
SHINGLE SPRINGS 21099372 | {27097EEC-9CFC-4746-AAF9-881A597C47F0}
SHINGLE SPRINGS 2109CB | {8CA8A29D-825E-4F83-82F2-58C55E66E077}
SHINGLE SPRINGS 2110386572 | {FC00237C-3D62-4C01-88CF-5974E60BEBEE}
SHINGLE SPRINGS 211051790 | {189FDEE6-C0C8-4312-8E54-D1B717348AC0}
SHINGLE SPRINGS 211051800 | {027EA52B-9771-4584-AAFD-2CA838E196C2}
SHINGLE SPRINGS 21107742 | {3C509C6A-BB81-43C3-A023-21038DF3E84A}
SHINGLE SPRINGS 2110CB | {064C2459-8C22-4F74-A2C9-18905DBD3086}
SILVERADO 21022495 | {E417384C-CD10-4D00-B136-62F02EAF1C4A}
SILVERADO 2102285782 | {7650C201-F544-4286-9EA7-A492BFABD887}
SILVERADO 21023010 | {B8F94D37-4665-475E-83A6-71024C2C2EB0}
SILVERADO 210234959 | {03890B2D-86C2-4585-9C1D-5FAACC6CEB0E}
SILVERADO 2102437194 | {7001DE25-A96B-4176-B38D-AB056F29A6CA}
SILVERADO 210258626 | {05AC1C5B-D6E1-429E-A072-263D6E199803}
SILVERADO 2102636 | {163BDA39-807E-4AA9-AD15-91460635EEBA}
SILVERADO 2102714 | {65C50E41-4A19-4EF0-8E02-55AD7C68E0C7}
SILVERADO 2102772792 | {A1E340CE-2BA1-4C87-8C2A-156A4355C24F}
SILVERADO 2102808 | {F03C5A67-D53B-453A-A832-9C316BDAD400}
SILVERADO 2102922022 | {11969599-658C-4879-9EBE-BD3B4F21FB32}
SILVERADO 210298998 | {B9DFD3D4-5938-44FA-A6FD-F2608641C707}
SILVERADO 2102CB | {E417384C-CD10-4D00-B136-62F02EAF1C4A}
SILVERADO 2103403102 | {CFFB1C96-B030-4780-B25A-3AB8C753331F}
SILVERADO 2103507513 | {5DB6403E-B6A2-4C39-88E1-26D243AA9FAC}
SILVERADO 2103617828 | {F7F03C40-551D-4024-8031-59C5BBC7C6D4}
SILVERADO 2103920793 | {86671C53-A1BD-408B-B0CD-99AC0557F97B}
SILVERADO 2103CB | {66AAADD9-54A2-4D43-B82B-F401906AF14B}
SILVERADO 2104209359 | {BD4C596C-96B3-4100-88AD-27FF2E8D22A0}
SILVERADO 2104324994 | {7059E145-7DB1-4280-BEA3-DE79205E5125}
SILVERADO 2104324994 | {EFE5B889-8D89-4A64-9276-050798F3B9A5}
SILVERADO 2104324994 | {E948BFE3-2646-4701-991A-B5E0EF4D54D5}
SILVERADO 2104324994 | {52F85645-24BD-4BC9-86B1-206C2D8B3AF0}
SILVERADO 210437632 | {13A712E3-B547-41AB-8639-0CAD4756D0FC}
SILVERADO 2104515946 | {05AA93CC-3E16-4AA0-9C09-002C77C18466}
SILVERADO 2104632 | {841AD544-FFC0-4D92-904D-46B27F7D9430}
SILVERADO 2104633600 | {6697AFF9-8F2D-420E-9557-3177BC3896A0}
SILVERADO 2104646776 | {2B351D0D-34E9-4ED5-B9F6-58321332BC38}
SILVERADO 2104708 | {65E252BA-B6AF-41C8-8302-CDA75AAEE4FD}
SILVERADO 2104722 | {73D28043-CFDC-4F62-93B5-37CC33588BEA}
SILVERADO 210478268 | {49BFB9F2-5C6B-4B7C-8CFC-569E7EA29701}
SILVERADO 2104806 | {9C074E92-95C4-4617-9408-27935E560EC6}
SILVERADO 2104806500 | {301D5A5E-E790-4FFB-8489-CD78F4CA45CF}
SILVERADO 2104940 | {64400634-E6FB-4B73-87DB-F50EC6751223}
SILVERADO 2104CB | {BCC000F2-427B-4C85-BE86-EBEAE729A62B}
SILVERADO 21051306 | {C410A5EB-606F-456C-A426-9DF296A1E7C4}
SILVERADO 21051306 | {A2AE86BF-29D9-46AB-AC07-62E08E2FA633}
SILVERADO 21051308 | {E61E149E-984B-41E5-BBE8-57BFA4C46C56}
SILVERADO 2105131568 | {8DF4CE8D-8809-41EC-B891-BD4155C95E45}
SILVERADO 2105167360 | {0F3794E1-7800-452D-B826-F4E0E0581557}
SILVERADO 2105167360 | {C6357E73-88D5-4CF6-AB92-B3C80346E152}
SILVERADO 2105247660 | {99F7BEAE-C3B5-4D12-B703-F0449CE0ADD3}
SILVERADO 2105268508 | {AA30177A-A383-43BF-A978-435A7E84A10D}
SILVERADO 2105337226 | {0739C7E7-C007-4087-BADB-1D9A705F476F}
SILVERADO 2105359428 | {9FD052B0-6B15-4CAB-B530-047A5976AD91}
SILVERADO 2105394844 | {1CC6DAE7-1C84-4AF4-A013-6D8C6FB1596D}
SILVERADO 2105533226 | {4F585A0F-3E69-42C6-8427-3D94B7790006}
SILVERADO 2105658898 | {991CF770-C017-4F1E-B905-05B063249BE8}
SILVERADO 2105768606 | {095C5936-5504-4C4B-8302-1844A5C0B939}
SILVERADO 2105861266 | {AA30177A-A383-43BF-A978-435A7E84A10D}
SILVERADO 2105900104 | {6E66B86C-1327-427E-BBA9-5D2C3C6622A5}
SILVERADO 2105CB | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
SISQUOC 1101CB | {335463E4-7716-4BC6-BF55-B39E4654D44F}
SISQUOC 1101M96 | {ABA8F0B5-44C5-49D7-B132-C788FC15DD52}
SISQUOC 1102113874 | {92EB9460-E02A-4A24-A181-995BD1F9489E}
SISQUOC 110245261 | {B8793525-C43B-4B72-9E84-4F6812828DC2}
SISQUOC 1102CB | {92EB9460-E02A-4A24-A181-995BD1F9489E}
SISQUOC 1102M26 | {92EB9460-E02A-4A24-A181-995BD1F9489E}
SISQUOC 1102M52 | {B8793525-C43B-4B72-9E84-4F6812828DC2}
SISQUOC 1102M54 | {96906956-5C77-4774-B51C-564876632563}
SISQUOC 1103858898 | {258E8CE1-3F22-41A9-95CF-5107746239B3}
SISQUOC 1103867486 | {E782E12A-3164-4752-BB70-4CC8003C0253}
SISQUOC 1103M14 | {BE479CE6-8809-4A3B-A6FB-86A2FCDE06C2}
SISQUOC 1103M98 | {72D51786-0F19-4A21-BD91-493BA8FA331E}
SISQUOC 1104301229 | {4D6D6BF4-E19B-4629-9318-504AFE626164}
SISQUOC 1104675420 | {4D6D6BF4-E19B-4629-9318-504AFE626164}
SISQUOC 1104CB | {4D6D6BF4-E19B-4629-9318-504AFE626164}
SISQUOC 1104M58 | {4D6D6BF4-E19B-4629-9318-504AFE626164}
SMARTVILLE 1101CB | {90A2FAB3-9517-4F41-ABE9-643E537A58ED}
SMUD 15805CB | {87AE3F12-9778-4DE4-AC04-CB4537906F79}
SNEATH LANE 110134438 | {5A5EFB63-6847-4F33-8DBE-F9C3D6DCF54A}
SNEATH LANE 11015311 | {609F8931-DB33-4C51-8B0A-74D7E061F069}
SNEATH LANE 11016525 | {609F8931-DB33-4C51-8B0A-74D7E061F069}
SNEATH LANE 110168070 | {AE75174C-F0FD-4D78-8720-D705019718D7}
SNEATH LANE 1101CB | {E63B66A6-F711-492C-AE55-754D3FBB9FA4}
SNEATH LANE 110210255 | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
SNEATH LANE 110210287 | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
SNEATH LANE 110275844 | {AC57E8D0-E406-43BB-B0B4-92AB46A557F5}
SNEATH LANE 1102CB | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
SNEATH LANE 1103CB | {D862DEF1-5511-4286-A2B1-2632590ECCB0}
SNEATH LANE 110611792 | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
SNEATH LANE 11061339 | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
SNEATH LANE 1106CB | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
SNEATH LANE 11071277 | {8E15B458-F29C-4328-B8BB-225EB178302D}
SNEATH LANE 110715341 | {935F9503-A6EA-4581-B689-528244098488}
SNEATH LANE 110748338 | {83D7785E-7AE6-4CFF-B401-9FB72EBCD47F}
SNEATH LANE 110796530 | {387BB7F7-C1FA-403D-B1F2-AEFE2A510405}
SNEATH LANE 1107CB | {88158706-37CE-4050-9559-5A1E15835B03}
SO. CAL. EDISON #3 1101CB | {5456497F-E6D1-4A61-8929-89D313B5537F}
SO. CAL. EDISON #3 1101CB | {2930446B-6F6A-4AE7-9663-D1ACD14CCB1A}
SO. CAL. EDISON #3 1101CB | {A682EEBB-6AE6-4657-88BB-F6D984C7AC46}
SO. CAL. EDISON #3 1101CB | {FEFF3CD8-2343-48D8-93C4-6004850FEF87}
SO. CAL. EDISON #3 1101CB | {226F8C50-CE54-4E67-B9F5-B8A492EBF4DF}
SOBRANTE 110142914 | {D5713EAC-4361-483E-B20A-724A36C5F247}
SOBRANTE 1101934036 | {21AC5929-6E59-49F5-90AA-DFB268A45B54}
SOBRANTE 1101CB | {AC34AADC-41EC-4F75-A750-22A938BF80E6}
SOBRANTE 1101L534R | {25DCD8D9-03C2-4BC1-93F7-DF5BB3FCC448}
SOBRANTE 1102690098 | {2B19DC4F-7A35-4B7B-9AF2-F2CF56BFB136}
SOBRANTE 1102CB | {FAE87638-3327-4270-9C08-0DC3E3B13CC0}
SOBRANTE 1102L510R | {2F07459D-47C1-4462-B0ED-65839CB76ED4}
SOBRANTE 1103215046 | {6AFEB52D-9F4A-444E-B3FC-D10C077C8013}
SOBRANTE 11033342 | {4892CAAF-65E7-4660-A10F-F15BB35B52DD}
SOBRANTE 1103CB | {D5F18742-859C-45AE-BB95-2396135F0809}
SOBRANTE 1103LA401R | {6DF01F7D-D94B-4655-BAF6-B3A3B3F7FF40}
SOLEDAD 2101107872 | {13A55BCC-4738-480A-B6AB-19B8FE7F095B}
SOLEDAD 21017048 | {820718CC-7467-4DD2-B2F8-381F3D5B3CFD}
SOLEDAD 21017048 | {31A9BD2C-C5E0-444C-8986-49C4476C94B7}
SOLEDAD 2101775342 | {F417DA2A-C751-4206-9B93-7957CC7AB9E6}
SOLEDAD 2101823854 | {C9EB66D5-F17E-475C-84E3-A6D209341971}
SOLEDAD 2101955138 | {9A077527-882A-4F06-B221-C25746AA1F96}
SOLEDAD 2102304826 | {1DEF416A-A481-48CF-9FEF-A85EC33985E3}
SOLEDAD 21027008 | {7065F476-A653-46B8-B768-E4B58582997C}
SOLEDAD 2102858388 | {14F60B66-6FBD-423A-A8D4-1F6DF8B5B464}
SOLEDAD 210435306 | {B67EAAD0-18CE-4C8C-8264-33FF5297FE06}
SOLEDAD 2104413916 | {FD7651EF-898B-49C0-B621-C2068E1D4495}
SOLEDAD 2105125484 | {E0D1D31B-EE07-4A3C-BA17-91B209FA1390}
SOLEDAD 21053076 | {36177CF1-DF55-4FEE-893C-1AD0F53C4183}
SOLEDAD 2105315500 | {9FC0A9A6-641B-4A0C-A239-731EDA3A94A8}
SOLEDAD 21053720 | {1D34DC58-836D-4803-AFE9-57F78BAE9DE7}
SOLEDAD 2105404754 | {45F2F69A-4C2B-4AA3-A4EC-6985ACDF99C7}
SOLEDAD 2105526864 | {D2B3A3CD-1B80-46B9-AE2C-D2AC9CDB39D2}
SOLEDAD 21057056 | {36177CF1-DF55-4FEE-893C-1AD0F53C4183}
SONOMA 1102118 | {4BCD6EE2-7FEC-4152-907C-A38A16D3BF51}
SONOMA 110213367 | {2300EEC9-D815-4DFC-98C2-FB3F79503060}
SONOMA 1102441730 | {4F0353F4-993B-4228-9665-B8F36201BBD8}
SONOMA 1102CB | {2300EEC9-D815-4DFC-98C2-FB3F79503060}
SONOMA 11033052 | {4B7DC187-5EE3-45A7-A2F4-3F80A5EC9C80}
SONOMA 11033138 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
SONOMA 1103470636 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
SONOMA 1103849082 | {F69AA987-5730-4EE0-9E35-B096CCC08119}
SONOMA 1103880540 | {C15AE5B8-7C8B-4C0A-941A-BC50C59FC9B4}
SONOMA 1104412 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
SONOMA 1104414 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
SONOMA 11045661 | {9E74C19B-FD10-4380-8F7F-0DF0A358D1AB}
SONOMA 110478372 | {883C1192-DE93-49B0-9D61-992A9165A32C}
SONOMA 1104914376 | {9E74C19B-FD10-4380-8F7F-0DF0A358D1AB}
SONOMA 1105138 | {7B41A8E9-FC21-424B-BE2E-1E6F807F59E5}
SONOMA 1105229588 | {13B9141B-C5BC-4FB2-B1B5-84BF6E8CCF1E}
SONOMA 1105404 | {A0925B55-2E02-42A8-B141-C53A4CA4086F}
SONOMA 1105435024 | {2B737C15-F621-4E73-AF75-8131ECC2AA24}
SONOMA 11054456 | {4BB2B9D0-8D98-43BA-87AD-9BC7CE46F8C2}
SONOMA 1105539450 | {83741DC0-AB8A-4A6A-AF87-708226B87F58}
SONOMA 1105575872 | {D464C20D-2D07-4CD1-B506-ECBC5597DD8D}
SONOMA 11061678 | {80158D87-8FBA-4904-925F-F73ECFE1E50A}
SONOMA 1106296492 | {55EA2698-B693-4D7C-84A6-FBA73C981197}
SONOMA 1106376 | {3704160C-56F4-464C-949D-B0353C9BFECB}
SONOMA 1106510055 | {E5FD210F-062C-4CDB-BD2B-F92685B10DF5}
SONOMA 1106CB | {80158D87-8FBA-4904-925F-F73ECFE1E50A}
SONOMA 1107126 | {8F27A86E-670B-4331-ABF1-9BA9A6222879}
SONOMA 11071309 | {35F57AD2-0209-4C33-8C6F-331DBFF4518F}
SONOMA 1107294 | {35F57AD2-0209-4C33-8C6F-331DBFF4518F}
SONOMA 110749132 | {B66DFA6A-6131-4186-B4AB-0BA7B611120F}
SONOMA 1107606 | {8F27A86E-670B-4331-ABF1-9BA9A6222879}
SONOMA 1107844168 | {DFD9B477-AC78-4483-B663-8671DA768CEC}
SONOMA 1107CB | {B66DFA6A-6131-4186-B4AB-0BA7B611120F}
SPAULDING 1101578852 | {4B4ECB86-924B-4487-850F-9E73F5ADEBBF}
SPENCE 1101965598 | {E9D1075E-68D1-4D19-916B-47C6CD439F6E}
SPENCE 1102276712 | {4738DB4A-9FDF-4C6A-833D-7B9AB689B6AF}
SPENCE 1102321000 | {E93A7BD3-7283-4B37-990A-F7132697460F}
SPENCE 1102990464 | {E5160FAE-67B2-410A-AE3B-822157B58701}
SPENCE 1104965598 | {E9D1075E-68D1-4D19-916B-47C6CD439F6E}
SPRING GAP 170210720 | {A2735C5A-AC0C-48E2-9CB7-2F6A791B6D33}
SPRING GAP 1702188426 | {430BD33F-FEB4-414F-BF1F-8CCB997A468A}
SPRING GAP 1702693441 | {F823B297-BE7E-454D-B946-D904DF33E9F1}
SPRING GAP 170286032 | {17340C5D-4E9A-414F-A76B-922497EBB75D}
SPRING GAP 17029280 | {EF855D85-A8A9-46E0-809B-873120E44CEB}
SPRING GAP 17029690 | {06F65D45-2D82-470F-9B27-5D880652F1A1}
SPRING GAP 1702CB | {64CDB5CA-B54E-4043-BB09-802AFEE142DC}
STAFFORD 11011082 | {FF138367-96EF-4586-B73C-AE42FDD878F0}
STAFFORD 1101CB | {42AA63AD-C552-4EF9-BEF2-2D7A46307F74}
STAFFORD 11021048 | {B779C83B-3DC2-4512-9F97-360CB13A0909}
STAFFORD 11021202 | {07D78386-6A73-46DA-81CA-B20D2445579F}
STAFFORD 11021258 | {67620093-3D29-47F3-861E-D41DF7A61FA6}
STAFFORD 1102361952 | {58E1DDBF-27C2-479B-8E69-60E9501D29C8}
STAFFORD 1102524 | {890FBE04-45F2-477D-ABCA-3FF18127DAFA}
STAFFORD 11026121 | {890FBE04-45F2-477D-ABCA-3FF18127DAFA}
STAFFORD 1102784704 | {5DA8991F-2CE2-4FD2-84E6-8E0B8213A71A}
STAFFORD 1102CB | {C9CC8490-6E43-45D4-87C2-A85ACD7797AC}
STANISLAUS 17011331 | {34B1CFFF-1F43-44C3-AF15-E50BDC16F6A4}
STANISLAUS 17011812 | {34B1CFFF-1F43-44C3-AF15-E50BDC16F6A4}
STANISLAUS 17017144 | {EBD937A8-0F05-49AA-848E-8FB362E60B61}
STANISLAUS 170179826 | {2EBFCB83-8CD9-4937-9DF1-5F0721235A72}
STANISLAUS 1701CB | {918E0B8F-0C42-4226-8DC0-E78B4BED7E6D}
STANISLAUS 17021804 | {7A6C2092-3A26-4926-BE3F-3A04290F7325}
STANISLAUS 17021850 | {B87C881C-26C5-430F-BDD9-C06CB7701154}
STANISLAUS 17021888 | {63080617-6586-4F7A-B820-64DDE42B59AD}
STANISLAUS 170237276 | {C3619A95-0ECC-48A6-ABDA-B7A0B8AC9A76}
STANISLAUS 170237278 | {DBBC669E-53C3-46F8-B180-51E0DC203C00}
STANISLAUS 17024905 | {7A6C2092-3A26-4926-BE3F-3A04290F7325}
STANISLAUS 17026028 | {0ADE0ABE-2B1D-4CB6-BB2E-0E310321E755}
STANISLAUS 170275348 | {763723A0-FD03-42C3-9B8B-0F105886147F}
STANISLAUS 1702CB | {5ACF71BC-5CB9-4FB2-84D8-E7796B319ECF}
STANISLAUS 1702L3151 | {B87C881C-26C5-430F-BDD9-C06CB7701154}
STELLING 1108LM42 | {54B1742D-9454-4E0A-BDA8-E9A3850417C6}
STELLING 110913228 | {5E0E3DC2-02E2-401D-B8B6-13F779F80288}
STELLING 110913228 | {2F843716-F8D0-4F7B-9D4D-8575D36E9BFE}
STELLING 110913228 | {76970631-2436-4433-8ABE-AE41F160A6E0}
STELLING 110913228 | {02ACA21A-264E-42D3-A28D-4086D903C573}
STELLING 1109CB | {AA91D649-E1C5-491C-8F61-6E488119CD9F}
STELLING 1110396595 | {9194A519-A8B3-47FA-9F1B-13F504BA79E3}
STELLING 1110568350 | {D66F2372-56F2-4D8A-9310-F85A981AACD1}
STELLING 111060090 | {1AB7CEED-5C4C-4BB2-AA34-33FF777E7C4A}
STELLING 111060094 | {FAA8803D-2611-43AC-BDBE-E6661DD92FFB}
STELLING 1110733294 | {877E8EF7-F426-4EC0-9032-6E0C314907A6}
STELLING 1110881330 | {BB7AB05A-F6F1-4C97-8DCE-5C8338B638FC}
STELLING 11109265 | {D66F2372-56F2-4D8A-9310-F85A981AACD1}
STELLING 1110CB | {8E953D43-E75B-4D09-B2DE-0248B8D89E29}
STELLING 1110LL72 | {510ED089-9B5B-49AE-8C69-BD6EC85BCAAA}
STELLING 111160020 | {04E89A01-7DB9-4E29-BE3B-E16251E3C1EC}
STELLING 1111LM40 | {E9E9A7BE-6BF1-4820-BD71-A61CE1AF4848}
STILLWATER 11011320 | {7010B5A1-248E-4D8C-92BA-99C3D3CD7971}
STILLWATER 1101217504 | {59CCD17B-B63B-487B-90E6-A04047E8C25B}
STILLWATER 1101217504 | {969D0165-AB0E-4940-9C38-BF9AB022DA97}
STILLWATER 110148950 | {2473E4CF-72E3-4517-88B6-37E3090DCE92}
STILLWATER 1101747294 | {CCF6FF9B-457E-425D-A957-8AE034D58DB1}
STILLWATER 1101913434 | {FEFE500F-0532-4698-B2CB-49651843D0FF}
STILLWATER 1101CB | {05FAE411-CB1F-4ADD-9163-2A2B0A61C7F7}
STILLWATER 11021466 | {430AA5A2-7BC0-4425-A05E-76360F269642}
STILLWATER 11021644 | {2295AFD6-60F9-4656-92BA-00A16BCFB50A}
STILLWATER 110248952 | {096694C8-1954-4FED-B3CE-6072F54B2C4B}
STILLWATER 1102CB | {942A5D01-90B2-440A-92F6-C8D3C90D4346}
STONE CORRAL 1108001 | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 1108255186 | {0CA201EF-0A9B-4A84-97A7-EB95F1056EB9}
STONE CORRAL 11087100 | {7C3F27CE-B3FE-4A3A-A517-4F1EC2F3B587}
STONE CORRAL 11087310 | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 11087592F | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 11087759F | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 110878844 | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 1108CB | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 1110189488 | {DB3D7864-7F45-444C-BD96-835D23E12B3A}
STONE CORRAL 11107320 | {D090E99D-0335-45D1-8BE3-75B46FB44EC9}
STONE CORRAL 11107481F | {2BE56CEB-D130-4F64-98EE-3834ECE93155}
STONE CORRAL 111075288 | {2BE56CEB-D130-4F64-98EE-3834ECE93155}
STONE CORRAL 11107778F | {D090E99D-0335-45D1-8BE3-75B46FB44EC9}
STONE CORRAL 1110894956 | {28CCBA34-60FA-4FD7-81DE-39D9BA572A75}
STONE CORRAL 1110975698 | {475C3D60-9DB4-42CF-BD54-DCB20C6AF853}
STOREY 110921859 | {F6521ECD-18B4-4A6C-9FB9-B5018A20E90A}
STOREY 11095270 | {A7B17A78-9253-49C0-9DCD-46F08F0C14C3}
STOREY 11095580 | {F6521ECD-18B4-4A6C-9FB9-B5018A20E90A}
STOREY 11095680 | {4558735C-9506-4B45-82B0-A917961DD704}
SUMMIT 110147786 | {787994D9-582B-4D9D-9242-5F59A8A95135}
SUMMIT 110148632 | {E1505A10-613C-46C7-B0BB-34C322CF97E4}
SUMMIT 110148636 | {BC06A3DB-78BE-4381-AABB-ACBB02D3E9CD}
SUMMIT 11016627 | {E1505A10-613C-46C7-B0BB-34C322CF97E4}
SUMMIT 110168706 | {A427B0F7-F35D-4F9B-B915-6E1C81266A58}
SUMMIT 1101742 | {3E9B0952-44E2-4D0F-8A1E-44C0D690C0BA}
SUMMIT 110186658 | {2E3C216B-BFE5-488C-9EA5-E58CEF71CE83}
SUMMIT 1101CB | {CD142DCA-BFBC-491B-9C29-D02961854E56}
SUMMIT 11022302 | {4DAC7BB8-BA46-4649-99C3-6D0CB53CFA90}
SUMMIT 110249484 | {9B45EC1B-15DE-404E-A8B2-A4576946A1FC}
SUMMIT 110249484 | {4D17090F-B031-42D9-8E52-3D09021DC1AB}
SUMMIT 1102CB | {5BBF8789-23F7-470F-B0A3-CCE750BDABFE}
SUNOL 1101298061 | {BED88275-B880-467B-9628-7A276746EAD1}
SUNOL 110148180 | {4F589EB1-04B1-4740-ACAC-1766B4EEFC97}
SUNOL 1101605520 | {80474683-8128-4BE5-9DA4-10CEDF2ABB74}
SUNOL 1101904308 | {83D8DCCD-BCDE-421B-AFFC-11B0296CA2C4}
SUNOL 1101CB | {6830085F-FF28-4A85-9104-F5B6CFD24479}
SUNOL 1101MR169 | {61DFA90A-EDB2-455B-85E4-E1B3C2D31605}
SUNOL 1101MR297 | {144B98B4-D8D8-4444-BA16-D1CC613F7105}
SUNOL 1101MR387 | {475B4CFB-84F1-46E3-9FF3-409BD1FA54D8}
SUNOL 1101MR650 | {531B9791-D7B4-4DAF-8D61-5A68DAA7C3F6}
SWIFT 2102889948 | {B3225BC2-63D3-45D3-BA96-2AD2A0AB8E9E}
SWIFT 2102CB | {BE64DC1C-3443-4966-940E-5A564C032974}
SWIFT 2102XR440 | {BE64DC1C-3443-4966-940E-5A564C032974}
SWIFT 2107XR086 | {7CB97158-4C16-4CA5-9FF2-9C62CE30BD07}
SWIFT 2107XR526 | {F1466976-3470-44F4-BFAC-1A77DCF2CCD2}
SWIFT 2109XR300 | {17D989D5-D004-4CEC-9F17-89364403A1F1}
SWIFT 2109XR300 | {C1139140-8329-4FF9-96D1-1E3CB2E9BA54}
SWIFT 2109XR386 | {63AAF8AC-A447-481C-8FD7-216A552C90BD}
SWIFT 2110853720 | {24852CCC-5C31-4279-BF1F-19F7950A318A}
SWIFT 2110XR254 | {F246BE39-0175-4986-BDB0-A6E32868FF88}
SWIFT 2110XR332 | {DF04272D-0020-4DFE-BB56-C7BF45BF962F}
SWIFT 2110XR366 | {10854A52-7EF2-416D-830E-BF803A6482A0}
SYCAMORE CREEK 11092458 | {6DD04BFB-4C98-43A2-94E5-EF1AAF874533}
SYCAMORE CREEK 110979474 | {BEF311A1-A486-4265-8EB8-C5A6755295FB}
SYCAMORE CREEK 1109CB | {6DD04BFB-4C98-43A2-94E5-EF1AAF874533}
SYCAMORE CREEK 1111153260 | {39E14DE7-CA2E-4F61-9B12-2EF706A95B5E}
SYCAMORE CREEK 11112014 | {9FD8CC5B-B764-4FC0-90D0-B9293DA570EE}
SYCAMORE CREEK 11112268 | {BCBFDCD7-6D09-427B-8565-FE77C2D532E0}
SYCAMORE CREEK 11112544 | {D9A2A699-962C-4607-98AB-EA01299FAAB8}
SYCAMORE CREEK 11112602 | {5CDF71A4-CDCE-4614-B4AE-BACB8DC21516}
SYCAMORE CREEK 1111391406 | {A8EC7410-EC51-486D-9825-5F0C3E2E088F}
SYCAMORE CREEK 1111579750 | {999F5F71-1BDE-4099-9D8F-A77D79948BD8}
SYCAMORE CREEK 1111976428 | {78341850-739C-48F1-B508-024DE20CD1AD}
SYCAMORE CREEK 1111CB | {D9A2A699-962C-4607-98AB-EA01299FAAB8}
TAMARACK 1101291312 | {FEB92E46-4E4F-4CB9-B4AA-257412799ABB}
TAMARACK 1101CB | {1755A18B-6E24-4507-ACE5-9CCC118C7159}
TAMARACK 1102482896 | {FB391052-56E6-4289-94C4-964DB7340649}
TAMARACK 1102CB | {A8FAA54E-764C-43E1-B056-AE15ABB7C1D1}
TAR FLAT 0401922858 | {D165BF4B-3C2E-48AE-BC41-B95BCB317ED4}
TAR FLAT 0401CB | {EA023699-472E-4198-908E-801A3A6750F5}
TAR FLAT 04023144 | {C73A5D7F-692C-413A-8D72-DC21C7152C9F}
TAR FLAT 0402327672 | {A02A5B52-889C-4954-A0B9-9F5E9723A680}
TAR FLAT 0402CB | {15F62F46-8DEB-4CCA-80E4-1A07793D2B95}
TASSAJARA 21032705 | {C740351C-623B-4A79-8F81-B59FA4E58E72}
TASSAJARA 2103883664 | {84C3B577-3EBE-4F9C-94B3-B891086264A0}
TASSAJARA 2103883664 | {63B2FCDD-700B-4526-B8EA-5613D1DDBB60}
TASSAJARA 2103CB | {2ACF67F1-3B06-40EC-A04A-B6A9C336FB36}
TASSAJARA 2103CB | {C740351C-623B-4A79-8F81-B59FA4E58E72}
TASSAJARA 2104CB | {8DD57FAC-0D20-4DE3-898A-E73074144CC8}
TASSAJARA 2104CB | {B05D8AC6-2B7C-4E68-B328-BD625ED75426}
TASSAJARA 2106203380 | {C6A4A4CF-A03A-49E5-B0DC-3DB8EE99EA58}
TASSAJARA 2106CB | {0F972632-618F-44CB-A965-3BB4F6195935}
TASSAJARA 210791094 | {9BFCBF13-2D3A-4A17-97C5-BD97C03AE6D0}
TASSAJARA 2107CB | {9B0F8112-6AAA-47D5-A7C6-B8C0314DE7DA}
TASSAJARA 210812712 | {99848A3D-3AE5-4D01-A9C7-8BD9676BEFEE}
TASSAJARA 2108189700 | {8C428159-8CA3-458B-A6CE-F60FA4399D97}
TASSAJARA 210875010 | {FFB03A86-39E6-48B0-9234-84638A1DF85F}
TASSAJARA 210883368 | {F3272220-83F6-47EF-AA10-7270133DA2ED}
TASSAJARA 2108954811 | {F949AA4B-CECE-442A-AA8D-703A33BB749B}
TASSAJARA 2108CB | {7E453EBB-15B5-4455-9C0F-35AB481A3035}
TASSAJARA 2108D520R | {D91BF138-6798-4927-88BC-C1A382D4C37D}
TASSAJARA 2109CB | {E1A9F699-2041-4569-A9A7-03860994D8BC}
TASSAJARA 21123202 | {FFB25F94-DDAE-4CA7-A7FA-E0E40AD2E7D0}
TASSAJARA 2112676362 | {F9AD6B4B-3819-4B81-9BE7-73908ECEFCE0}
TASSAJARA 2112791386 | {0D1DD5D5-DD54-49CD-8DC6-C13ECFED047D}
TASSAJARA 2112900058 | {3F5B520C-846B-41F0-9E96-CA50F3A940DB}
TASSAJARA 2112CB | {4D869EED-AD00-4E5D-B02B-0CB786403D3A}
TASSAJARA 2112D514R | {3FFF1795-1315-4A71-8E91-178B9A0CCDE5}
TASSAJARA 2112D569R | {182E7891-748D-4B1C-AB5C-2655C693C420}
TASSAJARA 2113MR276 | {3C13801D-CC64-4F61-AF69-C39F394BB25E}
TASSAJARA 2113MR280 | {B9D0F1F0-F20F-489B-8E21-22409D603A4D}
TEJON 11022455 | {A9055457-4647-4903-9845-7B35001BBD43}
TEJON 11023751 | {F982DA9B-E6B3-4123-BDDF-635E01BF398E}
TEJON 11023760 | {6C424A0E-18F6-4E95-BDD7-E63E2F8C4F83}
TEJON 11024525 | {58DF11D2-6D0E-4BD8-9469-17767B55297B}
TEJON 1102732836 | {A9055457-4647-4903-9845-7B35001BBD43}
TEJON 1102CB | {FFCCB51D-8ABA-4A3C-849A-11EC19C62E8E}
TEJON 1103145334 | {13DF9C76-E2F4-4659-999F-3B0C5114903E}
TEJON 1103286542 | {E47780AD-DBC7-46C5-8517-B5A92A1EF564}
TEMBLOR 11041034 | {C2992F46-2554-463F-8E87-219C3C230B9E}
TEMBLOR 110414233 | {99CF017F-6ED0-462F-8AD1-7CD56A44DE93}
TEMBLOR 11043013 | {99CF017F-6ED0-462F-8AD1-7CD56A44DE93}
TEMBLOR 110437694 | {29FDF678-E116-4F18-93AB-072742A94198}
TEMBLOR 110459326 | {29FDF678-E116-4F18-93AB-072742A94198}
TEMBLOR 11049126 | {C2992F46-2554-463F-8E87-219C3C230B9E}
TEMBLOR 1104CB | {C2992F46-2554-463F-8E87-219C3C230B9E}
TEMPLETON 2108A64 | {FFDFCD62-3D83-4DB1-8291-20A4384347C8}
TEMPLETON 2108CB | {3F210877-7C55-4139-88CB-B237BD20F584}
TEMPLETON 2109313404 | {3A9A14B5-4831-413C-90EB-22B1436113DC}
TEMPLETON 2109CB | {3D2DC8C9-F0E2-4189-8946-5553A87031B9}
TEMPLETON 2109P32 | {BE3D916E-88E2-482C-892F-AF61F2F67735}
TEMPLETON 2109P60 | {B41EAAD7-8D6D-4395-8298-54FCF68764D6}
TEMPLETON 2109P68 | {DD7BFBA2-59F2-4AF7-93E5-DA92AEFE3901}
TEMPLETON 2109R34 | {D690C4D2-AB5F-4E55-BE78-1BFC0A0158F8}
TEMPLETON 2109R50 | {E9F4AFB5-1012-46CB-93BD-65999630DF83}
TEMPLETON 2109R52 | {881400C0-59DE-4789-9E3A-A9795EA7ADF7}
TEMPLETON 2109R74 | {6A908DD9-6B72-4423-AA27-E74CEDA485AB}
TEMPLETON 2109R78 | {23FDF1DB-782E-4000-92DD-5A064AF483AC}
TEMPLETON 2109R92 | {03B90DE8-00D2-4B58-B65C-ED90C57EE070}
TEMPLETON 2110211842 | {816EE1E7-10CB-4545-BFF4-506903516309}
TEMPLETON 2110307832 | {EAF87279-EF23-4A44-B5E2-CCA62D5C53AA}
TEMPLETON 2110317796 | {F014BBB3-CA2E-47B6-9852-740165FD3020}
TEMPLETON 2110901690 | {C383B6E8-D569-48F8-A225-7445F785217A}
TEMPLETON 2110941946 | {BC8B43E1-B72C-41FC-BFAC-30FCC8E9DB81}
TEMPLETON 2110CB | {43D83959-6253-49E9-BD6A-065B7EF0ABAF}
TEMPLETON 2110N30 | {F8FF5E67-EE4D-44BA-B232-2D0879C01CDF}
TEMPLETON 2110N32 | {33400389-0E2B-42A8-BC66-48CCE49F1F75}
TEMPLETON 2110R02 | {49CA67C6-8C55-4D93-BC3A-D344A8E723E1}
TEMPLETON 2110R06 | {29732AB3-8644-4D02-B399-63E828AF790C}
TEMPLETON 2110R90 | {F2DB4641-1C59-4A03-8B1A-285CBA9763E2}
TEMPLETON 2110R94 | {C64A1C77-F715-47FB-B91C-102C85AEBD60}
TEMPLETON 2111514592 | {E68CFE85-A05C-455F-90E9-908250F636D6}
TEMPLETON 2111A66 | {CD2443C5-9F0F-40FA-9737-DB91D76D5878}
TEMPLETON 2111CB | {1A1B9828-BB7B-4831-9B29-12F7B7720C90}
TEMPLETON 2111R76 | {E068C598-6807-40BC-B63F-804DC57F436F}
TEMPLETON 2111R86 | {C1DF3268-8D83-469E-AB38-F1D09D72570E}
TEMPLETON 2111R86 | {0CBBEFB6-9229-4A1C-A848-15AD84ED6B51}
TEMPLETON 2112116402 | {3329F03A-165F-42EE-9423-F38D6F793EB9}
TEMPLETON 2112238418 | {C5F748E0-B9D3-42AF-ADB5-0714F403D060}
TEMPLETON 2112485608 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
TEMPLETON 2112CB | {5E55D6F2-0179-4A06-BFE4-E717E82210A3}
TEMPLETON 2112R28 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
TEMPLETON 2112R80 | {3E696401-4261-4D08-869B-B3D4019E7D36}
TEMPLETON 2113175566 | {570CCEFD-E2D9-4041-AF4C-E6667A3EAF28}
TEMPLETON 2113205874 | {6DAFE91D-9A97-407E-B8BF-0F2EE33C22FB}
TEMPLETON 21132949 | {7937BCC6-E91C-41D5-AE9E-FB212F98DDB6}
TEMPLETON 2113587564 | {0AF55F6B-6D61-4EC5-ACAE-2DB5E6CBA844}
TEMPLETON 2113641367 | {FE304B9F-DFAE-423B-9FF6-FD34CCDB383B}
TEMPLETON 2113848137 | {FB380A98-AA0D-4842-98E9-EA318AC8BB0D}
TEMPLETON 2113A08 | {ED2FD62D-73A2-48E2-BABA-F5CBA9685A6D}
TEMPLETON 2113A10 | {E6F3FB48-7B73-44A2-9D22-75A3F05024E8}
TEMPLETON 2113A12 | {F518F823-D39A-4E63-8BF7-DA50E4754F15}
TEMPLETON 2113A20 | {63FF5E85-7320-4916-95DB-09A821D7A9F8}
TEMPLETON 2113A24 | {F76D7225-917A-402F-BB98-F7057EA3149E}
TEMPLETON 2113A30 | {982A8403-6DD7-4479-B96A-84BF654A0654}
TEMPLETON 2113A32 | {B5262924-E8BA-494C-94F2-552AF4F4F88E}
TEMPLETON 2113A70 | {7937BCC6-E91C-41D5-AE9E-FB212F98DDB6}
TEMPLETON 2113CB | {DD694EAA-A9BC-4C03-B675-60DCE9DF4147}
TEMPLETON 2113R82 | {F7BD212B-7F44-4A16-B423-2BCFB7829D6C}
TEMPORARY CARBONA 110145186 | {D5A2A0ED-5854-48FF-9353-DEF3C343CB3C}
TIDEWATER 2104226374 | {19823827-C5EA-4E2D-9FF7-7BB963BC816B}
TIDEWATER 210447828 | {19823827-C5EA-4E2D-9FF7-7BB963BC816B}
TIDEWATER 210487978 | {F47CA250-FEC5-4A9D-A7B7-CD6372963F55}
TIDEWATER 2104CB | {F47CA250-FEC5-4A9D-A7B7-CD6372963F55}
TIDEWATER 210614072 | {A74482B6-4F98-4489-A417-0B9C2832ACBF}
TIDEWATER 210618972 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
TIDEWATER 210618982 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
TIDEWATER 210638108 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
TIDEWATER 210638866 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
TIDEWATER 210657926 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
TIDEWATER 210665866 | {2CBEB58E-8C6C-48A4-AF77-398D7460FE13}
TIDEWATER 210665866 | {BE753D24-8AD5-497B-932F-CCEA608A77CC}
TIDEWATER 2106703654 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
TIDEWATER 210695842 | {DECD64D5-E92D-44EE-BF28-1EF0D6E10478}
TIDEWATER 2106C514R | {8FCD9F0C-12A9-46C8-B7B1-BF847BD03786}
TIGER CREEK 0201320746 | {C7F675D5-2B2A-49BD-AF13-9888C7E4FCA2}
TIGER CREEK 0201CB | {42CE80CD-1575-4D75-9DA9-13CC191BD6F8}
TIVY VALLEY 11067150 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIVY VALLEY 11067210 | {D8E13D73-EB68-4157-8FED-21C11BDD3D42}
TIVY VALLEY 1106CB | {36113653-5563-4401-879E-ECEBC9923AFA}
TIVY VALLEY 1106D8492 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIVY VALLEY 1106R1450 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIVY VALLEY 1107248306 | {BE7D1774-079A-4F76-A335-3394843B4D82}
TIVY VALLEY 110737522 | {DA50CC20-DF93-4A26-9942-3A43E97DCAC4}
TIVY VALLEY 1107584840 | {69DA4F1C-E07E-4189-8040-902C89E5A469}
TIVY VALLEY 1107599142 | {B0EAA688-0840-4FBA-BE74-3B15BA6BD7F3}
TIVY VALLEY 11077380 | {755777FC-6215-430E-868E-B21D92A14A1A}
TIVY VALLEY 1107822606 | {8C528F18-9D07-401C-90F8-07B202001D80}
TIVY VALLEY 1107822606 | {2CCB588B-990A-4DA3-9CC6-802905504EF9}
TIVY VALLEY 1107869946 | {8685FED6-DA63-4202-8ADA-3D58BFE83B0E}
TIVY VALLEY 1107CB | {B007F88B-9403-4642-A8D2-16BDDDACB785}
TOKAY 1101CB | {11EDF2B5-A0C5-48FD-9A56-5F2C5A063907}
TRES PINOS 1111203126 | {899DF856-B7D3-491D-B16E-756ACF7692DC}
TRES PINOS 11114032 | {BD94B291-9C0B-4C28-8C7B-50F4F86D7051}
TRES PINOS 11114064 | {68C1BEAC-9E07-4A35-9BA1-6FC5E18C5BE8}
TRES PINOS 1111CB | {81D7ACD1-11AF-45F6-91F4-8D9CD5CC46FD}
TRIDAM POWERHOUSE 2101CB | {A0F1DBF1-292A-454C-A5DF-A955BFE4DEBB}
TRINIDAD 1102314118 | {8F30516F-9B17-41F9-982D-7C654517E070}
TRINIDAD 110233936 | {8F30516F-9B17-41F9-982D-7C654517E070}
TRINIDAD 110246990 | {8F30516F-9B17-41F9-982D-7C654517E070}
TULARE LAKE 1104884818 | {639991A8-D9DB-4B2A-B168-DB2687AE8157}
TULARE LAKE 110854074 | {56DB22B5-CE56-48B6-8FE4-9109734E0A42}
TULARE LAKE 110876864 | {7219D019-06C4-402F-BD2E-8145F907D9F0}
TULE POWER HOUSE 1101CB | {35723AC1-565E-4787-875F-B05907FDAE4F}
TULUCAY 1101137224 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TULUCAY 11012280 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TULUCAY 1101323426 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TULUCAY 1101504524 | {4EA48B47-47EA-4694-BDCC-7065AA75E603}
TULUCAY 1101613014 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TULUCAY 1101628 | {E6EA8FFD-93FC-4EE2-B4B3-05C67BB86274}
TULUCAY 1101628 | {8F24D563-8C81-416A-9085-5DC65E76E490}
TULUCAY 1101684 | {5DBAA811-6F22-4836-935F-F9F50494B3FC}
TULUCAY 1101926496 | {5DBAA811-6F22-4836-935F-F9F50494B3FC}
TULUCAY 11019999 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TULUCAY 1101CB | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TYLER 11041522 | {0D1643DB-604E-4FBB-B45F-DBA97992B887}
TYLER 11051536 | {8FC5AABE-9067-41E2-B562-CCB95292040F}
TYLER 11051704 | {E58E84BF-2C2E-494E-AE66-0D141BD137C3}
TYLER 1105503690 | {99B508DB-4544-4193-87F9-B11616D1BA85}
TYLER 1105CB | {AAAE8701-80F0-46AE-8702-4013E06C972E}
UKIAH 1111379946 | {405F1015-C662-4950-99EE-1E4A689283D9}
UKIAH 1111422886 | {93D393BB-7553-4CDF-A3C5-3EDDACF2D482}
UKIAH 1111433984 | {90D9EBEA-E8B3-45BF-93FF-595A29473B29}
UKIAH 1111477890 | {C19836E9-D34E-4A81-923F-AE30E5CB731B}
UKIAH 1111789282 | {0679194D-94A5-4BEE-A3BC-BCA5B0434E05}
UKIAH 1111807988 | {183B4AB8-E049-4175-AED7-96F466044CA0}
UKIAH 1111CB | {FBA231AA-2A4C-4C3A-9CF9-4FC7651694D6}
UKIAH 1113548420 | {CD90789A-8C40-4BA6-B727-13DE18B4CBFD}
UKIAH 1113691436 | {6C8F23E8-D864-4646-ABCC-F348028A767E}
UKIAH 1113968652 | {81BDBB43-850C-4250-9194-B1A69ADA9BF8}
UKIAH 1113CB | {056DA4FC-3963-4A38-A47D-C0DB965F519F}
UKIAH 1113CB | {57AE83F3-7C35-4A08-BEA4-B10AAC4F4015}
UKIAH 1114206824 | {47F1875F-3F15-4519-A49C-1F4ECD7BF06F}
UKIAH 1114408 | {51D9F3E7-D9FC-4F6D-B9B5-400B76D74D25}
UKIAH 1114528 | {7CFF91C6-6122-459F-BD71-B9F17BE39EB0}
UKIAH 1114544 | {4F4D60A8-18DF-4AD7-9533-2FDA5C5224B4}
UKIAH 111472990 | {7D69F374-F9B0-4F64-806B-E0305A606677}
UKIAH 1114822 | {2D9FE14A-68D2-46A5-B4CD-1EF83FC0FBCE}
UKIAH 1114844294 | {E31B357F-7D66-4467-A543-DD5E914AB51D}
UKIAH 1114943840 | {F0BB0AAE-662A-48EA-9E79-24EA77E16FE7}
UKIAH 1114CB | {D98BCE06-B639-4635-9566-7FA7CFE5BC8F}
UKIAH 11151216 | {190ED11E-6BBE-4AB9-A430-D568E91970DF}
UKIAH 1115168892 | {E7C123E6-BA30-4506-A3E6-3FDF5CDF33DB}
UKIAH 1115534 | {CD599840-F925-4A8F-AC72-601D0F3A1898}
UKIAH 1115899594 | {3FF9A88F-E2C0-476A-97B0-2B726DE9CB26}
UKIAH 1115CB | {A99474C6-C1F9-4A19-8465-2D8ED25CEFB7}
UPPER LAKE 1101412 | {01C247AE-0349-4567-B4A6-340BCCA2F303}
UPPER LAKE 1101412 | {CEA08BFB-7016-4016-B5B7-B9CA2EAF8E9F}
UPPER LAKE 110142378 | {B4FEFEF6-4949-40A0-B2AB-64F4BB223B69}
UPPER LAKE 1101452 | {B4FEFEF6-4949-40A0-B2AB-64F4BB223B69}
UPPER LAKE 1101472084 | {9554D214-C3FE-4BE7-9CCD-F966D634C113}
UPPER LAKE 1101660 | {0F0F521B-1DED-434B-B495-1C9D87139123}
UPPER LAKE 110175370 | {5002339C-3B44-461E-A16D-6DB263D4D731}
UPPER LAKE 1101861806 | {911C4C68-2E5A-42A2-8C57-88BC3B5D0196}
UPPER LAKE 1101CB | {6A48DD4C-8096-4848-9316-CAF03427E24D}
VACA DIXON 1101139898 | {AE7E6891-05E6-46B9-AC20-6D7C3DA9F6B6}
VACA DIXON 110118292 | {C14F8C7D-2418-4308-A5BD-32845AC90D2E}
VACA DIXON 1101392848 | {3BE6396D-6D17-4036-BB25-F9592AB5B612}
VACA DIXON 1101454328 | {9837C0F6-0F2F-4E27-A1F9-23B2A5A0AE60}
VACA DIXON 1101604552 | {24619094-D4BA-4F34-8E61-5CF30DBB0C99}
VACA DIXON 1101628308 | {EF20F4FD-42A6-47E6-BDFD-6030249E700E}
VACA DIXON 1105965390 | {DF536E94-F9F9-48D4-A625-EBCDF4893D0B}
VACA DIXON 11059792 | {30E4D883-8616-4202-B2EA-1D70554D1ADA}
VACA DIXON 11059792 | {E29DDFD8-87C7-4111-AD68-0CCC26FD3BAF}
VACAVILLE 1103CB | {404CB668-CECA-42E3-95F0-FB6161DA4FDC}
VACAVILLE 1104196294 | {52D876F7-4D74-4BF0-9E35-C5DD910689A2}
VACAVILLE 1104293462 | {6E87673B-0332-4D64-B876-B31C65A7FB01}
VACAVILLE 11046542 | {82F07A4A-6ADB-4C33-B8E8-182597EEA877}
VACAVILLE 1104CB | {CBB1E17F-BE5D-42E9-AB86-48D61CF7F4ED}
VACAVILLE 1104CB | {7D640C16-1A66-477D-BE47-5556BC09F802}
VACAVILLE 110838316 | {E6AEA11E-7550-4515-89AF-4FC9B6C0C260}
VACAVILLE 110838316 | {05D49B9F-74A5-4524-8EF5-6986AE7D334D}
VACAVILLE 1108873678 | {21E07584-F130-4C43-95FC-B64A0DEA91EB}
VACAVILLE 11088762 | {ADB960B7-1B6C-413D-B1F8-E0FB7A88FA0F}
VACAVILLE 1108922767 | {BAE6CC17-1005-410C-815D-1B7C2B8B4161}
VACAVILLE 1108CB | {59386278-9020-4BB7-BD46-9280C84FE5FF}
VACAVILLE 110941782 | {D12E3D2F-1998-4DA6-942A-7BE316909F83}
VACAVILLE 1109592742 | {695B9A66-1C5D-4614-8CBB-D52A4B4D47A7}
VACAVILLE 111112342 | {3A0CCFE3-C12C-4384-B593-6A5D6B4AD5AF}
VACAVILLE 111113652 | {A457A03A-C6E6-47D1-86AC-AE763850EDD5}
VACAVILLE 1111772224 | {7CDC7EE7-6A7B-4AD7-84A2-1F7D5EB3BFDB}
VACAVILLE 1111CB | {1F08C74E-1D18-453D-9F09-2E91ADE9AFB1}
VACAVILLE 1112239276 | {D860A6A4-4492-4A71-A749-BCD6B53CBA01}
VACAVILLE 1112354578 | {6407F04E-6CB0-4F44-9E99-762FC3F45056}
VACAVILLE 1112CB | {5828CFD8-0F34-469A-AB4B-4395B45CE3D2}
VALLEY HOME 17031532 | {F0B34ED0-42FC-4061-AC8E-1112027FAE68}
VALLEY HOME 17031558 | {1005EDC8-1357-436D-879A-4415102F0FE3}
VALLEY HOME 170339660 | {A2F287EF-C287-4618-B3E6-557974E96CE4}
Valley Springs 110111158 | {441CFEC9-1CA0-48DF-94A7-C868FF359EA8}
Valley Springs 1101207256 | {744E490C-4B9D-43E3-89F3-EC14E8D89F45}
Valley Springs 1101CB | {657DBFAC-1DEB-4C8D-A356-BB20B766D324}
VALLEY VIEW 1103218424 | {0AF2BCCE-C158-41A1-A8FA-127B4D2028A8}
VALLEY VIEW 1103CB | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
VALLEY VIEW 1103P156 | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
VALLEY VIEW 1103P158 | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
VALLEY VIEW 1103P160 | {2371EFC2-B46C-4698-931C-537DFFB0D5A5}
VALLEY VIEW 1105305072 | {A9274254-950F-4772-BD6F-0C6FB4FEF4A4}
VALLEY VIEW 1105CB | {7F8D329C-2906-4CB9-89A6-48A9455878D0}
VALLEY VIEW 1105P124 | {D661A4C9-F1EC-4DA6-BD47-BB819E0F490C}
VALLEY VIEW 1105P126 | {1A179874-1BC4-4379-BC93-DB3AE752926F}
VALLEY VIEW 1105P190 | {75634943-F60A-4935-9A1D-02ADD9591487}
VALLEY VIEW 1106496670 | {772F24AF-7DA1-47C8-B6AE-4C4810E9D260}
VALLEY VIEW 1106865650 | {B79581BD-E589-4E72-A7CE-26316DC5699E}
VALLEY VIEW 1106CB | {D9DED303-0FA6-4611-A466-91E33B741947}
VALLEY VIEW 1106P128 | {30491B06-175D-4B50-9477-0E42FFDBA4F5}
VALLEY VIEW 1106P166 | {064EA0EC-DFDE-4FA8-8393-49958A6F3357}
VALLEY VIEW 1106P176 | {1A50D894-CA6E-4856-B84F-5DA7159938A7}
VALLEY VIEW 1106P176 | {B787A327-E708-4D5C-865B-C65998470D53}
VALLEY VIEW 1106P180 | {27893E9C-0A5B-4290-96D8-63CEC0636192}
VALLEY VIEW 1106P182 | {772F24AF-7DA1-47C8-B6AE-4C4810E9D260}
VASCO 1102208712 | {A9FBDDA8-24C2-4BE2-8132-60998883919B}
VASCO 1102546328 | {940E4DBA-804F-4033-AFB1-1900E1E5DF1D}
VASCO 1102886522 | {4653D811-6732-4F47-994C-B6C9ADAB66CF}
VASCO 1102MR178 | {C757B1E5-E864-41C5-8F1F-450BE13C3852}
VASCO 1103964102 | {DA001B7B-04D4-4B91-80D8-0CD4D55EE955}
VASCO 1103CB | {D777EA4E-3A7C-4425-B34B-DA242E9EFE4C}
VIEJO 22012064 | {410C255F-3E61-44D1-A47D-CA8172B6BCA6}
VIEJO 2201563516 | {DE1EEE83-8C6C-447F-B024-0ED2E3DD3250}
VIEJO 22019490 | {D5629837-45B4-4B33-A660-AFDD9F409AB3}
VIEJO 22019698 | {7C0AA1F8-3024-4D35-BAB8-1475B467A597}
VIEJO 22019704 | {49931849-9CA4-43E6-B559-5E2CB6D2E2B4}
VIEJO 2201CB | {11A2851C-72B1-4A62-98D6-D6E2FFA710C1}
VIEJO 22022014 | {8E85DA31-E8CD-4D80-BE55-60AFA6937F74}
VIEJO 22022179 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
VIEJO 22022606 | {DA30E872-22F6-4600-80CD-C659254182C9}
VIEJO 220235388 | {5487E49D-3A5D-43A1-BCCA-6878D14EA68E}
VIEJO 220285904 | {2C01517C-E612-4085-8398-17DFB2943C5D}
VIEJO 22029100 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
VIEJO 22029104 | {AD318D3F-F8E0-477A-9CA4-DF6AF7B738B6}
VIEJO 22029112 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
VIEJO 22029118 | {BA7590D4-FA7A-4E66-A4E2-9385E2F5FD08}
VIEJO 22029120 | {3A16450D-C56F-42B5-80F8-8369EAD6F0C2}
VIEJO 220292792 | {C8ECEDCB-3AAA-445C-9FF2-2773F53D5EAE}
VIEJO 22029488 | {8E85DA31-E8CD-4D80-BE55-60AFA6937F74}
VIEJO 220298146 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
VIEJO 2202CB | {204F3E15-8D98-42F3-A6B0-F8D2FC5C7EAD}
VIEJO 22032634 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 22032636 | {2745EA16-9172-4362-B554-6BC9B1A69619}
VIEJO 22039094 | {BCAEB21F-2017-4B30-B93C-AB6BCBE099D0}
VIEJO 2203947314 | {2745EA16-9172-4362-B554-6BC9B1A69619}
VIEJO 2203CB | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 2204385618 | {84E279B4-A57A-4132-ABEC-C7AA0EE5903D}
VIEJO 2204481042 | {540DA92C-2BA2-4C83-857C-5060FD1BE289}
VIEJO 220486890 | {82047029-EAC1-4E39-B4D2-10647DA90BC3}
VIEJO 22049440 | {35D3CEF8-0523-4ECA-BC11-26CD68907349}
VIEJO 22049540 | {D3AE8800-862E-498F-9908-541EA621BA7E}
VIEJO 2204CB | {DB34AA1E-C0F6-41DF-BFC5-43E5CD8E6B2B}
VINA 11011570 | {427F674F-2998-4807-8909-FFE2EF8784B5}
VINA 11012681 | {427F674F-2998-4807-8909-FFE2EF8784B5}
VINA 110135730 | {DE33B171-715A-4B55-A52C-48E0D345F70B}
VINEYARD 2107978364 | {3BBA2979-D28D-4292-8651-8D6BC40655D3}
VINEYARD 2107CB | {E0DA3FA9-134E-46BA-BA63-A138252A7798}
VINEYARD 2107MR332 | {5E4EB8F1-F20C-4A10-9616-09E586C03349}
VINEYARD 2107MR649 | {E0DA3FA9-134E-46BA-BA63-A138252A7798}
VINEYARD 2108MR172 | {719ECDBC-AADB-4BEE-A55F-93F185A30BDE}
VINEYARD 2108MR172 | {D247C9D4-2385-4C86-98D9-FAEFF0DAB6B3}
VINEYARD 2110946322 | {14A8794B-8A75-4FC8-9957-3059A6D6C76B}
VINEYARD 2110CB | {4B9A456E-40C9-431E-A74D-1C7F9C39E74C}
VINEYARD 2110CB | {F7813E92-72BA-4ABD-9638-C1769106789A}
VINEYARD 2110CB | {14A8794B-8A75-4FC8-9957-3059A6D6C76B}
VOLTA 11011516 | {3F11AD42-8CBD-4A85-ACAE-76F96892C309}
VOLTA 11011596 | {2F8DBBAA-A379-4ECE-8007-F482E8F75EAA}
VOLTA 11011640 | {DF67F6ED-C0C1-4634-A8E7-5650468AFAD4}
VOLTA 1101239094 | {9AEB66C9-A93D-411C-A30F-DBF0D525FC91}
VOLTA 110149742 | {2B3F7DCA-485E-4940-AF70-C148286D4D0A}
VOLTA 1101507876 | {BF0E4538-86EF-4A16-BC6B-FF3CC49B1D10}
VOLTA 110153118 | {0F8042BD-810A-4C9D-833A-F377AF6EE4DF}
VOLTA 110165764 | {375728DD-644E-4E4B-9A8F-230DD2D4E917}
VOLTA 110185234 | {ED0B6774-A707-41C7-AD0B-86162B275429}
VOLTA 1101914816 | {5F524D99-5A7F-42DE-BC2E-51D7912A1CAB}
VOLTA 1101CB | {F21A680A-E282-4C69-AC36-05BB391457FE}
VOLTA 11021502 | {1EA4A0A1-3D5B-4E8F-B75B-661AF3FEE831}
VOLTA 11021504 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
VOLTA 11021646 | {82B5D74E-1D42-49A6-873C-1363407619B8}
VOLTA 11021650 | {FEE27DB0-3817-4D7E-9EF5-189449263C1D}
VOLTA 1102281296 | {6381DBA6-6F66-4F8E-9BD7-1A77E260C1A5}
VOLTA 1102453266 | {98C4DD6D-D3EE-4676-9123-391728297153}
VOLTA 110254932 | {3AA926AF-5D59-48E9-968A-65279153CE9D}
VOLTA 1102641544 | {06F73A44-E6BF-4E7C-AE40-21A987895C90}
VOLTA 1102765366 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
VOLTA 11029742 | {666559A7-03EB-4157-BF3B-FDC9527EC86F}
VOLTA 11029742 | {A7123BEC-B365-4766-B96E-6C5017CAB086}
VOLTA 1102CB | {DC239059-B1DA-4C89-A482-3310C8764DA5}
WALDO 0401965216 | {B6A1E84D-F904-4E0D-8713-BF77906CA63F}
WALDO 0402258792 | {41C45E4C-83D0-45DA-8DDC-FF29D2FC8610}
WALNUT CREEK 0404CB | {D56BF5EB-906E-4B51-BA5A-E962F016AADF}
WATERSHED 0402CB | {1B6353F3-7152-4A32-A40C-9970C5A62BA9}
WATSONVILLE 21015470 | {2C7BC800-10C3-4DC0-9802-A63A1E430DC6}
WEIMAR 11012058 | {77B75A1F-CEB2-4775-8F57-5AD0D012EF37}
WEIMAR 11012058 | {7EF077DC-E313-42E9-8185-688E5BE27A63}
WEIMAR 11012084 | {1AAC91CD-F390-4834-9229-DA9482F10795}
WEIMAR 11012740 | {DA254098-CE2F-4B1D-8DCD-E2A142ECA867}
WEIMAR 11012764 | {CBE676E4-58AB-460F-8EF4-93AB8DD21D9C}
WEIMAR 1101963878 | {3F2C9EA4-8A25-4199-991D-03F34AC1B306}
WEIMAR 1101CB | {C6D2DBB1-9437-46D3-8E37-6D1AD2333690}
WEIMAR 11022038 | {AAA92226-2A7F-4F0B-BFD9-7222659B7631}
WEIMAR 1102CB | {576CF59E-86D2-4E41-A7A3-27CEB8B77F40}
WELLFIELD 11022842 | {94668338-D057-4AD5-892F-BB0D86C28946}
WELLFIELD 1102CB | {B75AE0C3-AE32-4560-9D2E-0C12544F84C7}
WEST POINT 110112256 | {10618A90-ED86-44CD-8B76-773E3BF2AE42}
WEST POINT 110113444 | {1F21142A-72EE-4D4A-A8F0-E9702D60226C}
WEST POINT 110136674 | {B0AD76E8-C8B6-4D91-BE40-831E99BE5659}
WEST POINT 11014706 | {E8E54876-15CA-4535-8C00-844AA0076F05}
WEST POINT 1101CB | {B92F58F2-6135-47A4-8467-3E84B6151393}
WEST POINT 1101L1969 | {10618A90-ED86-44CD-8B76-773E3BF2AE42}
WEST POINT 11021305 | {0EFB4216-A177-4018-B731-828073FEC64E}
WEST POINT 11021341 | {7DA2EEB5-1A19-437C-8020-DD813277F9CC}
WEST POINT 110234416 | {0EFB4216-A177-4018-B731-828073FEC64E}
WEST POINT 110236676 | {1445490F-C0B5-460E-8F6D-3B7658CD2546}
WEST POINT 11024788 | {7DA2EEB5-1A19-437C-8020-DD813277F9CC}
WEST POINT 11024790 | {4C31F9F3-FF43-4013-B249-266EFA0B514A}
WEST POINT 110272036 | {4D3D5180-6A6C-4C43-B692-915E3881962C}
WEST POINT 110277204 | {6211F369-8BB0-4A6F-AF12-1490B4F377A4}
WEST POINT 110293116 | {2DE74D61-95A1-4D32-9CCA-28AB5E692CE7}
WEST POINT 1102CB | {EC11255E-1283-4994-89AE-376C709CBC76}
WEST POINT 1102CB | {386D733D-CD43-4317-BE17-EAA2ED2E8030}
WESTLEY 110111730 | {5D9D0169-9A60-4F2E-81FE-3563A32A79B5}
WESTLEY 110111736 | {A40369F9-5BFB-4A69-8B09-DA1A82DE5EFA}
WESTLEY 1101463982 | {E05B0763-14F9-4FE9-A6CE-D2FD7DA8396A}
WESTLEY 1103237522 | {248AE4B1-0618-414C-9295-0197646733FC}
WESTLEY 11039010 | {0DB6DB9D-7804-4D10-B639-1A5CA91DDA98}
WESTLEY 11039900 | {0DB6DB9D-7804-4D10-B639-1A5CA91DDA98}
WHEATLAND 11041348 | {86B4B4F4-9AA5-4F80-9B50-3C90FCAE3FE6}
WHEATLAND 11042700 | {4B414DEC-F869-45CA-863F-BA162E505527}
WHEATLAND 1105248490 | {373720FB-6F75-4350-A081-94440166CEBB}
WHEATLAND 110591170 | {B814ECD9-6160-4057-8AF0-345725EF4AA1}
WHEELER RIDGE 1101234580 | {6E248E69-5334-44F4-BB88-9697823ED075}
WHEELER RIDGE 11012878 | {F5B58D0D-3D6A-436B-9C40-AFEED4581FEF}
WHEELER RIDGE 110137662 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
WHEELER RIDGE 11014164 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
WHEELER RIDGE 110170228 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
WHEELER RIDGE 110183646 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
WHEELER RIDGE 110190844 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
WHEELER RIDGE 1101CB | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
WHITMORE 11011594 | {6D09044C-C5BE-4454-95FA-4A81291B04F9}
WHITMORE 11011598 | {0A7498D4-3D67-421B-B0F9-EE472ACD2B71}
WHITMORE 110145262 | {D9E3C410-A0BF-4EA8-96F2-E696EF9ADFFA}
WHITMORE 1101589578 | {9B3AF54F-5B2F-4275-8A5D-51F2329D7BA1}
WHITMORE 1101903576 | {D707507F-8C93-4538-B5F3-ACA8DB6C9EF7}
WHITMORE 1101CB | {E0835FD3-053C-4202-87EB-465B52D17969}
WHITMORE 1101WTGLR | {E0835FD3-053C-4202-87EB-465B52D17969}
WILDWOOD 11011454 | {D78DCFCA-A3F5-48E7-AD4B-409B173DF385}
WILDWOOD 11011576 | {57B8A89B-DB5A-4A47-A82F-ABC7F06A8571}
WILDWOOD 1101384582 | {DE2BE838-418E-479A-846C-D45336A92EC1}
WILDWOOD 110185112 | {DBAB12BB-6159-4B5E-9921-C1747473FB98}
WILDWOOD 110198896 | {BF76B4C8-9530-427B-8649-806B9F48C554}
WILDWOOD 1101CB | {47D06C81-6B61-4B8B-8054-D7C4BE7B9ED2}
WILLIAMS 110230232 | {ADFD680A-942E-4051-AFFB-E1BB46F8DE19}
WILLITS 11021270 | {1C1CA89F-8D6E-4D8E-B038-38C87CE5A599}
WILLITS 1102350324 | {E32B6BE0-3764-43AD-A424-17E7100BD267}
WILLITS 1102CB | {9734DBF0-6F90-4CE9-BF04-F2CD4B5AEADC}
WILLITS 1102CUS8736 | {9734DBF0-6F90-4CE9-BF04-F2CD4B5AEADC}
WILLITS 11032506 | {3B860DB0-A747-4B2B-900E-A58BF536B758}
WILLITS 110337504 | {00459A21-49A7-4C9F-B533-C9081A2B5652}
WILLITS 110337506 | {0E5984A8-2AB8-4609-A4AD-A7903A25522F}
WILLITS 1103409216 | {9EA45B12-9DAE-41DD-A093-6F45C691C648}
WILLITS 1103538 | {BE2F5686-D520-4116-B2FF-E45C57EBCDE2}
WILLITS 1103564506 | {4F653083-189E-4DD0-AEDF-74D1A3A4FADD}
WILLITS 1103696 | {EC79F2BF-D405-4EF8-A570-37C7BDE7D1BE}
WILLITS 1103826 | {72556B33-F33B-4E33-8959-39723007B093}
WILLITS 110391810 | {75E7E1B3-D461-49A0-A0AB-E84CDEE528DF}
WILLITS 110391948 | {69FCB8B8-95BC-4541-BD6A-BC578FAA27C9}
WILLITS 1103964 | {B6068DE4-2B76-4559-A97F-83EC4465ECB7}
WILLITS 1103966 | {BD0977E2-D82F-4AAC-B014-EDCBC19E0BA7}
WILLITS 1103968 | {7E4735B5-33E8-4CD6-9F8D-A9385ABC1901}
WILLITS 1103CB | {30B0A48E-C3E5-42AA-9273-8BF1B6001968}
WILLITS 1104188268 | {F170EA1C-ED28-4FA0-9674-709AC3DC1CC0}
WILLITS 1104329646 | {B6D81FD3-E8F1-4789-8A3D-786E0C133AC6}
WILLITS 110434008 | {5B3D2F2F-DF90-45C0-963C-1589633A1498}
WILLITS 1104341020 | {47E718CA-B049-4197-84E1-96CD58F2DA8A}
WILLITS 11044650 | {CBE7DCF1-ECDA-4517-A76B-79D934ABEB82}
WILLITS 1104504 | {A1E50B4A-662D-4B26-9A77-844EAB929468}
WILLITS 1104627552 | {E29C36BB-A169-479C-AE48-87F28EBCCCAD}
WILLITS 1104936096 | {8248C880-166C-430F-A087-7EE0312E38BC}
WILLITS 1104CB | {19EB4414-DC45-4E37-BE88-7022C918AAEC}
WILLOW CREEK 110129362 | {1D151194-CF04-464D-9004-1F697BF4DA48}
WILLOW CREEK 11013050 | {339F8F9F-E6E2-48FC-94D7-73A8490708ED}
WILLOW CREEK 11014904 | {2D4A5008-1C90-406A-A2B7-E4FA7A353F8A}
WILLOW CREEK 11015002 | {D8150527-3285-419A-A933-812F08668577}
WILLOW CREEK 11015002 | {F93B7399-B5D7-47F7-B54D-9C6933AF7A2F}
WILLOW CREEK 110191926 | {ABEF63BB-FD93-485F-8439-718A3A0F3B42}
WILLOW CREEK 1101CB | {D8B02D5B-6C13-4C05-89BB-FB46690FC150}
WILLOW CREEK 110237374 | {E5474BC9-1FBC-47D7-924C-371BAFB1C79B}
WILLOW CREEK 1102CB | {0F7FFA32-0648-474C-B64E-A51E578D757F}
WILLOW CREEK 1103181562 | {A739E4CD-6027-447C-8193-CB877EF24141}
WILLOW CREEK 1103205028 | {14EDF25B-565E-45F6-929A-4EE758947CA8}
WILLOW CREEK 11032936 | {2C99C690-D2AE-47A9-8969-EBD60FC1E2F7}
WILLOW CREEK 11033090 | {999C3E0D-1E31-46AC-B115-3B4EB4A2A32A}
WILLOW CREEK 110347966 | {17DD54A2-E0AC-4BEA-A392-1296720E1866}
WILLOW CREEK 110347966 | {E7E4CCFA-1ADF-4735-A0EC-4090945D6801}
WILLOW CREEK 11035012 | {315E4027-C3C2-48C5-87DF-DFA709D95931}
WILLOW CREEK 11037514 | {2ADAB335-F68D-4E0E-93A5-403C7C54DA76}
WILLOW CREEK 1103CB | {A739E4CD-6027-447C-8193-CB877EF24141}
WILLOW PASS 1101152874 | {F4D0AF9A-071E-4C57-9A34-14AB7BA67617}
WILLOW PASS 1101CB | {7CF27098-3028-4D6C-96BA-430FB7E80045}
WILLOW PASS 210721135 | {AAC60A33-2BAE-4745-8C6C-2A17FF968240}
WILLOW PASS 2107273996 | {85D52075-D52D-4D71-A7CF-355529F177DC}
WILLOW PASS 2107273996 | {31EEDA66-62CC-4E94-9F57-70FF511E1CF4}
WILLOW PASS 2107537100 | {24C8C7E8-733A-453C-8A4F-FE8CF59DAF59}
WILLOW PASS 2107CB | {24C8C7E8-733A-453C-8A4F-FE8CF59DAF59}
WILLOW PASS 210879972 | {1FEB7E65-DDE1-46AE-83AD-B5F30417F926}
WILLOW PASS 2108CB | {1FEB7E65-DDE1-46AE-83AD-B5F30417F926}
WILSON 110310690 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WILSON 110310700 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WILSON 11034140 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WILSON 110347636 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WILSON 110348236 | {A1AC7D41-B778-451D-ABF3-8E1F77E14CAD}
WILSON 1103873156 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WILSON 11039080 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WINDSOR 1102382 | {8BAFFC14-6408-458C-A293-E7A624D7DE6D}
WINDSOR 11025066 | {8BAFFC14-6408-458C-A293-E7A624D7DE6D}
WINDSOR 1102596 | {59925254-34DF-4AF0-8CD9-F41C717859C6}
WINDSOR 1103171410 | {CF3D4281-EA2F-4415-B4CD-AC674F9B4864}
WINDSOR 11035060 | {5C89CE05-2636-4AC9-BAFC-5707AC921B94}
WINDSOR 1103701650 | {4CA5D300-8532-4AF9-BD85-CE58373188C7}
WINDSOR 1103CB | {AC54FADD-7787-4603-A3A1-1A1440375EA4}
WISE 11011404 | {924DEF09-31E0-4543-805A-687FEB1C84E6}
WISE 110163199 | {919A8A04-B874-4A68-AF90-D4143250C76A}
WISE 1101CB | {919A8A04-B874-4A68-AF90-D4143250C76A}
WISE 11022054 | {E6EC7043-C8B2-457F-AB90-031C70C010CA}
WISE 11022230 | {F1207558-CC1A-4752-93E1-1A45AF2EEAFE}
WISE 11022234 | {2EBA7959-7933-4246-BD38-55C2DE2602D7}
WISE 1102307494 | {DAD370F0-D502-456B-9D6C-C04B93F7ABC9}
WISE 1102449556 | {51CECB7D-FE74-4A7F-A054-30E9A1B3F446}
WISE 1102465074 | {551FC8A6-8E47-4C6B-BA77-51B1DF1DDFC3}
WISE 1102697216 | {64620CA8-4B52-4298-8F14-91A606AD81F8}
WISE 1102697216 | {BFD9E547-EC0B-4BBF-83A2-6E5AE3B0CA31}
WISE 1102CB | {605358FE-4007-4349-A521-8A072F22F69A}
WISHON 1101514298 | {CACEDC8F-E904-428B-BE98-B04E14D43479}
WOOD 0401CB | {1F25C3BD-C09D-4433-9558-CEA0BEA55FCC}
WOOD 0401CB | {F6FBF5EF-0F39-43BE-9573-8D14EE89543A}
WOOD 0401CB | {8F0A48D9-A322-4FA2-98F5-9BA99B0B225E}
WOODACRE 11011456 | {1ACD7F45-5073-4366-9697-A511E06B0768}
WOODACRE 1101404 | {9E6A6B97-69AF-4332-A126-23324C3DC522}
WOODACRE 110191900 | {315B41A4-2763-4241-B96A-998B94A74075}
WOODACRE 110196844 | {829ACA47-635E-4880-92A0-8C929EC179A6}
WOODACRE 1101CB | {0C1EAF38-D291-4410-BD5A-7EDE35C497EC}
WOODACRE 11021280 | {2D7883CD-6608-4310-8AB5-FA60A939C766}
WOODACRE 1102137662 | {C3672683-8002-442C-8DD0-CA97E76D56C3}
WOODACRE 1102851 | {61FE98E8-80EF-4BDB-989C-5A04CDB81F15}
WOODACRE 1102CB | {61FE98E8-80EF-4BDB-989C-5A04CDB81F15}
WOODSIDE 11011922 | {26E85C09-0B57-42B9-B352-ED273600E95D}
WOODSIDE 11012299 | {0C4874FF-D222-478C-B9D7-BED0F08FA35C}
WOODSIDE 110147872 | {3F2B4E81-3F76-4F92-B31C-17D1A0284314}
WOODSIDE 110176194 | {D1B97B5C-C0C0-4C1A-A0E9-54FF1BD58307}
WOODSIDE 110179892 | {B37068EA-10E5-4EBE-BB13-FA7A8D9F573E}
WOODSIDE 11018522 | {0C4874FF-D222-478C-B9D7-BED0F08FA35C}
WOODSIDE 11018884 | {E37F33F6-1C0A-4C76-AC62-7F0B65A2F196}
WOODSIDE 11018912 | {2C96F5E7-EFFA-439D-98B4-19B9F97DA294}
WOODSIDE 11018912 | {429461DA-3754-40D0-8283-6B07C0ED0208}
WOODSIDE 11018972 | {31C2E01B-7B87-407B-9DC8-52C242320576}
WOODSIDE 11018974 | {95843233-31DE-4B8A-A7FD-7E8E48EA1CD1}
WOODSIDE 11018974 | {AE7048D1-B6D6-4F66-8C2D-AEADECFC750D}
WOODSIDE 1101CB | {74C9689B-27E2-45AE-B69F-F01C8E2CB358}
WOODSIDE 110239574 | {BF6AF21E-B6B4-453B-837A-E823913B38FF}
WOODSIDE 1102472928 | {DEE5BC84-14D0-4B16-967C-4B20A0B07E86}
WOODSIDE 11028862 | {4C49C25B-7AC8-408B-8A99-E4CB51688164}
WOODSIDE 11029046 | {BF6AF21E-B6B4-453B-837A-E823913B38FF}
WOODSIDE 1102CB | {1A7707ED-44BC-402D-AC12-5D698199529B}
WOODSIDE 11042337 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
WOODSIDE 11043583 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
WOODSIDE 11043585 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
WOODSIDE 1104420146 | {39508B32-B583-4F3B-8AB5-C8A9DFC4FCD3}
WOODSIDE 1104456052 | {B5C1CCF7-3737-412C-9D78-BAC61B5ECBAC}
WOODSIDE 1104520832 | {2CDC70D4-A195-46DD-838C-5A22FD1041DB}
WOODSIDE 1104555372 | {73C37461-BB3B-432F-BC96-82FA7CA2E859}
WOODSIDE 11049030 | {24F38127-D3B0-46CD-A96D-4474F1F7C2CF}
WOODSIDE 11049032 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
WOODSIDE 11049116 | {37A21F97-AEE6-4520-B851-056330FD3EDF}
WOODSIDE 1104931904 | {ABDE444A-2BE8-4532-B3C2-F916DD3C67D7}
WOODSIDE 1104CB | {C0699A77-D9F1-4326-8400-EC5E43167E10}
WOODSIDE 110551262 | {B0B93653-ABAA-40D2-863C-C601369FC194}
WOODSIDE 11059160 | {B0B93653-ABAA-40D2-863C-C601369FC194}
WOODSIDE 1105CB | {B0B93653-ABAA-40D2-863C-C601369FC194}
WOODWARD 2108441553 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
WOODWARD 21085060 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
WOODWARD 2108935396 | {54379B90-C0BC-4B7C-8E22-0C10DD6F3A72}
WOODWARD 2108979850 | {61F2ACD6-570E-4D22-AC3A-276FF7469BBF}
WOODWARD 2108CB | {8314795F-0D04-45BD-AE69-B7277494B0E9}
WOODWARD 2108CUS1164 | {61F2ACD6-570E-4D22-AC3A-276FF7469BBF}
WOODWARD 2108CUS5875 | {41DA8C6A-A66B-4741-8630-05B8383240D3}
WOODWARD 2108D412 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
WOODWARD 2108R2860 | {41DA8C6A-A66B-4741-8630-05B8383240D3}
WOODWARD 2108R867 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
WRIGHT 111011942 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WRIGHT 1110288242 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WRIGHT 11103220 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WRIGHT 11103800 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WRIGHT 111084280 | {339E2C7E-2DBD-42B5-BF29-414F5F6E8F92}
WRIGHT 1110888088 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WRIGHT 11109090 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WRIGHT 1110CB | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WYANDOTTE 110213044 | {6DDE6DFF-A5B7-42A5-A5E6-915A880E38B9}
WYANDOTTE 110213916 | {6520C128-A5D2-408B-801E-4626440008FB}
WYANDOTTE 11021502 | {A54ECB41-5029-41D9-AD67-64342065DC6F}
WYANDOTTE 1102CB | {835C2D90-E2D1-4649-9C53-DD5E51FB29AE}
WYANDOTTE 110313018 | {FD9CCA92-C052-4A36-88EE-05418588C974}
WYANDOTTE 11031504 | {ED98A6D0-06D7-43E4-A03B-484FE67F86A6}
WYANDOTTE 11031508 | {1F5D8008-7EA4-4278-A040-64AB0E7AD925}
WYANDOTTE 1103640652 | {59B1EFCE-EA13-4733-ADA9-7461CE4DCF90}
WYANDOTTE 110366146 | {44DEC261-543D-4709-894B-61B8ADC18491}
WYANDOTTE 1103CB | {729134BB-0DFA-4145-807F-650A6E064048}
WYANDOTTE 1105329930 | {C09D41C2-6107-4911-B847-897C1DB6C91E}
WYANDOTTE 1105CB | {2426BD3B-3A69-4A04-A051-7581B14322B3}
WYANDOTTE 11061046 | {830E8D18-621D-4CC3-9150-C991F796F6A1}
WYANDOTTE 110613016 | {73895C48-E496-423A-BB9D-D8E6858BCD72}
WYANDOTTE 110613046 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 11061512 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 1106304014 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 110641650 | {87BD5616-A670-4B3C-B36B-8B72CB70DFA6}
WYANDOTTE 110697550 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 1106CB | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 11071026 | {F4C4052A-4712-4518-990B-FE0E43960860}
WYANDOTTE 11071510 | {9879E6FE-604B-48B5-AF02-92364DF9D405}
WYANDOTTE 1107219854 | {3460E96C-6AF2-473D-98AF-BD2B8C01E558}
WYANDOTTE 110737472 | {B3E100DA-AA63-42D1-94E1-A7F9E0DF29D9}
WYANDOTTE 110738438 | {112CEC5D-7594-450C-A06E-88C65F1E5892}
WYANDOTTE 110777578 | {E0470028-6FEE-4E7A-BA03-DFBD06B93819}
WYANDOTTE 1107829470 | {112CEC5D-7594-450C-A06E-88C65F1E5892}
WYANDOTTE 110796390 | {B74488FF-9B39-410B-9AAC-30106EC9509F}
WYANDOTTE 1107CB | {C8520005-9EA7-4C87-B336-C3E6B2DAE20B}
WYANDOTTE 1107CB | {0E127264-C3E4-4550-BC79-8854D7BB9B29}
WYANDOTTE 1107CB | {BDA7E326-12C4-4DD0-876F-746C4DA51193}
WYANDOTTE 11091040 | {10790C99-0AC4-4885-95AD-50DB99DD62BD}
WYANDOTTE 110913052 | {790FA841-FFAA-4636-AEC1-FF360B754DBB}
WYANDOTTE 11091520 | {FC542AC7-29DE-47A0-A073-41001E21B2E1}
WYANDOTTE 110931758 | {4018E6B5-9FD7-42B6-984E-3899183793C0}
WYANDOTTE 110932586 | {81BB6A5C-2DB9-49AA-A7A4-75F68838201B}
WYANDOTTE 110940608 | {CDE1CEEE-8C9B-4065-8C9F-F4DC3E571419}
WYANDOTTE 11095575 | {CDE1CEEE-8C9B-4065-8C9F-F4DC3E571419}
WYANDOTTE 11095607 | {790FA841-FFAA-4636-AEC1-FF360B754DBB}
WYANDOTTE 11095973 | {10790C99-0AC4-4885-95AD-50DB99DD62BD}
WYANDOTTE 1109702710 | {EEE67C1F-6C23-4D81-9B06-45B190348549}
WYANDOTTE 1109758802 | {EC08C284-9906-406B-94E5-ADD7510D64ED}
WYANDOTTE 1109759354 | {4C66E0D5-78ED-42EB-9F37-6A9ACA5BD894}
WYANDOTTE 110979932 | {67B8C4D8-FEA1-4243-99E7-B5C8BD7D2FA9}
WYANDOTTE 1109CB | {A372AD67-1459-47B8-8964-55AFC8B0D599}
WYANDOTTE 11101952 | {40F33AAB-5B9C-4B70-A571-E111B152C68A}
WYANDOTTE 11101954 | {652E0C25-B4E5-4F56-A678-A27ED9716769}
WYANDOTTE 11102590 | {EF5D8957-32CC-44F0-808E-217DC0A13E35}
WYANDOTTE 1110747922 | {60F5524C-0FF9-43B2-B1B9-D30D40C3AD67}
WYANDOTTE 1110873858 | {B9243DFE-989F-4BFE-A52A-70EF1DB7EE8E}
WYANDOTTE 1110CB | {B4858E1E-C2DC-43E7-A857-62EE09547E47}
ZACA 1101CB | {84844AA6-33FE-4B77-BE7F-2142383F94DA}
ZACA 1101Y70 | {C56ADC1A-9E36-443A-A4AD-EABCB05C5CD5}
ZACA 1101Y72 | {1D20AD79-1B20-4BDE-B0E8-CF4AA41EFB2A}
ZACA 1102CB | {06AE963E-8682-491C-931E-D311BC02A28D}
ZACA 1102Y02 | {615A0700-A424-4825-ACAC-C9AB34833626}
ZACA 1102Y48 | {6170E12A-002A-40B3-A4BB-42077F0D87F0}
ZACA 1102Y54 | {49C145C8-C8F5-459A-817E-3F37A5597C7A}

## YTD Ignition Data
fixed_index_no | OIS_Numbers | ignition_start_create_timestamp | dev_plbk_instruction | epss_circuit_opnum | circuit | circuit_protection_zone | fire_size | Response Time
20230530 | 2138125, 2138158, 2138756 | 2023-06-16 02:10 | N/A | 12022212-81608 | CLAYTON 2212 | CLAYTON 2212681608 | 1 meter - <3 meters | 57
20230659 | 2156712, 2156662 | 2023-07-07 20:26 | N/A | - | - | - | 10-99 | -
20230676 | 2159010 | 2023-07-10 21:27 | FTS | 182391103-N42 | OILFIELDS 1103 | OILFIELDS 1103N42 | 3 meters - 0.25 Acres | 57
20230692 | 2162104 | 2023-07-14 04:40 | FTS | 192221101-438596 | GARBERVILLE 1101 | GARBERVILLE 1101438596 | 0.26-9.99 | 58
20230693 | 2162458 | 2023-07-14 10:36 | FTS | 43381101-476 | POINT ARENA 1101 | POINT ARENA 1101476 | 1 meter - <3 meters | 31
20230707N | 2163487 | 2023-07-15 13:57 | FTS | 103201102-1064 | CHALLENGE 1102 | CHALLENGE 11021064 | 3 meters - 0.25 Acres | 43
20230782N | 2174538 | 2023-07-26 14:13 | N/A | 83252106-5178 | PAUL SWEET 2106 | PAUL SWEET 21065178 | 3 meters - 0.25 Acres | 40
20230792 | 2176618 | 2023-07-28 16:00 | N/A | 83622106-12760 | CAMP EVERS 2106 | CAMP EVERS 210612760 | 3 meters - 0.25 Acres | 49
20230823 | 2179861 | 2023-08-01 18:52 | N/A | 182771102-CB | CAMBRIA 1102 | CAMBRIA 1102CB | 0.26-9.99 | 56
20230875 | 2188744 | 2023-08-11 14:19 | N/A | 192171103-5012 | WILLOW CREEK 1103 | WILLOW CREEK 11035012 | 1 meter - <3 meters | 45
20230912 | 2195808, 2195954 | 2023-08-19 16:19 | N/A | 192321121-CB | FORT SEWARD 1121 | FORT SEWARD 1121CB | 3 meters - 0.25 Acres | 46
20230973 | 2204971 | 2023-08-29 16:55 | N/A | 192221101-39524 | GARBERVILLE 1101 | GARBERVILLE 110139524 | 0.26-9.99 | 38
20230981 | 2206272 | 2023-08-30 17:20 | N/A | 182742104-88772 | SAN BENITO 2104 | SAN BENITO 210488772 | 3 meters - 0.25 Acres | 18
20231004 | 2210314 | 2023-09-05 16:40 | FTS | 182611104-R12 | PASO ROBLES 1104 | PASO ROBLES 1104R12 | 3 meters - 0.25 Acres | 44
20231006 | 2210308 | 2023-09-05 16:33 | FTS | 153652110-7742 | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 21107742 | 3 meters - 0.25 Acres | 30
20231045 | 2218270 | 2023-09-13 19:34 | FTS | 013432207-99096 | FAIRVIEW 2207 | FAIRVIEW 220799096 | 0.26-9.99 | 63
20231071 | 2223636 | 2023-09-20 17:04 | N/A | 252941107-822606 | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | 0.26-9.99 | 18
20231073 | 2224441 | 2023-09-22 07:07 | N/A | 152261105-2102 | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11052102 | 0.26-9.99 | 36
20231074 | 2224492 | 2023-09-22 08:00 | FTS | 043051101-718 | MONTICELLO 1101 | MONTICELLO 1101718 | 3 meters - 0.25 Acres | 27
20231083 | 2226767 | 2023-09-25 14:38 | N/A | 042601102-2600 | PHILO 1102 | PHILO 11022600 | 0.26-9.99 | 18
20231136 | 2237281 | 2023-10-07 01:55 | FTS | 182981102-CB | JOLON 1102 | JOLON 1102CB | 3 meters - 0.25 Acres | 45
20231356 | 2292498 | 2023-12-15 10:34 | FTS | 253642103-CB | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | 100-299 | 19.7833